## Price Comparison
|  | RFQ No: R0443 COST COMPARISON REPORT | RFQ No: R0443 COST COMPARISON REPORT | RFQ No: R0443 COST COMPARISON REPORT | Comp. Date : 05/03/2024 | Comp. Date : 05/03/2024 | Comp. Date : 05/03/2024 | Vendor Name : Red Room Referesh interiors Pvt. Ltd. (RV232409799) | [5 empty] | Vendor Name : KMS INTERIOR (RV232410212) | [5 empty] | Vendor Name : Distint India Enterprises LLP (RV232421254) | [5 empty] | Vendor Name : VYAN VENTURES PRIVATE LIMITED (RV232410150)
|  | RFQ No: R0443 COST COMPARISON REPORT | RFQ No: R0443 COST COMPARISON REPORT | RFQ No: R0443 COST COMPARISON REPORT | RFQ #: R0443 | RFQ #: R0443 | RFQ #: R0443 | Contact Name : Jayant | [5 empty] | Contact Name : Kundan Suthar | [5 empty] | Contact Name : Sanjay Jain | [5 empty] | Contact Name : Santosh Kumar/Ved Prakash Pandey
|  | RFQ No: R0443 COST COMPARISON REPORT | RFQ No: R0443 COST COMPARISON REPORT | RFQ No: R0443 COST COMPARISON REPORT | RFQ Date : 05/03/2024 12:44:16 | RFQ Date : 05/03/2024 12:44:16 | RFQ Date : 05/03/2024 12:44:16 | Vendor City : Delhi | [5 empty] | Vendor City : | [5 empty] | Vendor City : | [5 empty] | Vendor City :
|  | RFQ No: R0443 COST COMPARISON REPORT | RFQ No: R0443 COST COMPARISON REPORT | RFQ No: R0443 COST COMPARISON REPORT | BCD Date : | BCD Date : | BCD Date : | Telephone # : 9999984384 | [5 empty] | Telephone # : | [5 empty] | Telephone # : | [5 empty] | Telephone # :
|  | RFQ No: R0443 COST COMPARISON REPORT | RFQ No: R0443 COST COMPARISON REPORT | RFQ No: R0443 COST COMPARISON REPORT |  |  |  | Mobile # : 9999984384 | [5 empty] | Mobile # : | [5 empty] | Mobile # : 98102 60645 | [5 empty] | Mobile # :
PR Number : TFS-2324-00039 | PR Number : TFS-2324-00039 | PR Number : TFS-2324-00039 | PR Number : TFS-2324-00039 | PR Number : TFS-2324-00039 | PR Number : TFS-2324-00039 | PR Number : TFS-2324-00039 | PR Number : TFS-2324-00039 | Email : info.rrrinteriors@gmail.com | [5 empty] | Email : pravin.takle@kapcocatering.com | [5 empty] | Email : di.sanjayjain@gmail.com | [5 empty] | Email : vyanventures01@gmail.com
Package / RFQ Name : ELECTRICAL WORK FOR BIKANERVALA | Package / RFQ Name : ELECTRICAL WORK FOR BIKANERVALA | Package / RFQ Name : ELECTRICAL WORK FOR BIKANERVALA | Package / RFQ Name : ELECTRICAL WORK FOR BIKANERVALA | Package / RFQ Name : ELECTRICAL WORK FOR BIKANERVALA | Package / RFQ Name : ELECTRICAL WORK FOR BIKANERVALA | Package / RFQ Name : ELECTRICAL WORK FOR BIKANERVALA | Package / RFQ Name : ELECTRICAL WORK FOR BIKANERVALA | Round # : 2 (Auction) | [5 empty] | Round # : 2 (Auction) | [5 empty] | Round # : 2 (Auction) | [5 empty] | Round # : 2 (Auction)
Buyer : Jogeswar Sahu / Technical : / Approver : | Buyer : Jogeswar Sahu / Technical : / Approver : | Buyer : Jogeswar Sahu / Technical : / Approver : | Buyer : Jogeswar Sahu / Technical : / Approver : | Buyer : Jogeswar Sahu / Technical : / Approver : | Buyer : Jogeswar Sahu / Technical : / Approver : | Buyer : Jogeswar Sahu / Technical : / Approver : | Buyer : Jogeswar Sahu / Technical : / Approver : | Quotation Date : |  |  | Quotation Validity Date : |  |  | Quotation Date : |  |  | Quotation Validity Date : |  |  | Quotation Date : |  |  | Quotation Validity Date : |  |  | Quotation Date : |  |  | Quotation Validity Date :
Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Currency :INR | Currency :INR | Currency :INR | Buyer Remark : . | [5 empty] | Buyer Remark : | [5 empty] | Buyer Remark : | [5 empty] | Buyer Remark :
Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | BUDGET PRICE : | .00 |  | Quote Currency : INR | [5 empty] | Quote Currency : INR | [5 empty] | Quote Currency : INR | [5 empty] | Quote Currency : INR
# | Item Code | Item Description | Unit | Qty | Last PO Details | Lowest Unit Rate | Lowest Vendor | First Bid | Disc % | GST % | Technical | Unit Price | Total | First Bid | Disc % | GST % | Technical | Unit Price | Total | First Bid | Disc % | GST % | Technical | Unit Price | Total | First Bid | Disc % | GST % | Technical | Unit Price | Total
1 |  | ELECTRICAL WORK FOR BIKANERVALA | LOT | 1.00 |  | 631809.00 | Red Room Referesh interiors Pvt. Ltd. | 651350.00 | 0.00 | 0.00 |  | 631,809.00 | 631,809.00 | 680970.00 | 0.00 | 0.00 |  | 680,970.00 | 680,970.00 | 915510.00 | 0.00 | 0.00 |  | 825,000.00 | 825,000.00 | 1513530.00 | 0.00 | 0.00 |  | 1,513,530.00 | 1,513,530.00
Item Total | [8 empty] | .00 | .00 |  |  | 631,809.00 |  | .00 | .00 |  |  | 680,970.00 |  | .00 | .00 |  |  | 825,000.00 |  | .00 | .00 |  |  | 1,513,530.00
Discount Total Value | [7 empty] | Grand Dis. Amt | .00 |  |  |  | .00 | Grand Dis. Amt | .00 |  |  |  | .00 | Grand Dis. Amt | .00 |  |  |  | .00 | Grand Dis. Amt | .00 |  |  |  | .00
GST Total Amount | [12 empty] | .00 | [5 empty] | .00 | [5 empty] | .00 | [5 empty] | .00
Net Landed Cost | [11 empty] | INR | 631,809.00 |  |  |  |  | INR | 680,970.00 |  |  |  |  | INR | 825,000.00 |  |  |  |  | INR | 1,513,530.00
Vendor Status | [7 empty] | Round # : 2 (Auction) | Round # : 2 (Auction)
Sr No. | Vendor Code | Vendor Name | [5 empty] | Status | Remarks
1 | RV232421254 | Distint India Enterprises LLP | [5 empty] | Participate
2 | RV232409799 | Red Room Referesh interiors Pvt. Ltd. | [5 empty] | Participate
3 | RV232410212 | KMS INTERIOR | [5 empty] | Participate
4 | RV232410155 | V S CONSTRUCTION | [5 empty] | Participate
5 | RV232410150 | VYAN VENTURES PRIVATE LIMITED | [5 empty] | Participate

## BOQ Price Bid
|  | RFQ No: R0443 COST COMPARISON REPORT | RFQ No: R0443 COST COMPARISON REPORT | Comp. Date : 05/03/2024 | Comp. Date : 05/03/2024 | Comp. Date : 05/03/2024 | Vendor Name : Red Room Referesh interiors Pvt. Ltd. | Vendor Name : Red Room Referesh interiors Pvt. Ltd. | Vendor Name : KMS INTERIOR | Vendor Name : KMS INTERIOR | Vendor Name : Distint India Enterprises LLP | Vendor Name : Distint India Enterprises LLP | Vendor Name : VYAN VENTURES PRIVATE LIMITED | Vendor Name : VYAN VENTURES PRIVATE LIMITED
|  | RFQ No: R0443 COST COMPARISON REPORT | RFQ No: R0443 COST COMPARISON REPORT | RFQ #: R0443 | RFQ #: R0443 | RFQ #: R0443 | Contact Name : Jayant | Contact Name : Jayant | Contact Name : Kundan Suthar | Contact Name : Kundan Suthar | Contact Name : Sanjay Jain | Contact Name : Sanjay Jain | Contact Name : Santosh Kumar/Ved Prakash Pandey | Contact Name : Santosh Kumar/Ved Prakash Pandey
|  | RFQ No: R0443 COST COMPARISON REPORT | RFQ No: R0443 COST COMPARISON REPORT | RFQ Date : 05/03/2024 12:44:16 | RFQ Date : 05/03/2024 12:44:16 | RFQ Date : 05/03/2024 12:44:16 | Vendor City : Delhi | Vendor City : Delhi | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City :
|  | RFQ No: R0443 COST COMPARISON REPORT | RFQ No: R0443 COST COMPARISON REPORT | BCD Date : | BCD Date : | BCD Date : | Telephone # : 9999984384 | Telephone # : 9999984384 | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # :
|  | RFQ No: R0443 COST COMPARISON REPORT | RFQ No: R0443 COST COMPARISON REPORT |  |  |  | Mobile # : 9999984384 | Mobile # : 9999984384 | Mobile # : | Mobile # : | Mobile # : 98102 60645 | Mobile # : 98102 60645 | Mobile # : | Mobile # :
PR Number : TFS-2324-00039 | PR Number : TFS-2324-00039 | PR Number : TFS-2324-00039 | PR Number : TFS-2324-00039 | PR Number : TFS-2324-00039 | PR Number : TFS-2324-00039 | PR Number : TFS-2324-00039 | Email : info.rrrinteriors@gmail.com | Email : info.rrrinteriors@gmail.com | Email : pravin.takle@kapcocatering.com | Email : pravin.takle@kapcocatering.com | Email : di.sanjayjain@gmail.com | Email : di.sanjayjain@gmail.com | Email : vyanventures01@gmail.com | Email : vyanventures01@gmail.com
Package / RFQ Name : ELECTRICAL WORK FOR BIKANERVALA | Package / RFQ Name : ELECTRICAL WORK FOR BIKANERVALA | Package / RFQ Name : ELECTRICAL WORK FOR BIKANERVALA | Package / RFQ Name : ELECTRICAL WORK FOR BIKANERVALA | Package / RFQ Name : ELECTRICAL WORK FOR BIKANERVALA | Package / RFQ Name : ELECTRICAL WORK FOR BIKANERVALA | Package / RFQ Name : ELECTRICAL WORK FOR BIKANERVALA | Round # : 2 (Auction) | Round # : 2 (Auction) | Round # : 2 (Auction) | Round # : 2 (Auction) | Round # : 2 (Auction) | Round # : 2 (Auction) | Round # : 2 (Auction) | Round # : 2 (Auction)
Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score :
Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Currency :INR | Currency :INR | Currency :INR | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date :
Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | BUDGET PRICE :.00 | BUDGET PRICE :.00 | BUDGET PRICE :.00 | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date :
Sr No. | Item Code | Item Name | Item Description | UOM | Qty | Minimum Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount
1 |  | ELECTRICAL WORK FOR BIKANERVALA | ELECTRICAL WORK FOR BIKANERVALA | LOT | 1.000 |  |  | 651,350.00 |  | 680,970.00 |  | 915,510.00 |  | 1,513,530.00
1 |  | PANELS, SWITCHGEARS DISTRIBUTION BOARD | PANELS, SWITCHGEARS DISTRIBUTION BOARD
2 |  | MAIN PANEL-1 | MAIN PANEL-1 | Nos. | 1.000 | 75,000.00 | 75000.00 | 75,000.00 | 155000.00 | 155,000.00 | 165000.00 | 165,000.00 | 175000.00 | 175,000.00
3 |  | Incomer 100 AMPS 4P MCCB, 25kA with TM Based O C SC Release. | Incomer 100 AMPS 4P MCCB, 25kA with TM Based O C SC Release.
4 |  | Meter Protection ELR with CBCT; 100 5A, 15VA, CL-1 CT s -3 Nos. for Schneider make Digital Load Manager (EM 6400 NG) | Meter Protection ELR with CBCT; 100 5A, 15VA, CL-1 CT s -3 Nos. for Schneider make Digital Load Manager (EM 6400 NG)
5 |  | Indication Phase indicating lamps with 6A MCB | Indication Phase indicating lamps with 6A MCB
6 |  | Busbar 125A TPN Cu Busbar | Busbar 125A TPN Cu Busbar
7 |  | Outgoings | Outgoings
8 |  | a) 63A 4P MCCB, 16kA, TM BASED-1 Nos. | a) 63A 4P MCCB, 16kA, TM BASED-1 Nos.
9 |  | b) 40A 4P MCB, 16kA, TM BASED-1 Nos. | b) 40A 4P MCB, 16kA, TM BASED-1 Nos.
10 |  | c) 32A DP MCB, 10kA, TM BASED-5 Nos. | c) 32A DP MCB, 10kA, TM BASED-5 Nos.
11 |  | d) 16-25A DP MCB, 10kA, -15 Nos. | d) 16-25A DP MCB, 10kA, -15 Nos.
12 |  | e) 6-16A SP MCB, 10kA, -20 Nos. | e) 6-16A SP MCB, 10kA, -20 Nos.
13 |  | f) 32A 4P MCCB 16kA TM Based Releases with 1.5 kW DOL Starter, Phase Indicating lamps, ON OFF TRIP Indication, ON OFF Push Button-1 Nos. | f) 32A 4P MCCB 16kA TM Based Releases with 1.5 kW DOL Starter, Phase Indicating lamps, ON OFF TRIP Indication, ON OFF Push Button-1 Nos.
14 |  | MAIN PANEL-2 | MAIN PANEL-2 | Nos. | 0.000 | .00 | 0.00 | .00 | 85000.00 | .00 | 0.00 | .00 | 0.00 | .00
15 |  | Incomer 40 AMPS 4P MCCB, 25kA with TM Based O C SC Release. | Incomer 40 AMPS 4P MCCB, 25kA with TM Based O C SC Release.
16 |  | Meter Protection ELR with CBCT; 40 5A, 15VA, CL-1 CT s -3 Nos. for Schneider make Digital Load Manager (EM 6400 NG) | Meter Protection ELR with CBCT; 40 5A, 15VA, CL-1 CT s -3 Nos. for Schneider make Digital Load Manager (EM 6400 NG)
17 |  | Indication Phase indicating lamps with 6A MCB | Indication Phase indicating lamps with 6A MCB
18 |  | Busbar 75A TPN Cu Busbar | Busbar 75A TPN Cu Busbar
19 |  | Outgoings | Outgoings
20 |  | a) 32A 4P MCB, 10kA-1 Nos. | a) 32A 4P MCB, 10kA-1 Nos.
21 |  | b) 25A 4P MCB, 10kA-1 Nos. | b) 25A 4P MCB, 10kA-1 Nos.
22 |  | c) 32A DP MCB, 10kA-1 Nos. | c) 32A DP MCB, 10kA-1 Nos.
23 |  | d) 40A DP MCB, 10kA-1 Nos. | d) 40A DP MCB, 10kA-1 Nos.
24 |  | SWITCHGEARS DISTRIBUTION BOARD | SWITCHGEARS DISTRIBUTION BOARD
25 |  | Supplying installing at site in positioning, connecting, testing and commissioning of the following type Distribution Boards Switchgears. (IP-43) ACRY DB | Supplying installing at site in positioning, connecting, testing and commissioning of the following type Distribution Boards Switchgears. (IP-43) ACRY DB
26 |  | Provide insulated dedicated earth link for UPS DB | Provide insulated dedicated earth link for UPS DB
27 |  | All MCB s for UPS shall be D Curve, C Curve for Power B Curve for Lighting. | All MCB s for UPS shall be D Curve, C Curve for Power B Curve for Lighting.
28 |  | SWITCHGEARS | SWITCHGEARS
29 |  | Supply, installation, testing and commissioning of sheet metal enclosures for the following switchgears. | Supply, installation, testing and commissioning of sheet metal enclosures for the following switchgears.
30 |  | 63 40 32 20 amps 4P MCB C TYPE with complete with all mounting accessories – for Indoor Legrand make | 63 40 32 20 amps 4P MCB C TYPE with complete with all mounting accessories – for Indoor Legrand make | Nos. | 0.000 | .00 | 0.00 | .00 | 3650.00 | .00 | 0.00 | .00 | 0.00 | .00
31 |  | 63 40 32 20 amps DP MCB C TYPE with complete with all mounting accessories – IP-65 | 63 40 32 20 amps DP MCB C TYPE with complete with all mounting accessories – IP-65
32 |  | 32 amps 4P MCB with 32A 5 Pin Ray Roll Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | 32 amps 4P MCB with 32A 5 Pin Ray Roll Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | Nos. | 0.000 | .00 | 0.00 | .00 | 2850.00 | .00 | 0.00 | .00 | 0.00 | .00
33 |  | 25 amps DP MCB with 25A 3 Pin Ray Roll Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | 25 amps DP MCB with 25A 3 Pin Ray Roll Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | Nos. | 0.000 | .00 | 0.00 | .00 | 2850.00 | .00 | 0.00 | .00 | 0.00 | .00
34 |  | 16 amps DP MCB with 15A 3 Pin Ray Roll Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | 16 amps DP MCB with 15A 3 Pin Ray Roll Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | Nos. | 0.000 | .00 | 0.00 | .00 | 1850.00 | .00 | 0.00 | .00 | 0.00 | .00
35 |  | 5 15 amps Switch Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | 5 15 amps Switch Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | Nos. | 0.000 | .00 | 0.00 | .00 | 1050.00 | .00 | 0.00 | .00 | 0.00 | .00
36 |  | DISTRIBUTION BOARDS | DISTRIBUTION BOARDS
37 |  | 6 WAY SPN DB - UPS DB | 6 WAY SPN DB - UPS DB | Nos. | 0.000 | .00 | 0.00 | .00 | 7500.00 | .00 | 0.00 | .00 | 0.00 | .00
38 |  | Incomer 20 AMPS DP MCB 10KA 1 Nos. | Incomer 20 AMPS DP MCB 10KA 1 Nos.
39 |  | Outgoings 6 10 16 A SP MCB B Type - 4 Nos. | Outgoings 6 10 16 A SP MCB B Type - 4 Nos.
40 |  | FABRICATED - LPDB | FABRICATED - LPDB | Nos. | 0.000 | .00 | 0.00 | .00 | 27500.00 | .00 | 0.00 | .00 | 0.00 | .00
41 |  | Incomer 80A, FP, MCB, 10kA 1 Nos | Incomer 80A, FP, MCB, 10kA 1 Nos
42 |  | Sub Incomer 63A, DP, RCCB, 100mA 3 Nos | Sub Incomer 63A, DP, RCCB, 100mA 3 Nos
43 |  | Outgoings 10 16 20 25 A SP MCB C Type - 36 Nos. | Outgoings 10 16 20 25 A SP MCB C Type - 36 Nos.
44 |  | Outgoings 32 A SP MCB C Type - 1 Nos. | Outgoings 32 A SP MCB C Type - 1 Nos.
45 |  | 12 WAY SPN DB - UPS DB | 12 WAY SPN DB - UPS DB | Nos. | 0.000 | .00 | 0.00 | .00 | 10500.00 | .00 | 0.00 | .00 | 0.00 | .00
46 |  | Incomer 32 AMPS DP RCBO 100mA | Incomer 32 AMPS DP RCBO 100mA
47 |  | Outgoings 10 16 20 A SP MCB C Type - 6 Nos. | Outgoings 10 16 20 A SP MCB C Type - 6 Nos.
48 |  | MV CABLES | MV CABLES
49 |  | POWER CABLING | POWER CABLING
50 |  | Supply and laying, effecting proper connections, testing commissioning of the following sizes of 1.1 KV XLPE FRLS armoured unarmoured PVC insulated PVC sheathed aluminium copper conductor cables conforming to IS 1554 and IS 694 for Flexible copp | Supply and laying, effecting proper connections, testing commissioning of the following sizes of 1.1 KV XLPE FRLS armoured unarmoured PVC insulated PVC sheathed aluminium copper conductor cables conforming to IS 1554 and IS 694 for Flexible copp
51 |  | Aluminium cables | Aluminium cables
52 |  | 4C x 50 Sq.mm. | 4C x 50 Sq.mm. | Mtr. | 0.000 | .00 | 0.00 | .00 | 380.00 | .00 | 0.00 | .00 | 0.00 | .00
53 |  | 3.5C x 35 Sq.mm. | 3.5C x 35 Sq.mm. | Mtr. | 0.000 | .00 | 0.00 | .00 | 315.00 | .00 | 0.00 | .00 | 0.00 | .00
54 |  | 4C x 25 Sq.mm. | 4C x 25 Sq.mm. | Mtr. | 20.000 | 5,300.00 | 350.00 | 7,000.00 | 265.00 | 5,300.00 | 560.00 | 11,200.00 | 450.00 | 9,000.00
55 |  | - do - but for copper cables | - do - but for copper cables
56 |  | 4C x 25 Sq.mm. | 4C x 25 Sq.mm. | Mtr. | 0.000 | .00 | 0.00 | .00 | 1800.00 | .00 | 0.00 | .00 | 0.00 | .00
57 |  | 4C x 16 Sq.mm. | 4C x 16 Sq.mm. | Mtr. | 0.000 | .00 | 0.00 | .00 | 1250.00 | .00 | 0.00 | .00 | 0.00 | .00
58 |  | 4C x 10 Sq.mm. | 4C x 10 Sq.mm. | Mtr. | 0.000 | .00 | 0.00 | .00 | 575.00 | .00 | 0.00 | .00 | 0.00 | .00
59 |  | 4C x 6 Sq.mm. | 4C x 6 Sq.mm. | Mtr. | 0.000 | .00 | 0.00 | .00 | 390.00 | .00 | 0.00 | .00 | 0.00 | .00
60 |  | 4C x 4 Sq.mm. | 4C x 4 Sq.mm. | Mtr. | 0.000 | .00 | 0.00 | .00 | 320.00 | .00 | 0.00 | .00 | 0.00 | .00
61 |  | 4C x 2.5 Sq.mm. | 4C x 2.5 Sq.mm. | Mtr. | 0.000 | .00 | 0.00 | .00 | 235.00 | .00 | 0.00 | .00 | 0.00 | .00
62 |  | 3C x 6 Sq.mm. | 3C x 6 Sq.mm. | Mtr. | 0.000 | .00 | 0.00 | .00 | 245.00 | .00 | 0.00 | .00 | 0.00 | .00
63 |  | 3C x 4 Sq.mm. | 3C x 4 Sq.mm. | Mtr. | 0.000 | .00 | 0.00 | .00 | 210.00 | .00 | 0.00 | .00 | 0.00 | .00
64 |  | 3C x 2.5 Sq.mm. | 3C x 2.5 Sq.mm. | Mtr. | 0.000 | .00 | 0.00 | .00 | 200.00 | .00 | 0.00 | .00 | 0.00 | .00
65 |  | CU Flexible Cables | CU Flexible Cables
66 |  | 4C x 6 Sq.mm. | 4C x 6 Sq.mm. | Mtr. | 0.000 | .00 | 0.00 | .00 | 350.00 | .00 | 0.00 | .00 | 0.00 | .00
67 |  | 4C x 4 Sq.mm. | 4C x 4 Sq.mm. | Mtr. | 0.000 | .00 | 0.00 | .00 | 220.00 | .00 | 0.00 | .00 | 0.00 | .00
68 |  | 3C x 4 Sq.mm. | 3C x 4 Sq.mm. | Mtr. | 0.000 | .00 | 0.00 | .00 | 185.00 | .00 | 0.00 | .00 | 0.00 | .00
69 |  | 3C x 2.5 Sq.mm. | 3C x 2.5 Sq.mm. | Mtr. | 0.000 | .00 | 0.00 | .00 | 120.00 | .00 | 0.00 | .00 | 0.00 | .00
70 |  | 2C x 2.5 Sq.mm. for Earthing | 2C x 2.5 Sq.mm. for Earthing | Mtr. | 0.000 | .00 | 0.00 | .00 | 100.00 | .00 | 0.00 | .00 | 0.00 | .00
71 |  | , - do - but for copper flexible cables | , - do - but for copper flexible cables
72 |  | 1c x 4 Sq.mm PVC insulated PVC flexible copper conductor cables alongwith termination (GREEN COLOUR) | 1c x 4 Sq.mm PVC insulated PVC flexible copper conductor cables alongwith termination (GREEN COLOUR) | Mtr. | 0.000 | .00 | 0.00 | .00 | 55.00 | .00 | 0.00 | .00 | 0.00 | .00
73 |  | TOTAL FOR POWER CABLES | TOTAL FOR POWER CABLES
74 |  | CABLE TERMINATION | CABLE TERMINATION
75 |  | Making cable and terminations including brass single compression glands and crimping type copper lugs for cable sizes mentioned below for aluminium or copper. | Making cable and terminations including brass single compression glands and crimping type copper lugs for cable sizes mentioned below for aluminium or copper.
76 |  | 4C x 50 Sq.mm. AL | 4C x 50 Sq.mm. AL | Nos. | 0.000 | .00 | 0.00 | .00 | 550.00 | .00 | 0.00 | .00 | 0.00 | .00
77 |  | 3.5C x 35 Sq.mm. | 3.5C x 35 Sq.mm. | Nos. | 0.000 | .00 | 0.00 | .00 | 500.00 | .00 | 0.00 | .00 | 0.00 | .00
78 |  | 4C x 25 Sq.mm. | 4C x 25 Sq.mm. | Nos. | 2.000 | 700.00 | 350.00 | 700.00 | 475.00 | 950.00 | 610.00 | 1,220.00 | 400.00 | 800.00
79 |  | 4C x 16 Sq.mm. CU | 4C x 16 Sq.mm. CU | Nos. | 0.000 | .00 | 0.00 | .00 | 550.00 | .00 | 0.00 | .00 | 0.00 | .00
80 |  | 4C x 10 Sq.mm. | 4C x 10 Sq.mm. | Nos. | 0.000 | .00 | 0.00 | .00 | 550.00 | .00 | 0.00 | .00 | 0.00 | .00
81 |  | 4C x 6 Sq.mm. | 4C x 6 Sq.mm. | Nos. | 0.000 | .00 | 0.00 | .00 | 500.00 | .00 | 0.00 | .00 | 0.00 | .00
82 |  | 4C x 4 Sq.mm. | 4C x 4 Sq.mm. | Nos. | 0.000 | .00 | 0.00 | .00 | 475.00 | .00 | 0.00 | .00 | 0.00 | .00
83 |  | 4C x 2.5 Sq.mm. | 4C x 2.5 Sq.mm. | Nos. | 0.000 | .00 | 0.00 | .00 | 300.00 | .00 | 0.00 | .00 | 0.00 | .00
84 |  | 3C x 6 Sq.mm. | 3C x 6 Sq.mm. | Nos. | 0.000 | .00 | 0.00 | .00 | 475.00 | .00 | 0.00 | .00 | 0.00 | .00
85 |  | 3C x 4 Sq.mm. | 3C x 4 Sq.mm. | Nos. | 0.000 | .00 | 0.00 | .00 | 400.00 | .00 | 0.00 | .00 | 0.00 | .00
86 |  | 3C x 2.5 Sq.mm. | 3C x 2.5 Sq.mm. | Nos. | 0.000 | .00 | 0.00 | .00 | 300.00 | .00 | 0.00 | .00 | 0.00 | .00
87 |  | Flexible cable | Flexible cable
88 |  | 4C x 6 Sq.mm. | 4C x 6 Sq.mm. | Nos. | 0.000 | .00 | 0.00 | .00 | 750.00 | .00 | 0.00 | .00 | 0.00 | .00
89 |  | 4C x 4 Sq.mm. | 4C x 4 Sq.mm. | Nos. | 0.000 | .00 | 0.00 | .00 | 700.00 | .00 | 0.00 | .00 | 0.00 | .00
90 |  | 3C x 4 Sq.mm. | 3C x 4 Sq.mm. | Nos. | 0.000 | .00 | 0.00 | .00 | 650.00 | .00 | 0.00 | .00 | 0.00 | .00
91 |  | 3C x 2.5 Sq.mm. (Lighting) | 3C x 2.5 Sq.mm. (Lighting) | Nos. | 0.000 | .00 | 0.00 | .00 | 350.00 | .00 | 0.00 | .00 | 0.00 | .00
92 |  | 2C x 2.5 Sq.mm. | 2C x 2.5 Sq.mm. | Nos. | 0.000 | .00 | 0.00 | .00 | 300.00 | .00 | 0.00 | .00 | 0.00 | .00
93 |  | RACEWAYS AND CABLE TRAYS | RACEWAYS AND CABLE TRAYS
94 |  | TRUNKING Fabricating supplying to site of installation, installation on ceiling surface 1.6 mm thick G.I. Trunking of height 50 mm and 2.0 mm thick openable cover, totally enclosed, the joints between two lengths of channels or between channel and | TRUNKING Fabricating supplying to site of installation, installation on ceiling surface 1.6 mm thick G.I. Trunking of height 50 mm and 2.0 mm thick openable cover, totally enclosed, the joints between two lengths of channels or between channel and
95 |  | 100 mm (wide) x 100 mm (height) | 100 mm (wide) x 100 mm (height) | Mtr. | 0.000 | .00 | 0.00 | .00 | 860.00 | .00 | 0.00 | .00 | 0.00 | .00
96 |  | 50 mm (wide) x 50 mm (height) | 50 mm (wide) x 50 mm (height) | Mtr. | 0.000 | .00 | 0.00 | .00 | 475.00 | .00 | 0.00 | .00 | 0.00 | .00
97 |  | RACEWAY Fabricating, supplying to site of installation, installation in the floor before the flooring from 2 mm thick pregalvanised MS CRCA sheet, totally enclosed, height 40 mm . The two lengths of raceways shall be fitted with Collars , 50 mm wide, 3 m | RACEWAY Fabricating, supplying to site of installation, installation in the floor before the flooring from 2 mm thick pregalvanised MS CRCA sheet, totally enclosed, height 40 mm . The two lengths of raceways shall be fitted with Collars , 50 mm wide, 3 m
98 |  | 100 mm (wide) x 40 mm (height) | 100 mm (wide) x 40 mm (height) | Mtr. | 0.000 | .00 | 0.00 | .00 | 550.00 | .00 | 0.00 | .00 | 0.00 | .00
99 |  | 65 mm (wide) x 40 mm (height) | 65 mm (wide) x 40 mm (height) | Mtr. | 0.000 | .00 | 0.00 | .00 | 350.00 | .00 | 0.00 | .00 | 0.00 | .00
100 |  | JUNCTION BOXES Fabricating supplying to site of installation, Junction boxes made from 2 mm thick pregalvanised sheet, with 3.0 mm thick pregalvanised cover including providing neoprene gaskets between the cover and the junction box, cadmium plated fla | JUNCTION BOXES Fabricating supplying to site of installation, Junction boxes made from 2 mm thick pregalvanised sheet, with 3.0 mm thick pregalvanised cover including providing neoprene gaskets between the cover and the junction box, cadmium plated fla
101 |  | (variation in height may be considered for quoting as floor thickness may vary) | (variation in height may be considered for quoting as floor thickness may vary)
102 |  | 250 mm x 250 x 60 50 mm (height) | 250 mm x 250 x 60 50 mm (height) | Mtr. | 0.000 | .00 | 0.00 | .00 | 1550.00 | .00 | 0.00 | .00 | 0.00 | .00
103 |  | 150 mm x 150 x 60 50 mm (height) | 150 mm x 150 x 60 50 mm (height) | Mtr. | 0.000 | .00 | 0.00 | .00 | 1000.00 | .00 | 0.00 | .00 | 0.00 | .00
104 |  | 100 mm x 150 x 60 50 mm (height) | 100 mm x 150 x 60 50 mm (height) | Mtr. | 0.000 | .00 | 0.00 | .00 | 750.00 | .00 | 0.00 | .00 | 0.00 | .00
105 |  | CABLE TRAY Design manufacture , supply and fixing in position the cable trays of the following sizes for supporting 1.1 KV grade armoured unarmoured aluminium copper conductor cables. Fabricate the cable trays from perforated 1.6 2mm thick M.S. CRCA she | CABLE TRAY Design manufacture , supply and fixing in position the cable trays of the following sizes for supporting 1.1 KV grade armoured unarmoured aluminium copper conductor cables. Fabricate the cable trays from perforated 1.6 2mm thick M.S. CRCA she
106 |  | 300 mm wide x 50 mm x 2.0 mm thk | 300 mm wide x 50 mm x 2.0 mm thk | Mtr. | 0.000 | .00 | 0.00 | .00 | 800.00 | .00 | 0.00 | .00 | 0.00 | .00
107 |  | 150 mm wide x 50 mm x 2.0 mm thk | 150 mm wide x 50 mm x 2.0 mm thk | Mtr. | 15.000 | 7,500.00 | 500.00 | 7,500.00 | 650.00 | 9,750.00 | 810.00 | 12,150.00 | 800.00 | 12,000.00
108 |  | 100 mm wide x 50 mm x 2.0 mm thk | 100 mm wide x 50 mm x 2.0 mm thk | Mtr. | 0.000 | .00 | 0.00 | .00 | 550.00 | .00 | 0.00 | .00 | 0.00 | .00
109 |  | 50 mm wide x 50 mm x 2.0 mm thk | 50 mm wide x 50 mm x 2.0 mm thk | Mtr. | 0.000 | .00 | 0.00 | .00 | 400.00 | .00 | 0.00 | .00 | 0.00 | .00
110 |  | POINT WIRING | POINT WIRING
111 |  | Point wiring LENGTH from DB to SB or First Light point control be MCB shall be avg. of 15Mtr. of 3C x 2.5 sq mm FRLS PVC insulated stranded copper conductor wires. For SB to SB the length shall be measured in Mtr. | Point wiring LENGTH from DB to SB or First Light point control be MCB shall be avg. of 15Mtr. of 3C x 2.5 sq mm FRLS PVC insulated stranded copper conductor wires. For SB to SB the length shall be measured in Mtr.
112 |  | The secondary Loop point length shall be 10Mtr from Light fixture to light fixture. If secondary point shall be operated from MCB then the length shall be 10 Mtr. | The secondary Loop point length shall be 10Mtr from Light fixture to light fixture. If secondary point shall be operated from MCB then the length shall be 10 Mtr.
113 |  | All sockets to be checked with a Check Plug socket tester for live-neutral reverse, no earth,neutral fault, live earth reverse, neutral earth reverse. | All sockets to be checked with a Check Plug socket tester for live-neutral reverse, no earth,neutral fault, live earth reverse, neutral earth reverse.
114 |  | The Circuit No. and DB no. label shall be provided on all UPS ,RAW sockets and switchboards with label printer. | The Circuit No. and DB no. label shall be provided on all UPS ,RAW sockets and switchboards with label printer.
115 |  | The Length shall be paid as per the actual measurements as per following manner. | The Length shall be paid as per the actual measurements as per following manner.
116 |  | Wiring for the Primary light points with 3C x 2.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in GI conduits in F.ceiling walls ceiling as direc­ted from Distribution Board to Switch Board including providing 6 amps flush type switches, 5 | Wiring for the Primary light points with 3C x 2.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in GI conduits in F.ceiling walls ceiling as direc­ted from Distribution Board to Switch Board including providing 6 amps flush type switches, 5
117 |  | From DB to Normal Switch Board | From DB to Normal Switch Board | Nos. | 8.000 | 5,600.00 | 1100.00 | 8,800.00 | 2800.00 | 22,400.00 | 700.00 | 5,600.00 | 1500.00 | 12,000.00
118 |  | From DB to Emergency Switch Board | From DB to Emergency Switch Board | Nos. | 0.000 | .00 | 0.00 | .00 | 2800.00 | .00 | 0.00 | .00 | 0.00 | .00
119 |  | Wiring for the following light points with 3 x 2.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in GI conduits in F.ceiling walls ceiling as direc­ted including providing 6 amps flush type switches, 5 sided G.I Boxes for housing switc­hes a | Wiring for the following light points with 3 x 2.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in GI conduits in F.ceiling walls ceiling as direc­ted including providing 6 amps flush type switches, 5 sided G.I Boxes for housing switc­hes a
120 |  | First point controlled by one no. 6 amp switch. (upto 10Mtr.) | First point controlled by one no. 6 amp switch. (upto 10Mtr.) | Nos. | 7.000 | 7,700.00 | 1100.00 | 7,700.00 | 2200.00 | 15,400.00 | 1950.00 | 13,650.00 | 1250.00 | 8,750.00
121 |  | First point controlled by one no. 6 amp switch. (upto 20Mtr.) | First point controlled by one no. 6 amp switch. (upto 20Mtr.) | Nos. | 0.000 | .00 | 0.00 | .00 | 4400.00 | .00 | 0.00 | .00 | 0.00 | .00
122 |  | First point controlled by one no. 6 amp switch. For Emergency Light (upto 10Mtr.) | First point controlled by one no. 6 amp switch. For Emergency Light (upto 10Mtr.) | Nos. | 5.000 | 5,500.00 | 1100.00 | 5,500.00 | 2200.00 | 11,000.00 | 1950.00 | 9,750.00 | 1250.00 | 6,250.00
123 |  | First point controlled by one no. 6 amp switch. For Emergency Light (upto 20Mtr.) | First point controlled by one no. 6 amp switch. For Emergency Light (upto 20Mtr.) | Nos. | 0.000 | .00 | 0.00 | .00 | 4400.00 | .00 | 0.00 | .00 | 0.00 | .00
124 |  | Same as item No. 4.2.1 4.2.2 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS PVC insulated copper conductor wire in concealed exposed GI conduit and earthing | Same as item No. 4.2.1 4.2.2 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS PVC insulated copper conductor wire in concealed exposed GI conduit and earthing | Nos. | 10.000 | 9,500.00 | 950.00 | 9,500.00 | 1300.00 | 13,000.00 | 1550.00 | 15,500.00 | 1000.00 | 10,000.00
125 |  | Same as item No. 4.2.3 4.2.4 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS PVC insulated copper conductor wire in concealed exposed GI conduit and earthing For Emergency Light | Same as item No. 4.2.3 4.2.4 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS PVC insulated copper conductor wire in concealed exposed GI conduit and earthing For Emergency Light | Nos. | 6.000 | 5,700.00 | 950.00 | 5,700.00 | 1500.00 | 9,000.00 | 1550.00 | 9,300.00 | 1000.00 | 6,000.00
126 |  | Wiring for the following light points controlled by MCB in DB (Cost of MCB has been taken elsewhere in the tender) with 3C x 2.5 sq. mm FRLS PVC insulated copper conductor wires in concealed exposed GI conduits as called for and earthing. | Wiring for the following light points controlled by MCB in DB (Cost of MCB has been taken elsewhere in the tender) with 3C x 2.5 sq. mm FRLS PVC insulated copper conductor wires in concealed exposed GI conduits as called for and earthing.
127 |  | First point controlled by existing MCB in D.B. | First point controlled by existing MCB in D.B. | Nos. | 0.000 | .00 | 0.00 | .00 | 2200.00 | .00 | 0.00 | .00 | 0.00 | .00
128 |  | First Emergency point controlled by existing MCB in D.B. | First Emergency point controlled by existing MCB in D.B. | Nos. | 0.000 | .00 | 0.00 | .00 | 2200.00 | .00 | 0.00 | .00 | 0.00 | .00
129 |  | Same as item No.4.5.1 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS. insulated copper conductor wire in concealed exposed GI conduit and earthing | Same as item No.4.5.1 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS. insulated copper conductor wire in concealed exposed GI conduit and earthing | Nos. | 0.000 | .00 | 0.00 | .00 | 1100.00 | .00 | 0.00 | .00 | 0.00 | .00
130 |  | Same as item No. 4.5.2 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS. insulated copper conductor wire in concealed exposed M.S. conduit and earthing For Emergency Lighting | Same as item No. 4.5.2 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS. insulated copper conductor wire in concealed exposed M.S. conduit and earthing For Emergency Lighting | Nos. | 0.000 | .00 | 0.00 | .00 | 1100.00 | .00 | 0.00 | .00 | 0.00 | .00
131 |  | Wiring for UPS Raw plug outlets points with 3C x 4 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS 694-1990 with latest amendments, in existing Channels con | Wiring for UPS Raw plug outlets points with 3C x 4 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS 694-1990 with latest amendments, in existing Channels con | Mtr. | 625.000 | 109,375.00 | 450.00 | 281,250.00 | 175.00 | 109,375.00 | 450.00 | 281,250.00 | 375.00 | 234,375.00
132 |  | Wiring for UPS Raw plug outlets points with 4C x 4 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS 694-1990 with latest amendments, in existing Channels con | Wiring for UPS Raw plug outlets points with 4C x 4 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS 694-1990 with latest amendments, in existing Channels con | Mtr. | 150.000 | 26,250.00 | 600.00 | 90,000.00 | 175.00 | 26,250.00 | 485.00 | 72,750.00 | 425.00 | 63,750.00
133 |  | Providing and fixing in position the following GI RIGID conduits including all accessories concealed in F. ceiling wall floor as required including pull boxes with 3mm thick perspex sheet cover plate complete with 1.6 mm dia. G.I. pull wires in the leng | Providing and fixing in position the following GI RIGID conduits including all accessories concealed in F. ceiling wall floor as required including pull boxes with 3mm thick perspex sheet cover plate complete with 1.6 mm dia. G.I. pull wires in the leng
134 |  | 20 mm dia GI Conduit | 20 mm dia GI Conduit | Mtr. | 500.000 | 35,000.00 | 70.00 | 35,000.00 | 175.00 | 87,500.00 | 135.00 | 67,500.00 | 250.00 | 125,000.00
135 |  | 25 mm dia GI Conduit | 25 mm dia GI Conduit | Mtr. | 310.000 | 26,350.00 | 85.00 | 26,350.00 | 195.00 | 60,450.00 | 155.00 | 48,050.00 | 300.50 | 93,155.00
136 |  | Providing and fixing in position the following GI FLEXIBLE conduits including all accessories concealed in F. ceiling wall floor as required including pull boxes with 3mm thick perspex sheet cover plate complete with 1.6 mm dia. G.I. pull wires in the l | Providing and fixing in position the following GI FLEXIBLE conduits including all accessories concealed in F. ceiling wall floor as required including pull boxes with 3mm thick perspex sheet cover plate complete with 1.6 mm dia. G.I. pull wires in the l
137 |  | 20 mm dia GI Conduit | 20 mm dia GI Conduit | Mtr. | 0.000 | .00 | 0.00 | .00 | 200.00 | .00 | 0.00 | .00 | 0.00 | .00
138 |  | 25 mm dia GI Conduit | 25 mm dia GI Conduit | Mtr. | 120.000 | 9,600.00 | 80.00 | 9,600.00 | 220.00 | 26,400.00 | 120.00 | 14,400.00 | 5000.00 | 600,000.00
139 |  | Supply Laying of 2Cx2.5 Sq.mm FRLS Cu Flexible Cable in 25mm dia. GI Conduit for CCTV | Supply Laying of 2Cx2.5 Sq.mm FRLS Cu Flexible Cable in 25mm dia. GI Conduit for CCTV | Mtr. | 60.000 | 6,600.00 | 110.00 | 6,600.00 | 165.00 | 9,900.00 | 150.00 | 9,000.00 | 350.00 | 21,000.00
140 |  | MODULAR SWITCHES | MODULAR SWITCHES
141 |  | Supply, installation, testing commissioning of following types of modular switches, cover plates, 5 sided G.I. Boxes for housing the modular switches earthing complete as required. GI Boxes to have earth pin for body earthing. The Circuit No. and DB n | Supply, installation, testing commissioning of following types of modular switches, cover plates, 5 sided G.I. Boxes for housing the modular switches earthing complete as required. GI Boxes to have earth pin for body earthing. The Circuit No. and DB n
142 |  | 6A One Way Switch | 6A One Way Switch | Nos. | 19.000 | 2,755.00 | 350.00 | 6,650.00 | 145.00 | 2,755.00 | 610.00 | 11,590.00 | 250.00 | 4,750.00
143 |  | 6A 5 pin Socket - 1Nos. 6A Switch - 1Nos. | 6A 5 pin Socket - 1Nos. 6A Switch - 1Nos. | Nos. | 9.000 | 1,890.00 | 400.00 | 3,600.00 | 210.00 | 1,890.00 | 1550.00 | 13,950.00 | 700.00 | 6,300.00
144 |  | 6 16A Socket outlet - 1Nos. 16A Switch - 1Nos.(Raw UPS Power) | 6 16A Socket outlet - 1Nos. 16A Switch - 1Nos.(Raw UPS Power) | Nos. | 25.000 | 8,000.00 | 500.00 | 12,500.00 | 320.00 | 8,000.00 | 1550.00 | 38,750.00 | 750.00 | 18,750.00
145 |  | 5 15 amps Switch Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | 5 15 amps Switch Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | Nos. | 3.000 | 1,500.00 | 500.00 | 1,500.00 | 500.00 | 1,500.00 | 1450.00 | 4,350.00 | 700.00 | 2,100.00
146 |  | 20 Amp 1- Ph Industrial Socket (Metal Clad) | 20 Amp 1- Ph Industrial Socket (Metal Clad) | Nos. | 4.000 | 7,200.00 | 1800.00 | 7,200.00 | 1800.00 | 7,200.00 | 5500.00 | 22,000.00 | 2200.00 | 8,800.00
147 |  | 32 Amp 3- Ph Industrial Socket (Metal Clad) | 32 Amp 3- Ph Industrial Socket (Metal Clad) | Nos. | 4.000 | 15,200.00 | 3800.00 | 15,200.00 | 6000.00 | 24,000.00 | 6500.00 | 26,000.00 | 8000.00 | 32,000.00
148 |  | 20 Amp 1- Ph Electrical Outlet | 20 Amp 1- Ph Electrical Outlet | Nos. | 3.000 | .00 | 1500.00 | 4,500.00 | 1950.00 | 5,850.00 | 3850.00 | 11,550.00 | 0.00 | .00
149 |  | Data Outlet (RJ-45) | Data Outlet (RJ-45) | Nos. | 3.000 | 1,050.00 | 350.00 | 1,050.00 | 2650.00 | 7,950.00 | 1850.00 | 5,550.00 | 7000.00 | 21,000.00
150 |  | Telephone Outlet (RJ-11) | Telephone Outlet (RJ-11) | Nos. | 2.000 | 500.00 | 350.00 | 700.00 | 2500.00 | 5,000.00 | 250.00 | 500.00 | 6500.00 | 13,000.00
151 |  | GENERAL EARTHING | GENERAL EARTHING
152 |  | Supplying and erecting following GI strip used for earthing on wall with necessary MS clamps fixed on wall Cable trays Hume pipes etc. The jointes shall be Bolted Welded. The joints shall be painted with bituminous paint in an approved manner. | Supplying and erecting following GI strip used for earthing on wall with necessary MS clamps fixed on wall Cable trays Hume pipes etc. The jointes shall be Bolted Welded. The joints shall be painted with bituminous paint in an approved manner.
153 |  | 25 x 3 mm | 25 x 3 mm | Mtr. | 0.000 | .00 | 0.00 | .00 | 110.00 | .00 | 0.00 | .00 | 0.00 | .00
154 |  | Supplying and erecting bare Copper conductor of following sizes | Supplying and erecting bare Copper conductor of following sizes
155 |  | 8 SWG | 8 SWG | Mtr. | 35.000 | 1,750.00 | 150.00 | 5,250.00 | 90.00 | 3,150.00 | 250.00 | 8,750.00 | 50.00 | 1,750.00
156 |  | MISCELLANEOUS WORKS | MISCELLANEOUS WORKS
157 |  | Supply fixing in position approved shock treatment chart written in English, Hindi and Local language. These charts shall be framed in wooden frame covered with clear glass. | Supply fixing in position approved shock treatment chart written in English, Hindi and Local language. These charts shall be framed in wooden frame covered with clear glass. | Nos. | 1.000 | 750.00 | 1000.00 | 1,000.00 | 3500.00 | 3,500.00 | 750.00 | 750.00 | 2000.00 | 2,000.00
158 |  | Supply fixing in position the best quality danger notice boards of approved shape size as reqd. by the local Electrical Inspecting Authority written in English, Hindi local language. | Supply fixing in position the best quality danger notice boards of approved shape size as reqd. by the local Electrical Inspecting Authority written in English, Hindi local language. | Nos. | 1.000 | 450.00 | 1000.00 | 1,000.00 | 3500.00 | 3,500.00 | 450.00 | 450.00 | 1000.00 | 1,000.00
159 |  | The contractor to submit all the AS BUILT DRAWINGS after the completion of the project for Electrical ELV Services executed at site. | The contractor to submit all the AS BUILT DRAWINGS after the completion of the project for Electrical ELV Services executed at site. | Part of Tender | 0.000 | .00 | 0.00 | .00 | 10000.00 | .00 | 0.00 | .00 | 0.00 | .00
160 |  | UPS System | UPS System
161 |  | Supply,Installation, testing and commissioning of following type of Online UPS Inverter as per drawings and specifications with all other accessories. | Supply,Installation, testing and commissioning of following type of Online UPS Inverter as per drawings and specifications with all other accessories. | Nos. | 1.000 | 15,000.00 | 15000.00 | 15,000.00 | 45000.00 | 45,000.00 | 35000.00 | 35,000.00 | 25000.00 | 25,000.00
162 |  | Online UPS | Online UPS
163 |  | 1.0 KVA UPS | 1.0 KVA UPS
164 |  | 12V DC 25AH maintenance free batteries for 30 minutes battery backup. | 12V DC 25AH maintenance free batteries for 30 minutes battery backup.
165 |  | Input supply voltage -230-250 Volts | Input supply voltage -230-250 Volts
166 |  | Output voltage -220-240V+ -1% | Output voltage -220-240V+ -1%
167 |  | Voltage Regulation -Less than or equal to + - 1% | Voltage Regulation -Less than or equal to + - 1%
168 |  | Output frequency -50 Hz + - 0.05 Hz | Output frequency -50 Hz + - 0.05 Hz
169 |  | Type of cooling -Forced air cooled | Type of cooling -Forced air cooled
170 |  | Invertor Efficiency -Better than 85% | Invertor Efficiency -Better than 85%
171 |  | Output Power factor -0.8 | Output Power factor -0.8

## Technical Score Detail
|  | RFQ No: R0443 COST COMPARISON REPORT | RFQ No: R0443 COST COMPARISON REPORT | RFQ No: R0443 COST COMPARISON REPORT | Comp. Date : 05/03/2024 | Comp. Date : 05/03/2024 | Comp. Date : 05/03/2024 | Vendor Name : Red Room Referesh interiors Pvt. Ltd. |  | Vendor Name : KMS INTERIOR |  | Vendor Name : Distint India Enterprises LLP |  | Vendor Name : VYAN VENTURES PRIVATE LIMITED
|  | RFQ No: R0443 COST COMPARISON REPORT | RFQ No: R0443 COST COMPARISON REPORT | RFQ No: R0443 COST COMPARISON REPORT | RFQ #: R0443 | RFQ #: R0443 | RFQ #: R0443 | Contact Name : Jayant |  | Contact Name : Kundan Suthar |  | Contact Name : Sanjay Jain |  | Contact Name : Santosh Kumar/Ved Prakash Pandey
|  | RFQ No: R0443 COST COMPARISON REPORT | RFQ No: R0443 COST COMPARISON REPORT | RFQ No: R0443 COST COMPARISON REPORT | RFQ Date : 05/03/2024 12:44:16 | RFQ Date : 05/03/2024 12:44:16 | RFQ Date : 05/03/2024 12:44:16 | Vendor City : Delhi |  | Vendor City : |  | Vendor City : |  | Vendor City :
|  | RFQ No: R0443 COST COMPARISON REPORT | RFQ No: R0443 COST COMPARISON REPORT | RFQ No: R0443 COST COMPARISON REPORT | BCD Date : | BCD Date : | BCD Date : | Telephone # : 9999984384 |  | Telephone # : |  | Telephone # : |  | Telephone # :
|  | RFQ No: R0443 COST COMPARISON REPORT | RFQ No: R0443 COST COMPARISON REPORT | RFQ No: R0443 COST COMPARISON REPORT |  |  |  | Mobile # : 9999984384 |  | Mobile # : |  | Mobile # : 98102 60645 |  | Mobile # :
PR Number : TFS-2324-00039 | PR Number : TFS-2324-00039 | PR Number : TFS-2324-00039 | PR Number : TFS-2324-00039 | PR Number : TFS-2324-00039 | PR Number : TFS-2324-00039 | PR Number : TFS-2324-00039 | PR Number : TFS-2324-00039 | Email : info.rrrinteriors@gmail.com |  | Email : pravin.takle@kapcocatering.com |  | Email : di.sanjayjain@gmail.com |  | Email : vyanventures01@gmail.com
Package / RFQ Name : ELECTRICAL WORK FOR BIKANERVALA | Package / RFQ Name : ELECTRICAL WORK FOR BIKANERVALA | Package / RFQ Name : ELECTRICAL WORK FOR BIKANERVALA | Package / RFQ Name : ELECTRICAL WORK FOR BIKANERVALA | Package / RFQ Name : ELECTRICAL WORK FOR BIKANERVALA | Package / RFQ Name : ELECTRICAL WORK FOR BIKANERVALA | Package / RFQ Name : ELECTRICAL WORK FOR BIKANERVALA | Package / RFQ Name : ELECTRICAL WORK FOR BIKANERVALA | Round # : 2 (Auction) |  | Round # : 2 (Auction) |  | Round # : 2 (Auction) |  | Round # : 2 (Auction)
Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Quotation Date : |  | Quotation Date : |  | Quotation Date : |  | Quotation Date :
Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Currency :INR | Currency :INR | Currency :INR | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date :
Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | BUDGET PRICE : | .00 |  | Quote Currency : |  | Quote Currency : |  | Quote Currency : |  | Quote Currency :
# | Item Code | Item Description | Last PO Details | Unit | Qty | Last PO Unit Rate | Last PO Total Value | Score | Justification | Score | Justification | Score | Justification | Score | Justification
1 |  | ELECTRICAL WORK FOR BIKANERVALA |  | LOT | 1.000 | 0.00 | 0.00
2 |  | PANELS, SWITCHGEARS DISTRIBUTION BOARD |  |  | 0.000 | 0.00 | 0.00
3 |  | MAIN PANEL-1 |  | Nos. | 1.000 | 0.00 | 0.00
4 |  | Incomer 100 AMPS 4P MCCB, 25kA with TM Based O C SC Release. |  |  | 0.000 | 0.00 | 0.00
5 |  | Meter Protection ELR with CBCT; 100 5A, 15VA, CL-1 CT s -3 Nos. for Schneider make Digital Load Manager (EM 6400 NG) |  |  | 0.000 | 0.00 | 0.00
6 |  | Indication Phase indicating lamps with 6A MCB |  |  | 0.000 | 0.00 | 0.00
7 |  | Busbar 125A TPN Cu Busbar |  |  | 0.000 | 0.00 | 0.00
8 |  | Outgoings |  |  | 0.000 | 0.00 | 0.00
9 |  | a) 63A 4P MCCB, 16kA, TM BASED-1 Nos. |  |  | 0.000 | 0.00 | 0.00
10 |  | b) 40A 4P MCB, 16kA, TM BASED-1 Nos. |  |  | 0.000 | 0.00 | 0.00
11 |  | c) 32A DP MCB, 10kA, TM BASED-5 Nos. |  |  | 0.000 | 0.00 | 0.00
12 |  | d) 16-25A DP MCB, 10kA, -15 Nos. |  |  | 0.000 | 0.00 | 0.00
13 |  | e) 6-16A SP MCB, 10kA, -20 Nos. |  |  | 0.000 | 0.00 | 0.00
14 |  | f) 32A 4P MCCB 16kA TM Based Releases with 1.5 kW DOL Starter, Phase Indicating lamps, ON OFF TRIP Indication, ON OFF Push Button-1 Nos. |  |  | 0.000 | 0.00 | 0.00
15 |  | MAIN PANEL-2 |  | Nos. | 0.000 | 0.00 | 0.00
16 |  | Incomer 40 AMPS 4P MCCB, 25kA with TM Based O C SC Release. |  |  | 0.000 | 0.00 | 0.00
17 |  | Meter Protection ELR with CBCT; 40 5A, 15VA, CL-1 CT s -3 Nos. for Schneider make Digital Load Manager (EM 6400 NG) |  |  | 0.000 | 0.00 | 0.00
18 |  | Indication Phase indicating lamps with 6A MCB |  |  | 0.000 | 0.00 | 0.00
19 |  | Busbar 75A TPN Cu Busbar |  |  | 0.000 | 0.00 | 0.00
20 |  | Outgoings |  |  | 0.000 | 0.00 | 0.00
21 |  | a) 32A 4P MCB, 10kA-1 Nos. |  |  | 0.000 | 0.00 | 0.00
22 |  | b) 25A 4P MCB, 10kA-1 Nos. |  |  | 0.000 | 0.00 | 0.00
23 |  | c) 32A DP MCB, 10kA-1 Nos. |  |  | 0.000 | 0.00 | 0.00
24 |  | d) 40A DP MCB, 10kA-1 Nos. |  |  | 0.000 | 0.00 | 0.00
25 |  | SWITCHGEARS DISTRIBUTION BOARD |  |  | 0.000 | 0.00 | 0.00
26 |  | Supplying installing at site in positioning, connecting, testing and commissioning of the following type Distribution Boards Switchgears. (IP-43) ACRY DB |  |  | 0.000 | 0.00 | 0.00
27 |  | Provide insulated dedicated earth link for UPS DB |  |  | 0.000 | 0.00 | 0.00
28 |  | All MCB s for UPS shall be D Curve, C Curve for Power B Curve for Lighting. |  |  | 0.000 | 0.00 | 0.00
29 |  | SWITCHGEARS |  |  | 0.000 | 0.00 | 0.00
30 |  | Supply, installation, testing and commissioning of sheet metal enclosures for the following switchgears. |  |  | 0.000 | 0.00 | 0.00
31 |  | 63 40 32 20 amps 4P MCB C TYPE with complete with all mounting accessories – for Indoor Legrand make |  | Nos. | 0.000 | 0.00 | 0.00
32 |  | 63 40 32 20 amps DP MCB C TYPE with complete with all mounting accessories – IP-65 |  |  | 0.000 | 0.00 | 0.00
33 |  | 32 amps 4P MCB with 32A 5 Pin Ray Roll Socket complete with all mounting accessories waterproof (IP-65) for Kitchen |  | Nos. | 0.000 | 0.00 | 0.00
34 |  | 25 amps DP MCB with 25A 3 Pin Ray Roll Socket complete with all mounting accessories waterproof (IP-65) for Kitchen |  | Nos. | 0.000 | 0.00 | 0.00
35 |  | 16 amps DP MCB with 15A 3 Pin Ray Roll Socket complete with all mounting accessories waterproof (IP-65) for Kitchen |  | Nos. | 0.000 | 0.00 | 0.00
36 |  | 5 15 amps Switch Socket complete with all mounting accessories waterproof (IP-65) for Kitchen |  | Nos. | 0.000 | 0.00 | 0.00
37 |  | DISTRIBUTION BOARDS |  |  | 0.000 | 0.00 | 0.00
38 |  | 6 WAY SPN DB - UPS DB |  | Nos. | 0.000 | 0.00 | 0.00
39 |  | Incomer 20 AMPS DP MCB 10KA 1 Nos. |  |  | 0.000 | 0.00 | 0.00
40 |  | Outgoings 6 10 16 A SP MCB B Type - 4 Nos. |  |  | 0.000 | 0.00 | 0.00
41 |  | FABRICATED - LPDB |  | Nos. | 0.000 | 0.00 | 0.00
42 |  | Incomer 80A, FP, MCB, 10kA 1 Nos |  |  | 0.000 | 0.00 | 0.00
43 |  | Sub Incomer 63A, DP, RCCB, 100mA 3 Nos |  |  | 0.000 | 0.00 | 0.00
44 |  | Outgoings 10 16 20 25 A SP MCB C Type - 36 Nos. |  |  | 0.000 | 0.00 | 0.00
45 |  | Outgoings 32 A SP MCB C Type - 1 Nos. |  |  | 0.000 | 0.00 | 0.00
46 |  | 12 WAY SPN DB - UPS DB |  | Nos. | 0.000 | 0.00 | 0.00
47 |  | Incomer 32 AMPS DP RCBO 100mA |  |  | 0.000 | 0.00 | 0.00
48 |  | Outgoings 10 16 20 A SP MCB C Type - 6 Nos. |  |  | 0.000 | 0.00 | 0.00
49 |  | MV CABLES |  |  | 0.000 | 0.00 | 0.00
50 |  | POWER CABLING |  |  | 0.000 | 0.00 | 0.00
51 |  | Supply and laying, effecting proper connections, testing commissioning of the following sizes of 1.1 KV XLPE FRLS armoured unarmoured PVC insulated PVC sheathed aluminium copper conductor cables conforming to IS 1554 and IS 694 for Flexible copp |  |  | 0.000 | 0.00 | 0.00
52 |  | Aluminium cables |  |  | 0.000 | 0.00 | 0.00
53 |  | 4C x 50 Sq.mm. |  | Mtr. | 0.000 | 0.00 | 0.00
54 |  | 3.5C x 35 Sq.mm. |  | Mtr. | 0.000 | 0.00 | 0.00
55 |  | 4C x 25 Sq.mm. |  | Mtr. | 20.000 | 0.00 | 0.00
56 |  | - do - but for copper cables |  |  | 0.000 | 0.00 | 0.00
57 |  | 4C x 25 Sq.mm. |  | Mtr. | 0.000 | 0.00 | 0.00
58 |  | 4C x 16 Sq.mm. |  | Mtr. | 0.000 | 0.00 | 0.00
59 |  | 4C x 10 Sq.mm. |  | Mtr. | 0.000 | 0.00 | 0.00
60 |  | 4C x 6 Sq.mm. |  | Mtr. | 0.000 | 0.00 | 0.00
61 |  | 4C x 4 Sq.mm. |  | Mtr. | 0.000 | 0.00 | 0.00
62 |  | 4C x 2.5 Sq.mm. |  | Mtr. | 0.000 | 0.00 | 0.00
63 |  | 3C x 6 Sq.mm. |  | Mtr. | 0.000 | 0.00 | 0.00
64 |  | 3C x 4 Sq.mm. |  | Mtr. | 0.000 | 0.00 | 0.00
65 |  | 3C x 2.5 Sq.mm. |  | Mtr. | 0.000 | 0.00 | 0.00
66 |  | CU Flexible Cables |  |  | 0.000 | 0.00 | 0.00
67 |  | 4C x 6 Sq.mm. |  | Mtr. | 0.000 | 0.00 | 0.00
68 |  | 4C x 4 Sq.mm. |  | Mtr. | 0.000 | 0.00 | 0.00
69 |  | 3C x 4 Sq.mm. |  | Mtr. | 0.000 | 0.00 | 0.00
70 |  | 3C x 2.5 Sq.mm. |  | Mtr. | 0.000 | 0.00 | 0.00
71 |  | 2C x 2.5 Sq.mm. for Earthing |  | Mtr. | 0.000 | 0.00 | 0.00
72 |  | , - do - but for copper flexible cables |  |  | 0.000 | 0.00 | 0.00
73 |  | 1c x 4 Sq.mm PVC insulated PVC flexible copper conductor cables alongwith termination (GREEN COLOUR) |  | Mtr. | 0.000 | 0.00 | 0.00
74 |  | TOTAL FOR POWER CABLES |  |  | 0.000 | 0.00 | 0.00
75 |  | CABLE TERMINATION |  |  | 0.000 | 0.00 | 0.00
76 |  | Making cable and terminations including brass single compression glands and crimping type copper lugs for cable sizes mentioned below for aluminium or copper. |  |  | 0.000 | 0.00 | 0.00
77 |  | 4C x 50 Sq.mm. AL |  | Nos. | 0.000 | 0.00 | 0.00
78 |  | 3.5C x 35 Sq.mm. |  | Nos. | 0.000 | 0.00 | 0.00
79 |  | 4C x 25 Sq.mm. |  | Nos. | 2.000 | 0.00 | 0.00
80 |  | 4C x 16 Sq.mm. CU |  | Nos. | 0.000 | 0.00 | 0.00
81 |  | 4C x 10 Sq.mm. |  | Nos. | 0.000 | 0.00 | 0.00
82 |  | 4C x 6 Sq.mm. |  | Nos. | 0.000 | 0.00 | 0.00
83 |  | 4C x 4 Sq.mm. |  | Nos. | 0.000 | 0.00 | 0.00
84 |  | 4C x 2.5 Sq.mm. |  | Nos. | 0.000 | 0.00 | 0.00
85 |  | 3C x 6 Sq.mm. |  | Nos. | 0.000 | 0.00 | 0.00
86 |  | 3C x 4 Sq.mm. |  | Nos. | 0.000 | 0.00 | 0.00
87 |  | 3C x 2.5 Sq.mm. |  | Nos. | 0.000 | 0.00 | 0.00
88 |  | Flexible cable |  |  | 0.000 | 0.00 | 0.00
89 |  | 4C x 6 Sq.mm. |  | Nos. | 0.000 | 0.00 | 0.00
90 |  | 4C x 4 Sq.mm. |  | Nos. | 0.000 | 0.00 | 0.00
91 |  | 3C x 4 Sq.mm. |  | Nos. | 0.000 | 0.00 | 0.00
92 |  | 3C x 2.5 Sq.mm. (Lighting) |  | Nos. | 0.000 | 0.00 | 0.00
93 |  | 2C x 2.5 Sq.mm. |  | Nos. | 0.000 | 0.00 | 0.00
94 |  | RACEWAYS AND CABLE TRAYS |  |  | 0.000 | 0.00 | 0.00
95 |  | TRUNKING Fabricating supplying to site of installation, installation on ceiling surface 1.6 mm thick G.I. Trunking of height 50 mm and 2.0 mm thick openable cover, totally enclosed, the joints between two lengths of channels or between channel and |  |  | 0.000 | 0.00 | 0.00
96 |  | 100 mm (wide) x 100 mm (height) |  | Mtr. | 0.000 | 0.00 | 0.00
97 |  | 50 mm (wide) x 50 mm (height) |  | Mtr. | 0.000 | 0.00 | 0.00
98 |  | RACEWAY Fabricating, supplying to site of installation, installation in the floor before the flooring from 2 mm thick pregalvanised MS CRCA sheet, totally enclosed, height 40 mm . The two lengths of raceways shall be fitted with Collars , 50 mm wide, 3 m |  |  | 0.000 | 0.00 | 0.00
99 |  | 100 mm (wide) x 40 mm (height) |  | Mtr. | 0.000 | 0.00 | 0.00
100 |  | 65 mm (wide) x 40 mm (height) |  | Mtr. | 0.000 | 0.00 | 0.00
101 |  | JUNCTION BOXES Fabricating supplying to site of installation, Junction boxes made from 2 mm thick pregalvanised sheet, with 3.0 mm thick pregalvanised cover including providing neoprene gaskets between the cover and the junction box, cadmium plated fla |  |  | 0.000 | 0.00 | 0.00
102 |  | (variation in height may be considered for quoting as floor thickness may vary) |  |  | 0.000 | 0.00 | 0.00
103 |  | 250 mm x 250 x 60 50 mm (height) |  | Mtr. | 0.000 | 0.00 | 0.00
104 |  | 150 mm x 150 x 60 50 mm (height) |  | Mtr. | 0.000 | 0.00 | 0.00
105 |  | 100 mm x 150 x 60 50 mm (height) |  | Mtr. | 0.000 | 0.00 | 0.00
106 |  | CABLE TRAY Design manufacture , supply and fixing in position the cable trays of the following sizes for supporting 1.1 KV grade armoured unarmoured aluminium copper conductor cables. Fabricate the cable trays from perforated 1.6 2mm thick M.S. CRCA she |  |  | 0.000 | 0.00 | 0.00
107 |  | 300 mm wide x 50 mm x 2.0 mm thk |  | Mtr. | 0.000 | 0.00 | 0.00
108 |  | 150 mm wide x 50 mm x 2.0 mm thk |  | Mtr. | 15.000 | 0.00 | 0.00
109 |  | 100 mm wide x 50 mm x 2.0 mm thk |  | Mtr. | 0.000 | 0.00 | 0.00
110 |  | 50 mm wide x 50 mm x 2.0 mm thk |  | Mtr. | 0.000 | 0.00 | 0.00
111 |  | POINT WIRING |  |  | 0.000 | 0.00 | 0.00
112 |  | Point wiring LENGTH from DB to SB or First Light point control be MCB shall be avg. of 15Mtr. of 3C x 2.5 sq mm FRLS PVC insulated stranded copper conductor wires. For SB to SB the length shall be measured in Mtr. |  |  | 0.000 | 0.00 | 0.00
113 |  | The secondary Loop point length shall be 10Mtr from Light fixture to light fixture. If secondary point shall be operated from MCB then the length shall be 10 Mtr. |  |  | 0.000 | 0.00 | 0.00
114 |  | All sockets to be checked with a Check Plug socket tester for live-neutral reverse, no earth,neutral fault, live earth reverse, neutral earth reverse. |  |  | 0.000 | 0.00 | 0.00
115 |  | The Circuit No. and DB no. label shall be provided on all UPS ,RAW sockets and switchboards with label printer. |  |  | 0.000 | 0.00 | 0.00
116 |  | The Length shall be paid as per the actual measurements as per following manner. |  |  | 0.000 | 0.00 | 0.00
117 |  | Wiring for the Primary light points with 3C x 2.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in GI conduits in F.ceiling walls ceiling as direc­ted from Distribution Board to Switch Board including providing 6 amps flush type switches, 5 |  |  | 0.000 | 0.00 | 0.00
118 |  | From DB to Normal Switch Board |  | Nos. | 8.000 | 0.00 | 0.00
119 |  | From DB to Emergency Switch Board |  | Nos. | 0.000 | 0.00 | 0.00
120 |  | Wiring for the following light points with 3 x 2.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in GI conduits in F.ceiling walls ceiling as direc­ted including providing 6 amps flush type switches, 5 sided G.I Boxes for housing switc­hes a |  |  | 0.000 | 0.00 | 0.00
121 |  | First point controlled by one no. 6 amp switch. (upto 10Mtr.) |  | Nos. | 7.000 | 0.00 | 0.00
122 |  | First point controlled by one no. 6 amp switch. (upto 20Mtr.) |  | Nos. | 0.000 | 0.00 | 0.00
123 |  | First point controlled by one no. 6 amp switch. For Emergency Light (upto 10Mtr.) |  | Nos. | 5.000 | 0.00 | 0.00
124 |  | First point controlled by one no. 6 amp switch. For Emergency Light (upto 20Mtr.) |  | Nos. | 0.000 | 0.00 | 0.00
125 |  | Same as item No. 4.2.1 4.2.2 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS PVC insulated copper conductor wire in concealed exposed GI conduit and earthing |  | Nos. | 10.000 | 0.00 | 0.00
126 |  | Same as item No. 4.2.3 4.2.4 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS PVC insulated copper conductor wire in concealed exposed GI conduit and earthing For Emergency Light |  | Nos. | 6.000 | 0.00 | 0.00
127 |  | Wiring for the following light points controlled by MCB in DB (Cost of MCB has been taken elsewhere in the tender) with 3C x 2.5 sq. mm FRLS PVC insulated copper conductor wires in concealed exposed GI conduits as called for and earthing. |  |  | 0.000 | 0.00 | 0.00
128 |  | First point controlled by existing MCB in D.B. |  | Nos. | 0.000 | 0.00 | 0.00
129 |  | First Emergency point controlled by existing MCB in D.B. |  | Nos. | 0.000 | 0.00 | 0.00
130 |  | Same as item No.4.5.1 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS. insulated copper conductor wire in concealed exposed GI conduit and earthing |  | Nos. | 0.000 | 0.00 | 0.00
131 |  | Same as item No. 4.5.2 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS. insulated copper conductor wire in concealed exposed M.S. conduit and earthing For Emergency Lighting |  | Nos. | 0.000 | 0.00 | 0.00
132 |  | Wiring for UPS Raw plug outlets points with 3C x 4 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS 694-1990 with latest amendments, in existing Channels con |  | Mtr. | 625.000 | 0.00 | 0.00
133 |  | Wiring for UPS Raw plug outlets points with 4C x 4 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS 694-1990 with latest amendments, in existing Channels con |  | Mtr. | 150.000 | 0.00 | 0.00
134 |  | Providing and fixing in position the following GI RIGID conduits including all accessories concealed in F. ceiling wall floor as required including pull boxes with 3mm thick perspex sheet cover plate complete with 1.6 mm dia. G.I. pull wires in the leng |  |  | 0.000 | 0.00 | 0.00
135 |  | 20 mm dia GI Conduit |  | Mtr. | 500.000 | 0.00 | 0.00
136 |  | 25 mm dia GI Conduit |  | Mtr. | 310.000 | 0.00 | 0.00
137 |  | Providing and fixing in position the following GI FLEXIBLE conduits including all accessories concealed in F. ceiling wall floor as required including pull boxes with 3mm thick perspex sheet cover plate complete with 1.6 mm dia. G.I. pull wires in the l |  |  | 0.000 | 0.00 | 0.00
138 |  | 20 mm dia GI Conduit |  | Mtr. | 0.000 | 0.00 | 0.00
139 |  | 25 mm dia GI Conduit |  | Mtr. | 120.000 | 0.00 | 0.00
140 |  | Supply Laying of 2Cx2.5 Sq.mm FRLS Cu Flexible Cable in 25mm dia. GI Conduit for CCTV |  | Mtr. | 60.000 | 0.00 | 0.00
141 |  | MODULAR SWITCHES |  |  | 0.000 | 0.00 | 0.00
142 |  | Supply, installation, testing commissioning of following types of modular switches, cover plates, 5 sided G.I. Boxes for housing the modular switches earthing complete as required. GI Boxes to have earth pin for body earthing. The Circuit No. and DB n |  |  | 0.000 | 0.00 | 0.00
143 |  | 6A One Way Switch |  | Nos. | 19.000 | 0.00 | 0.00
144 |  | 6A 5 pin Socket - 1Nos. 6A Switch - 1Nos. |  | Nos. | 9.000 | 0.00 | 0.00
145 |  | 6 16A Socket outlet - 1Nos. 16A Switch - 1Nos.(Raw UPS Power) |  | Nos. | 25.000 | 0.00 | 0.00
146 |  | 5 15 amps Switch Socket complete with all mounting accessories waterproof (IP-65) for Kitchen |  | Nos. | 3.000 | 0.00 | 0.00
147 |  | 20 Amp 1- Ph Industrial Socket (Metal Clad) |  | Nos. | 4.000 | 0.00 | 0.00
148 |  | 32 Amp 3- Ph Industrial Socket (Metal Clad) |  | Nos. | 4.000 | 0.00 | 0.00
149 |  | 20 Amp 1- Ph Electrical Outlet |  | Nos. | 3.000 | 0.00 | 0.00
150 |  | Data Outlet (RJ-45) |  | Nos. | 3.000 | 0.00 | 0.00
151 |  | Telephone Outlet (RJ-11) |  | Nos. | 2.000 | 0.00 | 0.00
152 |  | GENERAL EARTHING |  |  | 0.000 | 0.00 | 0.00
153 |  | Supplying and erecting following GI strip used for earthing on wall with necessary MS clamps fixed on wall Cable trays Hume pipes etc. The jointes shall be Bolted Welded. The joints shall be painted with bituminous paint in an approved manner. |  |  | 0.000 | 0.00 | 0.00
154 |  | 25 x 3 mm |  | Mtr. | 0.000 | 0.00 | 0.00
155 |  | Supplying and erecting bare Copper conductor of following sizes |  |  | 0.000 | 0.00 | 0.00
156 |  | 8 SWG |  | Mtr. | 35.000 | 0.00 | 0.00
157 |  | MISCELLANEOUS WORKS |  |  | 0.000 | 0.00 | 0.00
158 |  | Supply fixing in position approved shock treatment chart written in English, Hindi and Local language. These charts shall be framed in wooden frame covered with clear glass. |  | Nos. | 1.000 | 0.00 | 0.00
159 |  | Supply fixing in position the best quality danger notice boards of approved shape size as reqd. by the local Electrical Inspecting Authority written in English, Hindi local language. |  | Nos. | 1.000 | 0.00 | 0.00
160 |  | The contractor to submit all the AS BUILT DRAWINGS after the completion of the project for Electrical ELV Services executed at site. |  | Part of Tender | 0.000 | 0.00 | 0.00
161 |  | UPS System |  |  | 0.000 | 0.00 | 0.00
162 |  | Supply,Installation, testing and commissioning of following type of Online UPS Inverter as per drawings and specifications with all other accessories. |  | Nos. | 1.000 | 0.00 | 0.00
163 |  | Online UPS |  |  | 0.000 | 0.00 | 0.00
164 |  | 1.0 KVA UPS |  |  | 0.000 | 0.00 | 0.00
165 |  | 12V DC 25AH maintenance free batteries for 30 minutes battery backup. |  |  | 0.000 | 0.00 | 0.00
166 |  | Input supply voltage -230-250 Volts |  |  | 0.000 | 0.00 | 0.00
167 |  | Output voltage -220-240V+ -1% |  |  | 0.000 | 0.00 | 0.00
168 |  | Voltage Regulation -Less than or equal to + - 1% |  |  | 0.000 | 0.00 | 0.00
169 |  | Output frequency -50 Hz + - 0.05 Hz |  |  | 0.000 | 0.00 | 0.00
170 |  | Type of cooling -Forced air cooled |  |  | 0.000 | 0.00 | 0.00
171 |  | Invertor Efficiency -Better than 85% |  |  | 0.000 | 0.00 | 0.00
172 |  | Output Power factor -0.8 |  |  | 0.000 | 0.00 | 0.00