## Price Comparison
|  | RFQ No: R0665 COST COMPARISON REPORT | RFQ No: R0665 COST COMPARISON REPORT | RFQ No: R0665 COST COMPARISON REPORT | Comp. Date : 28/03/2024 | Comp. Date : 28/03/2024 | Comp. Date : 28/03/2024 | Vendor Name : Pioneer Infra And Turnkey Solutions (RV232417609)
|  | RFQ No: R0665 COST COMPARISON REPORT | RFQ No: R0665 COST COMPARISON REPORT | RFQ No: R0665 COST COMPARISON REPORT | RFQ #: R0665 | RFQ #: R0665 | RFQ #: R0665 | Contact Name : Pankaj Upadhyay/Bipin Upadhyay
|  | RFQ No: R0665 COST COMPARISON REPORT | RFQ No: R0665 COST COMPARISON REPORT | RFQ No: R0665 COST COMPARISON REPORT | RFQ Date : 27/03/2024 17:37:48 | RFQ Date : 27/03/2024 17:37:48 | RFQ Date : 27/03/2024 17:37:48 | Vendor City :
|  | RFQ No: R0665 COST COMPARISON REPORT | RFQ No: R0665 COST COMPARISON REPORT | RFQ No: R0665 COST COMPARISON REPORT | BCD Date : 28/03/2024 16:20:00 | BCD Date : 28/03/2024 16:20:00 | BCD Date : 28/03/2024 16:20:00 | Telephone # :
|  | RFQ No: R0665 COST COMPARISON REPORT | RFQ No: R0665 COST COMPARISON REPORT | RFQ No: R0665 COST COMPARISON REPORT |  |  |  | Mobile # :
PR Number : Semolina-2324-00622 | PR Number : Semolina-2324-00622 | PR Number : Semolina-2324-00622 | PR Number : Semolina-2324-00622 | PR Number : Semolina-2324-00622 | PR Number : Semolina-2324-00622 | PR Number : Semolina-2324-00622 | PR Number : Semolina-2324-00622 | Email : bipinu@pioneerindinfra.com
Package / RFQ Name : PR for Electrical Work for Lucknow T3 Budweiser bar... | Package / RFQ Name : PR for Electrical Work for Lucknow T3 Budweiser bar... | Package / RFQ Name : PR for Electrical Work for Lucknow T3 Budweiser bar... | Package / RFQ Name : PR for Electrical Work for Lucknow T3 Budweiser bar... | Package / RFQ Name : PR for Electrical Work for Lucknow T3 Budweiser bar... | Package / RFQ Name : PR for Electrical Work for Lucknow T3 Budweiser bar... | Package / RFQ Name : PR for Electrical Work for Lucknow T3 Budweiser bar... | Package / RFQ Name : PR for Electrical Work for Lucknow T3 Budweiser bar... | Round # : 3 (RFQ)
Buyer : Sarvesh Patil / Technical : / Approver : | Buyer : Sarvesh Patil / Technical : / Approver : | Buyer : Sarvesh Patil / Technical : / Approver : | Buyer : Sarvesh Patil / Technical : / Approver : | Buyer : Sarvesh Patil / Technical : / Approver : | Buyer : Sarvesh Patil / Technical : / Approver : | Buyer : Sarvesh Patil / Technical : / Approver : | Buyer : Sarvesh Patil / Technical : / Approver : | Quotation Date : |  |  | Quotation Validity Date :
Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Currency :INR | Currency :INR | Currency :INR | Buyer Remark : .
Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | BUDGET PRICE : | .00 |  | Quote Currency : INR
# | Item Code | Item Description | Unit | Qty | Last PO Details | Lowest Unit Rate | Lowest Vendor | First Bid | Disc % | GST % | Technical | Unit Price | Total
1 |  | Electrical Work | no | 1.00 |  | 1162600.00 | Pioneer Infra And Turnkey Solutions | 1218050.00 | 0.00 | 18.00 |  | 1,162,600.00 | 1,162,600.00
Item Total | [8 empty] | .00 | 209,268.00 |  |  | 1,162,600.00
Discount Total Value | [7 empty] | Grand Dis. Amt | .00 |  |  |  | .00
GST Total Amount | [12 empty] | 209,268.00
Net Landed Cost | [11 empty] | INR | 1,371,868.00
Vendor Status | [7 empty] | Round # : 3 (RFQ) | Round # : 3 (RFQ)
Sr No. | Vendor Code | Vendor Name | [5 empty] | Status | Remarks
1 | RV232417609 | Pioneer Infra And Turnkey Solutions | [5 empty] | Participate

## BOQ Price Bid
|  | RFQ No: R0665 COST COMPARISON REPORT | RFQ No: R0665 COST COMPARISON REPORT | Comp. Date : 28/03/2024 | Comp. Date : 28/03/2024 | Comp. Date : 28/03/2024 | Vendor Name : Pioneer Infra And Turnkey Solutions | Vendor Name : Pioneer Infra And Turnkey Solutions
|  | RFQ No: R0665 COST COMPARISON REPORT | RFQ No: R0665 COST COMPARISON REPORT | RFQ #: R0665 | RFQ #: R0665 | RFQ #: R0665 | Contact Name : Pankaj Upadhyay/Bipin Upadhyay | Contact Name : Pankaj Upadhyay/Bipin Upadhyay
|  | RFQ No: R0665 COST COMPARISON REPORT | RFQ No: R0665 COST COMPARISON REPORT | RFQ Date : 27/03/2024 17:37:48 | RFQ Date : 27/03/2024 17:37:48 | RFQ Date : 27/03/2024 17:37:48 | Vendor City : | Vendor City :
|  | RFQ No: R0665 COST COMPARISON REPORT | RFQ No: R0665 COST COMPARISON REPORT | BCD Date : 28/03/2024 16:20:00 | BCD Date : 28/03/2024 16:20:00 | BCD Date : 28/03/2024 16:20:00 | Telephone # : | Telephone # :
|  | RFQ No: R0665 COST COMPARISON REPORT | RFQ No: R0665 COST COMPARISON REPORT |  |  |  | Mobile # : | Mobile # :
PR Number : Semolina-2324-00622 | PR Number : Semolina-2324-00622 | PR Number : Semolina-2324-00622 | PR Number : Semolina-2324-00622 | PR Number : Semolina-2324-00622 | PR Number : Semolina-2324-00622 | PR Number : Semolina-2324-00622 | Email : bipinu@pioneerindinfra.com | Email : bipinu@pioneerindinfra.com
Package / RFQ Name : PR for Electrical Work for Lucknow T3 Budweiser bar... | Package / RFQ Name : PR for Electrical Work for Lucknow T3 Budweiser bar... | Package / RFQ Name : PR for Electrical Work for Lucknow T3 Budweiser bar... | Package / RFQ Name : PR for Electrical Work for Lucknow T3 Budweiser bar... | Package / RFQ Name : PR for Electrical Work for Lucknow T3 Budweiser bar... | Package / RFQ Name : PR for Electrical Work for Lucknow T3 Budweiser bar... | Package / RFQ Name : PR for Electrical Work for Lucknow T3 Budweiser bar... | Round # : 3 (RFQ) | Round # : 3 (RFQ)
Buyer : Sarvesh Patil | Buyer : Sarvesh Patil | Buyer : Sarvesh Patil | Buyer : Sarvesh Patil | Buyer : Sarvesh Patil | Buyer : Sarvesh Patil | Buyer : Sarvesh Patil | Techanical Score : | Techanical Score :
Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Currency :INR | Currency :INR | Currency :INR | Quotation Date : | Quotation Date :
Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | BUDGET PRICE :.00 | BUDGET PRICE :.00 | BUDGET PRICE :.00 | Quotation Validity Date : | Quotation Validity Date :
Sr No. | Item Code | Item Name | Item Description | UOM | Qty | Minimum Amount | Unit Price | Amount
1 |  | Electrical Work | Electrical Work BOQ for LKN Budweiser bar | no | 1.000 |  |  | 1,162,600.00
1 |  | Design, fabrication, assembling, wiring , supply , Erection , Installation , testing and commissioning of MDB Panels fabricated out of 2mm thick for structural members (Load bearing members) and 1.6mm thick for door and covers (Non load bearing members) CRCA painted sheet steel in cubicle formation with reinforcement of suitable size angle iron, channels, T irons, flats wherever necessary for large meter boards. Cable gland plates shall be provided at top and bottom both and windows for meter reading, locking arrangement (pad-lock seal) with wiring upto KWH meter meter to MCB shall be done by using adequately rated flexible single core copper wire. The boards shall be treated with all anticorrosive process before painting as per standards with final approved shade of powder coated as approved, 2 nos. earthing terminals shall be provided for all panels. The boards shall be suitable for 415 V, 3 phase, 4 wire, 50 Hz supply system. Boards shall be fabricated in length, height, depth etc to match with site conditions. An approval shall be taken for each panel before manufacturing. Galvanised hardwares with zinc passivation shall be used in fabrication of boards. Note The following provisions shall be required to be made in the switchboard detailed below The Switchboard shall have provision for entry of all PVCA cables from the top bottom as required. All live accessible parts shall be shrouded and all equipment shall be finger touch proof. The busbar insulation shall be with heat shrinkable sleeves. SMC DMC shrouds and busbar supports shall be used. Suitable tinned copper extension links for incoming outgoing cables shall be provided wherever required Control circuits includes breaker control switch, auto manual selector switch, anti pumping relay, spring charging trip indication, TIMER, control wiring, Auxiliary contactors MCB’s as required at site. Positive isolation of all breakers. All fault level breaking capacity indicates shall be ICS value at 415 volts (ICS = ICU = ICW = 100%). Space Heater light air filter shall be provided for each vertical compartment Link and drops from MCCB shall be designed for full rated current of MCCB ratings at same current density as of Main Bus Bar 2 nos. GI earth strip throughout the panel. | Design, fabrication, assembling, wiring , supply , Erection , Installation , testing and commissioning of MDB Panels fabricated out of 2mm thick for structural members (Load bearing members) and 1.6mm thick for door and covers (Non load bearing members) CRCA painted sheet steel in cubicle formation with reinforcement of suitable size angle iron, channels, T irons, flats wherever necessary for large meter boards. Cable gland plates shall be provided at top and bottom both and windows for meter reading, locking arrangement (pad-lock seal) with wiring upto KWH meter meter to MCB shall be done by using adequately rated flexible single core copper wire. The boards shall be treated with all anticorrosive process before painting as per standards with final approved shade of powder coated as approved, 2 nos. earthing terminals shall be provided for all panels. The boards shall be suitable for 415 V, 3 phase, 4 wire, 50 Hz supply system. Boards shall be fabricated in length, height, depth etc to match with site conditions. An approval shall be taken for each panel before manufacturing. Galvanised hardwares with zinc passivation shall be used in fabrication of boards. Note The following provisions shall be required to be made in the switchboard detailed below The Switchboard shall have provision for entry of all PVCA cables from the top bottom as required. All live accessible parts shall be shrouded and all equipment shall be finger touch proof. The busbar insulation shall be with heat shrinkable sleeves. SMC DMC shrouds and busbar supports shall be used. Suitable tinned copper extension links for incoming outgoing cables shall be provided wherever required Control circuits includes breaker control switch, auto manual selector switch, anti pumping relay, spring charging trip indication, TIMER, control wiring, Auxiliary contactors MCB’s as required at site. Positive isolation of all breakers. All fault level breaking capacity indicates shall be ICS value at 415 volts (ICS = ICU = ICW = 100%). Space Heater light air filter shall be provided for each vertical compartment Link and drops from MCCB shall be designed for full rated current of MCCB ratings at same current density as of Main Bus Bar 2 nos. GI earth strip throughout the panel.
2 |  | MAIN MDB Incoming 1 No. 160 amps 25 kA 440 volt FP MCCB with Thermal Magnetic overcurrent and short circuit and with following Metering, Indication Protection 1 Nos. 6 Parameter Multi Function Mater with 3 Nos. Cast Resin CTs and MCBs Breaker ON OFF indication Lamps R-Y-B indication lamps with MCBs ELR with CBCT Bus Bar 200 A, TPN Al. Bus Bar of suitable length having Current density 1Amp sq.mm having high conductivity electrical grade suitable to withstand symmetrical fault level of 25 kA. Neutral busbar shall be of 100% capacity. Outgoings 2 No. 63 amps 4P MCB ( Type C) 2 No. 32 amps 4P MCB ( Type C) 1 No. 25 amps 4P MCB ( Type C) 2 No. 32 amps 2P MCB ( Type C) 1 No. 25 amps 2P MCB ( Type C) 1 No. 40 amps FP MCB + RCCB of 100mA sensitivity. 1 No. 25 amps FP MCB + RCCB of 100mA sensitivity. AHU Starters In Maon Panel 1 Nos. Fully automatic 0.75 KW Motor DOL starter with 16A TP Type C Curve MCB , 9A TP Contactor , ON OFF push buttons and on off Trip indicating lights , A M selector switch for local remote operations, CT operated Digital Ammeter, suitable NO NC Potential free contacts for Interlocking with Fire alarm panel 1.4A -2.3 A O L relay with inbuilt single phase preventor , selector switches etc as required. 1 Nos. Fully automatic 1.5 KW Motor DOL starter with 20A TP Type C Curve MCB , 9A TP Contactor , ON OFF push buttons and on off Trip indicating lights , A M selector switch for local remote operations, CT operated Digital Ammeter, suitable NO NC Potential free contacts for Interlocking with Fire alarm panel 2.5A -4.0 A O L relay with inbuilt single phase preventor , selector switches etc as required. 1 Nos. Fully automatic 2.25 KW Motor DOL starter with 25A TP Type C Curve MCB , 16A TP Contactor , ON OFF push buttons and on off Trip indicating lights , A M selector switch for local remote operations, CT operated Digital Ammeter, suitable NO NC Potential free contacts for Interlocking with Fire alarm panel 4.5A -7.5 A O L relay with inbuilt single phase preventor , selector switches etc as required. Main MDB as described above | MAIN MDB Incoming 1 No. 160 amps 25 kA 440 volt FP MCCB with Thermal Magnetic overcurrent and short circuit and with following Metering, Indication Protection 1 Nos. 6 Parameter Multi Function Mater with 3 Nos. Cast Resin CTs and MCBs Breaker ON OFF indication Lamps R-Y-B indication lamps with MCBs ELR with CBCT Bus Bar 200 A, TPN Al. Bus Bar of suitable length having Current density 1Amp sq.mm having high conductivity electrical grade suitable to withstand symmetrical fault level of 25 kA. Neutral busbar shall be of 100% capacity. Outgoings 2 No. 63 amps 4P MCB ( Type C) 2 No. 32 amps 4P MCB ( Type C) 1 No. 25 amps 4P MCB ( Type C) 2 No. 32 amps 2P MCB ( Type C) 1 No. 25 amps 2P MCB ( Type C) 1 No. 40 amps FP MCB + RCCB of 100mA sensitivity. 1 No. 25 amps FP MCB + RCCB of 100mA sensitivity. AHU Starters In Maon Panel 1 Nos. Fully automatic 0.75 KW Motor DOL starter with 16A TP Type C Curve MCB , 9A TP Contactor , ON OFF push buttons and on off Trip indicating lights , A M selector switch for local remote operations, CT operated Digital Ammeter, suitable NO NC Potential free contacts for Interlocking with Fire alarm panel 1.4A -2.3 A O L relay with inbuilt single phase preventor , selector switches etc as required. 1 Nos. Fully automatic 1.5 KW Motor DOL starter with 20A TP Type C Curve MCB , 9A TP Contactor , ON OFF push buttons and on off Trip indicating lights , A M selector switch for local remote operations, CT operated Digital Ammeter, suitable NO NC Potential free contacts for Interlocking with Fire alarm panel 2.5A -4.0 A O L relay with inbuilt single phase preventor , selector switches etc as required. 1 Nos. Fully automatic 2.25 KW Motor DOL starter with 25A TP Type C Curve MCB , 16A TP Contactor , ON OFF push buttons and on off Trip indicating lights , A M selector switch for local remote operations, CT operated Digital Ammeter, suitable NO NC Potential free contacts for Interlocking with Fire alarm panel 4.5A -7.5 A O L relay with inbuilt single phase preventor , selector switches etc as required. Main MDB as described above | Set | 1.000 | 135,000.00 | 135000.00 | 135,000.00
3 |  | DISTRIBUTION BOARDS - Supply, erection, testing and commissioning of the following sheet steel clad wall recess mounting dust and vermin proof double door type distribution boards constructed from 16 SWG sheet steel IP 42 construction, finished with rust proof duly powder coated in approved shade with hinged gasketed door and housing the following complete with P.V.C. insulated copper busbars rated 200 amp with interconnections, neutral and earth bar assembly per phase, earthing terminals complete as approved by Architects. Note All MCBs in distribuition board for power circuits shall be of C curve | DISTRIBUTION BOARDS - Supply, erection, testing and commissioning of the following sheet steel clad wall recess mounting dust and vermin proof double door type distribution boards constructed from 16 SWG sheet steel IP 42 construction, finished with rust proof duly powder coated in approved shade with hinged gasketed door and housing the following complete with P.V.C. insulated copper busbars rated 200 amp with interconnections, neutral and earth bar assembly per phase, earthing terminals complete as approved by Architects. Note All MCBs in distribuition board for power circuits shall be of C curve
4 |  | Type A - 1-63amp FP MCB with 3 single phase banks each comprising of 63A DP RCCB(100 mA) and 12 nos. 6 16 20 25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. | Type A - 1-63amp FP MCB with 3 single phase banks each comprising of 63A DP RCCB(100 mA) and 12 nos. 6 16 20 25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. | Set | 1.000 | 32,000.00 | 32000.00 | 32,000.00
5 |  | Type B - 1-32amp FP MCB with 3 single phase banks each comprising of 32A DP RCCB(100 mA) and 6 nos. 6 16 20 25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. | Type B - 1-32amp FP MCB with 3 single phase banks each comprising of 32A DP RCCB(100 mA) and 6 nos. 6 16 20 25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. | Set | 1.000 | 14,000.00 | 14000.00 | 14,000.00
6 |  | Type C - 1-32 amp DP MCB + DP RCCB ( 100mA) and 12 nos. 6 16 20 25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. | Type C - 1-32 amp DP MCB + DP RCCB ( 100mA) and 12 nos. 6 16 20 25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. | Set | 1.000 | 15,000.00 | 15000.00 | 15,000.00
7 |  | Type D - 1-32 amp DP MCB + DP RCCB ( 100mA) and 8 nos. 6 16 20 25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. | Type D - 1-32 amp DP MCB + DP RCCB ( 100mA) and 8 nos. 6 16 20 25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. | Set | 1.000 | 14,000.00 | 14000.00 | 14,000.00
8 |  | Supply installation testing and commisioning 3.0 kVA online ( 1ph input and 1ph output) UPS with 15 Min power back up complete with in buit Static by pass switch , Mannual external maintenance by pass switch , Rectifiers , Sealed MF batteries etc as required | Supply installation testing and commisioning 3.0 kVA online ( 1ph input and 1ph output) UPS with 15 Min power back up complete with in buit Static by pass switch , Mannual external maintenance by pass switch , Rectifiers , Sealed MF batteries etc as required | No. | 1.000 | 58,000.00 | 58000.00 | 58,000.00
9 |  | Supply, laying, testing commissioning of following sizes of Al Cu. conductor 1.1 kV grade, armoured, XLPE insulated FRLS LT Cables Control Cables including necessary cleats, clamps etc. (Cables shall be partly laid in Pipes, O H cable tray, on wall as required ) | Supply, laying, testing commissioning of following sizes of Al Cu. conductor 1.1 kV grade, armoured, XLPE insulated FRLS LT Cables Control Cables including necessary cleats, clamps etc. (Cables shall be partly laid in Pipes, O H cable tray, on wall as required )
10 |  | 3.5C – 70.0 (Al.) FRLS Armoured XLPE Cable * | 3.5C – 70.0 (Al.) FRLS Armoured XLPE Cable * | Mtrs | 40.000 | 30,000.00 | 750.00 | 30,000.00
11 |  | 3C – 4.0 (Cu.) FRLS Armoured XLPE Cable | 3C – 4.0 (Cu.) FRLS Armoured XLPE Cable | Mtrs | 100.000 | 41,000.00 | 410.00 | 41,000.00
12 |  | 3C – 6.0 (Cu.) FRLS Armoured XLPE Cable | 3C – 6.0 (Cu.) FRLS Armoured XLPE Cable | Mtrs | 10.000 | 3,950.00 | 395.00 | 3,950.00
13 |  | * Approximate and shall be as per point of supply from Airport Panel Isolator | * Approximate and shall be as per point of supply from Airport Panel Isolator
14 |  | Supply, erection, testing commissioning of following sizes of cable end terminations with Single compression gland for 1.1 kV grade, XLPE insulated, Al Cu Conductor cable | Supply, erection, testing commissioning of following sizes of cable end terminations with Single compression gland for 1.1 kV grade, XLPE insulated, Al Cu Conductor cable
15 |  | 3.5C – 70.0 (Al.) FRLS Armoured XLPE Cable *(Double Compression) | 3.5C – 70.0 (Al.) FRLS Armoured XLPE Cable *(Double Compression) | Nos. | 2.000 | 2,700.00 | 1350.00 | 2,700.00
16 |  | 3C – 4.0 (Cu.) FRLS Armoured XLPE Cable | 3C – 4.0 (Cu.) FRLS Armoured XLPE Cable | Nos. | 6.000 | 4,500.00 | 750.00 | 4,500.00
17 |  | 3C – 6.0 (Cu.) FRLS Armoured XLPE Cable | 3C – 6.0 (Cu.) FRLS Armoured XLPE Cable | Nos. | 2.000 | 1,500.00 | 750.00 | 1,500.00
18 |  | Wiring for DB Submains with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in surface concealed MS surface concealed conduit including cost of providing saddles etc as required for surface conduiting and or cost of cutting and filling chases as required and making suitable end termination with copper lugs complete as required and as below | Wiring for DB Submains with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in surface concealed MS surface concealed conduit including cost of providing saddles etc as required for surface conduiting and or cost of cutting and filling chases as required and making suitable end termination with copper lugs complete as required and as below
19 |  | 4 x 16 sq.mm + 2 No. 6.0 Sq. mm in 40 mm dia MS Conduit | 4 x 16 sq.mm + 2 No. 6.0 Sq. mm in 40 mm dia MS Conduit | Mtrs | 20.000 | 25,000.00 | 1250.00 | 25,000.00
20 |  | 4 x 10 sq.mm + 2 No. 4.0 Sq. mm in 32 mm dia MS Conduit | 4 x 10 sq.mm + 2 No. 4.0 Sq. mm in 32 mm dia MS Conduit | Mtrs | 20.000 | 23,000.00 | 1150.00 | 23,000.00
21 |  | 4 x 6 sq.mm + 2 No. 2.5 Sq. mm in 32 mm dia MS Conduit | 4 x 6 sq.mm + 2 No. 2.5 Sq. mm in 32 mm dia MS Conduit | Mtrs | 10.000 | 9,500.00 | 950.00 | 9,500.00
22 |  | 2 x 6 sq.mm + 1 No. 4 Sq. mm in 25 mm dia MS Conduit | 2 x 6 sq.mm + 1 No. 4 Sq. mm in 25 mm dia MS Conduit | Mtrs | 60.000 | 51,000.00 | 850.00 | 51,000.00
23 |  | 2 x 4 sq.mm + 1 No. 2.5 Sq. mm in 25 mm dia MS Conduit | 2 x 4 sq.mm + 1 No. 2.5 Sq. mm in 25 mm dia MS Conduit | Mtrs | 210.000 | 80,850.00 | 385.00 | 80,850.00
24 |  | Supplying and laying of the following earthing clamped to wall with suitable clamps saddles and fixing bolts in ground including the cost of digging and back filling as required and complete as required to comply with IS 3043 1987. All copper joints shall be tinned. The rates shall be inclusive of making test joints where ever required | Supplying and laying of the following earthing clamped to wall with suitable clamps saddles and fixing bolts in ground including the cost of digging and back filling as required and complete as required to comply with IS 3043 1987. All copper joints shall be tinned. The rates shall be inclusive of making test joints where ever required
25 |  | 25X6 mm GI Strip | 25X6 mm GI Strip | Mtrs | 20.000 | 9,000.00 | 450.00 | 9,000.00
26 |  | 25X3 mm GI Strip | 25X3 mm GI Strip | Mtrs | 30.000 | 12,000.00 | 400.00 | 12,000.00
27 |  | 8 SWG Copper Wire | 8 SWG Copper Wire | Mtrs | 30.000 | 2,550.00 | 85.00 | 2,550.00
28 |  | 8 SWG GI Wire | 8 SWG GI Wire | Mtrs | 200.000 | 15,000.00 | 75.00 | 15,000.00
29 |  | 1 Core 6.0 Sq. Mm FRLS Green Wire | 1 Core 6.0 Sq. Mm FRLS Green Wire | Mtrs | 30.000 | 3,300.00 | 110.00 | 3,300.00
30 |  | Supply, erection, testing commissioning of prefabricated GI Perforated type cable trays including Tees Bends Crossing Reducers Couping to be laid in cable trench, overhead on wall or hanged from ceiling complete with all accessories as required including support at every 1500mm as required | Supply, erection, testing commissioning of prefabricated GI Perforated type cable trays including Tees Bends Crossing Reducers Couping to be laid in cable trench, overhead on wall or hanged from ceiling complete with all accessories as required including support at every 1500mm as required
31 |  | 300 mm x 40 x 40 x 2 mm thick with 2 Nos. 25X3mm GI Earth Strip | 300 mm x 40 x 40 x 2 mm thick with 2 Nos. 25X3mm GI Earth Strip | Mtrs | 25.000 | 38,750.00 | 1550.00 | 38,750.00
32 |  | 150 mm x 40 x 40 x 2 mm thick with 2 Nos. 25X3mm GI Earth Strip | 150 mm x 40 x 40 x 2 mm thick with 2 Nos. 25X3mm GI Earth Strip | Mtrs | 60.000 | 75,000.00 | 1250.00 | 75,000.00
33 |  | Wiring for MCB controlled normal primary light points Wall Point Floor Point with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm dia 16 SWG MS conduit in wall ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq. mm PVC insulated copper conductor wire for loop earthing etc. complete as required. (Cost of MCB included in the item for per DB). | Wiring for MCB controlled normal primary light points Wall Point Floor Point with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm dia 16 SWG MS conduit in wall ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq. mm PVC insulated copper conductor wire for loop earthing etc. complete as required. (Cost of MCB included in the item for per DB). | Pt | 19.000 | 46,550.00 | 2450.00 | 46,550.00
34 |  | Wiring for secondary MCB controlled normal light points Wall Point Floor Point( Looped from above point) with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm 16 SWG MS conduit in wall ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq mm PVC insulated copper conductor wire for loop earthing etc. complete as required. | Wiring for secondary MCB controlled normal light points Wall Point Floor Point( Looped from above point) with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm 16 SWG MS conduit in wall ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq mm PVC insulated copper conductor wire for loop earthing etc. complete as required. | Pt | 60.000 | 99,000.00 | 1650.00 | 99,000.00
35 |  | Wiring for MCB controlled Emergency primary light points Wall Point Floor Point with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm dia 16 SWG MS conduit in wall ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq. mm PVC insulated copper conductor wire for loop earthing etc. complete as required. (Cost of MCB included in the item for per DB). | Wiring for MCB controlled Emergency primary light points Wall Point Floor Point with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm dia 16 SWG MS conduit in wall ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq. mm PVC insulated copper conductor wire for loop earthing etc. complete as required. (Cost of MCB included in the item for per DB). | Pt | 2.000 | 5,300.00 | 2650.00 | 5,300.00
36 |  | Wiring for secondary MCB controlled Emergency light points Wall Point Floor Point( Looped from above point) with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm 16 SWG MS conduit in wall ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq mm PVC insulated copper conductor wire for loop earthing etc. complete as required. | Wiring for secondary MCB controlled Emergency light points Wall Point Floor Point( Looped from above point) with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm 16 SWG MS conduit in wall ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq mm PVC insulated copper conductor wire for loop earthing etc. complete as required. | Pt | 12.000 | 21,000.00 | 1750.00 | 21,000.00
37 |  | Wiring for a 5 pin 240 volt 6 amp single phase and neutral switch socket outlet with 2.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall ceiling including cost of providing circuit wiring with 2.5 sq mm PVC insulated stranded copper conductor 1100 volt grade wires and including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and providing and fixing of a combined 5 pin 240 volt 6 amp socket outlet with safety shutters and 6 amp 240 volt single pole grid plate mounted switch with moulded cover plate in recessed GI box and including earthing of the 3rd pin with 1.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wires complete as requied( Switch and socket shall be as approved by the architect Client) | Wiring for a 5 pin 240 volt 6 amp single phase and neutral switch socket outlet with 2.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall ceiling including cost of providing circuit wiring with 2.5 sq mm PVC insulated stranded copper conductor 1100 volt grade wires and including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and providing and fixing of a combined 5 pin 240 volt 6 amp socket outlet with safety shutters and 6 amp 240 volt single pole grid plate mounted switch with moulded cover plate in recessed GI box and including earthing of the 3rd pin with 1.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wires complete as requied( Switch and socket shall be as approved by the architect Client) | Pt. | 7.000 | 22,750.00 | 3250.00 | 22,750.00
38 |  | Wiring same as in Item 12 above looped from an adjacent 6 amp switch socket outlet as required and providing and fixing of a modular type 5 pin 240 Volt 6 amp shuttered socket outlet and a modular type 6 amp 240 Volt single pole switch in a recessed GI boxes with internal wiring and moulded front plates complete as required. ( Switch and socket shall be as approved by the architect Client) | Wiring same as in Item 12 above looped from an adjacent 6 amp switch socket outlet as required and providing and fixing of a modular type 5 pin 240 Volt 6 amp shuttered socket outlet and a modular type 6 amp 240 Volt single pole switch in a recessed GI boxes with internal wiring and moulded front plates complete as required. ( Switch and socket shall be as approved by the architect Client) | Pt. | 16.000 | 15,200.00 | 950.00 | 15,200.00
39 |  | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (1 outlet wired on 1 circuit) with 2.5 sq. mm PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall Ceiling including the cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including providing and fixing 6 pin 240 volt 16 amp socket outlet with safety shutters and 16 amp 240 volt single pole grid plate mounted modular type switch with moulded cover plate in recessed GI box and including earthing of the 3rd pin with 1.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wires and complete as requied( Switch and socket shall be as approved by the architect Client) | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (1 outlet wired on 1 circuit) with 2.5 sq. mm PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall Ceiling including the cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including providing and fixing 6 pin 240 volt 16 amp socket outlet with safety shutters and 16 amp 240 volt single pole grid plate mounted modular type switch with moulded cover plate in recessed GI box and including earthing of the 3rd pin with 1.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wires and complete as requied( Switch and socket shall be as approved by the architect Client) | Pt. | 2.000 | 6,500.00 | 3250.00 | 6,500.00
40 |  | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (1 outlet wired on 1 circuit) with 4.0 sq. mm PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall Ceiling including the cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including providing and fixing 6 pin 240 volt 16 amp socket outlet with safety shutters and 16 amp 240 volt single pole grid plate mounted modular type switch with moulded cover plate in recessed GI box and including earthing of the 3rd pin with 2.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wires and complete as requied( Switch and socket shall be as approved by the architect Client) | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (1 outlet wired on 1 circuit) with 4.0 sq. mm PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall Ceiling including the cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including providing and fixing 6 pin 240 volt 16 amp socket outlet with safety shutters and 16 amp 240 volt single pole grid plate mounted modular type switch with moulded cover plate in recessed GI box and including earthing of the 3rd pin with 2.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wires and complete as requied( Switch and socket shall be as approved by the architect Client) | Pt. | 16.000 | 58,400.00 | 3650.00 | 58,400.00
41 |  | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (2 outlets wired on 1 circuit) with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS), 4.0 sq mm upto the first outlet and 2.5 sq mm from first to the second outlet in 25mm dia 16 SWG MS conduit in wall Ceiling including cost of providing saddles etc as required for surface conduiting and or cost of cutting and filling chases and including providing and fixing of two sets of 6 pin 240 volt 16 amp socket outlet with safety shutters and 16 amp 240 volt single pole grid plate mounted switches with moulded cover plate in a recessed GI box including earthing of the 3rd pin with 2.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wire complete as required. (Switch Socket Shall be as per approved sample by Architect) | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (2 outlets wired on 1 circuit) with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS), 4.0 sq mm upto the first outlet and 2.5 sq mm from first to the second outlet in 25mm dia 16 SWG MS conduit in wall Ceiling including cost of providing saddles etc as required for surface conduiting and or cost of cutting and filling chases and including providing and fixing of two sets of 6 pin 240 volt 16 amp socket outlet with safety shutters and 16 amp 240 volt single pole grid plate mounted switches with moulded cover plate in a recessed GI box including earthing of the 3rd pin with 2.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wire complete as required. (Switch Socket Shall be as per approved sample by Architect) | Pt. | 6.000 | 16,800.00 | 2800.00 | 16,800.00
42 |  | Wiring for primary switch board consisting of 3 Nos. 5 pin 240 volt 6 amp single phase and neutral switch socket outlets with 3 Nos. 6A switch with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS), 2.5 sq FRLS copper wire mm in 25mm dia 16 SWG MS conduit in wall Ceiling including cost of providing saddles etc as required for surface conduiting and or cost of cutting and filling chases and including providing and fixing prewired switch board each consisting of 3 Nos. 5 pin 240 volt 6 amp single phase and neutral switch socket outlets with 3 Nos. 6A modular switch , safety shutters in a recessed surface GI box including earthing of the 3rd pin with 1.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wire complete as required. (Switch Socket Shall be as per approved sample by Architect) Note- Conduits shall be 16 SWG MS on surface and FRLS PVC for wall concealed | Wiring for primary switch board consisting of 3 Nos. 5 pin 240 volt 6 amp single phase and neutral switch socket outlets with 3 Nos. 6A switch with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS), 2.5 sq FRLS copper wire mm in 25mm dia 16 SWG MS conduit in wall Ceiling including cost of providing saddles etc as required for surface conduiting and or cost of cutting and filling chases and including providing and fixing prewired switch board each consisting of 3 Nos. 5 pin 240 volt 6 amp single phase and neutral switch socket outlets with 3 Nos. 6A modular switch , safety shutters in a recessed surface GI box including earthing of the 3rd pin with 1.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wire complete as required. (Switch Socket Shall be as per approved sample by Architect) Note- Conduits shall be 16 SWG MS on surface and FRLS PVC for wall concealed | Pt. | 3.000 | 9,600.00 | 3200.00 | 9,600.00
43 |  | Supply installation testing and fixing 3 pin 20A , 240V , single Phase metal Clad industrial socket outlet with 20A DP MCB and complete in all respects( Wiring Excluded from scope of this item) | Supply installation testing and fixing 3 pin 20A , 240V , single Phase metal Clad industrial socket outlet with 20A DP MCB and complete in all respects( Wiring Excluded from scope of this item) | Nos. | 10.000 | 35,000.00 | 3500.00 | 35,000.00
44 |  | Supply installation testing and fixing 3 pin 25A 32A , 240V , single Phase metal Clad industrial socket outlet with 25A 32A DP MCB and complete in all respects( Wiring Excluded from scope of this item) | Supply installation testing and fixing 3 pin 25A 32A , 240V , single Phase metal Clad industrial socket outlet with 25A 32A DP MCB and complete in all respects( Wiring Excluded from scope of this item) | Nos. | 2.000 | 10,000.00 | 5000.00 | 10,000.00
45 |  | Supply installation testing and fixing 5 pin 25A 20A , 415V , single Phase metal Clad industrial socket outlet with 25A 20A FP MCB and complete in all respects( Wiring Excluded from scope of this item) | Supply installation testing and fixing 5 pin 25A 20A , 415V , single Phase metal Clad industrial socket outlet with 25A 20A FP MCB and complete in all respects( Wiring Excluded from scope of this item) | Nos. | 1.000 | 5,200.00 | 5200.00 | 5,200.00
46 |  | Supply installation testing and fixing 5 pin 40A , 415V , single Phase metal Clad industrial socket outlet with 40A FP MCB and complete in all respects( Wiring Excluded from scope of this item) | Supply installation testing and fixing 5 pin 40A , 415V , single Phase metal Clad industrial socket outlet with 40A FP MCB and complete in all respects( Wiring Excluded from scope of this item) | Nos. | 1.000 | 6,500.00 | 6500.00 | 6,500.00
47 |  | Supply , fixing Laying 2.0mm Thick FRLS PVC conduits on surface or concealed complete with PVC junction boxes, cover plates, PVC bends, PVC saddles, base and other accessories all made in PVC with GI screws as required to complete the job. . | Supply , fixing Laying 2.0mm Thick FRLS PVC conduits on surface or concealed complete with PVC junction boxes, cover plates, PVC bends, PVC saddles, base and other accessories all made in PVC with GI screws as required to complete the job. .
48 |  | 25 mm dia FRLS PVC conduit | 25 mm dia FRLS PVC conduit | Mtrs | 50.000 | 5,750.00 | 115.00 | 5,750.00
49 |  | 20 mm dia FRLS PVC conduit | 20 mm dia FRLS PVC conduit | Mtrs | 60.000 | 5,700.00 | 95.00 | 5,700.00
50 |  | Supply and installation of flush mounted (Enhanced Category 6T 568 A or B) outlets with 2 mm thick GI box complete including cutting, chases, fixing of GI boxes and making good. The plastic shall be high impact, flame-retardant, UL rate thermoplastic. Dust cover blank shall be provided to protect unused faceplate openings. Termination caps and plastic cover shall be provided to protect jack wiring. | Supply and installation of flush mounted (Enhanced Category 6T 568 A or B) outlets with 2 mm thick GI box complete including cutting, chases, fixing of GI boxes and making good. The plastic shall be high impact, flame-retardant, UL rate thermoplastic. Dust cover blank shall be provided to protect unused faceplate openings. Termination caps and plastic cover shall be provided to protect jack wiring.
51 |  | Single outlet face plate with RJ-45 Jack with information outlet | Single outlet face plate with RJ-45 Jack with information outlet | Nos. | 2.000 | 2,300.00 | 1150.00 | 2,300.00
52 |  | Duplex outlet face plate with RJ-45 Jack with information outlet | Duplex outlet face plate with RJ-45 Jack with information outlet | Nos. | 3.000 | 3,750.00 | 1250.00 | 3,750.00
53 |  | Supply,installtion testing and commisioning of Cat-6A UTP cables in existing Conduit complete as required for Telephone and Data System | Supply,installtion testing and commisioning of Cat-6A UTP cables in existing Conduit complete as required for Telephone and Data System | Mtrs | 150.000 | 20,250.00 | 135.00 | 20,250.00
54 |  | Supplying,installation and commisioning of CAT-6A patch cords 2 mtrs. | Supplying,installation and commisioning of CAT-6A patch cords 2 mtrs. | Nos | 8.000 | 5,200.00 | 650.00 | 5,200.00
55 |  | Supplying,installation and commisioning of CAT-6A patch cords 1 mtr. | Supplying,installation and commisioning of CAT-6A patch cords 1 mtr. | Nos | 8.000 | 4,400.00 | 550.00 | 4,400.00
56 |  | Installation of following light fixtures including connections and complete in all respects | Installation of following light fixtures including connections and complete in all respects
57 |  | Ceiling Suspended Linear Lights | Ceiling Suspended Linear Lights | No. | 45.000 | 33,750.00 | 750.00 | 33,750.00
58 |  | LED Strip Light ( Per Meter) | LED Strip Light ( Per Meter) | Mtrs | 25.000 | 5,250.00 | 210.00 | 5,250.00
59 |  | Signage | Signage | No. | 2.000 | 7,000.00 | 3500.00 | 7,000.00
60 |  | Hanging Pendant Light | Hanging Pendant Light | No. | 12.000 | 5,400.00 | 450.00 | 5,400.00
61 |  | Wall Lights | Wall Lights | No. | 15.000 | 6,750.00 | 450.00 | 6,750.00
62 |  | Tube Lights in BOH areas | Tube Lights in BOH areas | No. | 6.000 | 2,700.00 | 450.00 | 2,700.00

## Technical Score Detail
|  | RFQ No: R0665 COST COMPARISON REPORT | RFQ No: R0665 COST COMPARISON REPORT | RFQ No: R0665 COST COMPARISON REPORT | Comp. Date : 28/03/2024 | Comp. Date : 28/03/2024 | Comp. Date : 28/03/2024 | Vendor Name : Pioneer Infra And Turnkey Solutions
|  | RFQ No: R0665 COST COMPARISON REPORT | RFQ No: R0665 COST COMPARISON REPORT | RFQ No: R0665 COST COMPARISON REPORT | RFQ #: R0665 | RFQ #: R0665 | RFQ #: R0665 | Contact Name : Pankaj Upadhyay/Bipin Upadhyay
|  | RFQ No: R0665 COST COMPARISON REPORT | RFQ No: R0665 COST COMPARISON REPORT | RFQ No: R0665 COST COMPARISON REPORT | RFQ Date : 27/03/2024 17:37:48 | RFQ Date : 27/03/2024 17:37:48 | RFQ Date : 27/03/2024 17:37:48 | Vendor City :
|  | RFQ No: R0665 COST COMPARISON REPORT | RFQ No: R0665 COST COMPARISON REPORT | RFQ No: R0665 COST COMPARISON REPORT | BCD Date : 28/03/2024 16:20:00 | BCD Date : 28/03/2024 16:20:00 | BCD Date : 28/03/2024 16:20:00 | Telephone # :
|  | RFQ No: R0665 COST COMPARISON REPORT | RFQ No: R0665 COST COMPARISON REPORT | RFQ No: R0665 COST COMPARISON REPORT |  |  |  | Mobile # :
PR Number : Semolina-2324-00622 | PR Number : Semolina-2324-00622 | PR Number : Semolina-2324-00622 | PR Number : Semolina-2324-00622 | PR Number : Semolina-2324-00622 | PR Number : Semolina-2324-00622 | PR Number : Semolina-2324-00622 | PR Number : Semolina-2324-00622 | Email : bipinu@pioneerindinfra.com
Package / RFQ Name : PR for Electrical Work for Lucknow T3 Budweiser bar... | Package / RFQ Name : PR for Electrical Work for Lucknow T3 Budweiser bar... | Package / RFQ Name : PR for Electrical Work for Lucknow T3 Budweiser bar... | Package / RFQ Name : PR for Electrical Work for Lucknow T3 Budweiser bar... | Package / RFQ Name : PR for Electrical Work for Lucknow T3 Budweiser bar... | Package / RFQ Name : PR for Electrical Work for Lucknow T3 Budweiser bar... | Package / RFQ Name : PR for Electrical Work for Lucknow T3 Budweiser bar... | Package / RFQ Name : PR for Electrical Work for Lucknow T3 Budweiser bar... | Round # : 3 (RFQ)
Buyer : Sarvesh Patil | Buyer : Sarvesh Patil | Buyer : Sarvesh Patil | Buyer : Sarvesh Patil | Buyer : Sarvesh Patil | Buyer : Sarvesh Patil | Buyer : Sarvesh Patil | Buyer : Sarvesh Patil | Quotation Date :
Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Currency :INR | Currency :INR | Currency :INR | Quotation Validity Date :
Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | BUDGET PRICE : | .00 |  | Quote Currency :
# | Item Code | Item Description | Last PO Details | Unit | Qty | Last PO Unit Rate | Last PO Total Value | Score | Justification
1 |  | Electrical Work |  | no | 1.000 | 0.00 | 0.00
2 |  | Design, fabrication, assembling, wiring , supply , Erection , Installation , testing and commissioning of MDB Panels fabricated out of 2mm thick for structural members (Load bearing members) and 1.6mm thick for door and covers (Non load bearing members) CRCA painted sheet steel in cubicle formation with reinforcement of suitable size angle iron, channels, T irons, flats wherever necessary for large meter boards. Cable gland plates shall be provided at top and bottom both and windows for meter reading, locking arrangement (pad-lock seal) with wiring upto KWH meter meter to MCB shall be done by using adequately rated flexible single core copper wire. The boards shall be treated with all anticorrosive process before painting as per standards with final approved shade of powder coated as approved, 2 nos. earthing terminals shall be provided for all panels. The boards shall be suitable for 415 V, 3 phase, 4 wire, 50 Hz supply system. Boards shall be fabricated in length, height, depth etc to match with site conditions. An approval shall be taken for each panel before manufacturing. Galvanised hardwares with zinc passivation shall be used in fabrication of boards. Note The following provisions shall be required to be made in the switchboard detailed below The Switchboard shall have provision for entry of all PVCA cables from the top bottom as required. All live accessible parts shall be shrouded and all equipment shall be finger touch proof. The busbar insulation shall be with heat shrinkable sleeves. SMC DMC shrouds and busbar supports shall be used. Suitable tinned copper extension links for incoming outgoing cables shall be provided wherever required Control circuits includes breaker control switch, auto manual selector switch, anti pumping relay, spring charging trip indication, TIMER, control wiring, Auxiliary contactors MCB’s as required at site. Positive isolation of all breakers. All fault level breaking capacity indicates shall be ICS value at 415 volts (ICS = ICU = ICW = 100%). Space Heater light air filter shall be provided for each vertical compartment Link and drops from MCCB shall be designed for full rated current of MCCB ratings at same current density as of Main Bus Bar 2 nos. GI earth strip throughout the panel. |  |  | 0.000 | 0.00 | 0.00
3 |  | MAIN MDB Incoming 1 No. 160 amps 25 kA 440 volt FP MCCB with Thermal Magnetic overcurrent and short circuit and with following Metering, Indication Protection 1 Nos. 6 Parameter Multi Function Mater with 3 Nos. Cast Resin CTs and MCBs Breaker ON OFF indication Lamps R-Y-B indication lamps with MCBs ELR with CBCT Bus Bar 200 A, TPN Al. Bus Bar of suitable length having Current density 1Amp sq.mm having high conductivity electrical grade suitable to withstand symmetrical fault level of 25 kA. Neutral busbar shall be of 100% capacity. Outgoings 2 No. 63 amps 4P MCB ( Type C) 2 No. 32 amps 4P MCB ( Type C) 1 No. 25 amps 4P MCB ( Type C) 2 No. 32 amps 2P MCB ( Type C) 1 No. 25 amps 2P MCB ( Type C) 1 No. 40 amps FP MCB + RCCB of 100mA sensitivity. 1 No. 25 amps FP MCB + RCCB of 100mA sensitivity. AHU Starters In Maon Panel 1 Nos. Fully automatic 0.75 KW Motor DOL starter with 16A TP Type C Curve MCB , 9A TP Contactor , ON OFF push buttons and on off Trip indicating lights , A M selector switch for local remote operations, CT operated Digital Ammeter, suitable NO NC Potential free contacts for Interlocking with Fire alarm panel 1.4A -2.3 A O L relay with inbuilt single phase preventor , selector switches etc as required. 1 Nos. Fully automatic 1.5 KW Motor DOL starter with 20A TP Type C Curve MCB , 9A TP Contactor , ON OFF push buttons and on off Trip indicating lights , A M selector switch for local remote operations, CT operated Digital Ammeter, suitable NO NC Potential free contacts for Interlocking with Fire alarm panel 2.5A -4.0 A O L relay with inbuilt single phase preventor , selector switches etc as required. 1 Nos. Fully automatic 2.25 KW Motor DOL starter with 25A TP Type C Curve MCB , 16A TP Contactor , ON OFF push buttons and on off Trip indicating lights , A M selector switch for local remote operations, CT operated Digital Ammeter, suitable NO NC Potential free contacts for Interlocking with Fire alarm panel 4.5A -7.5 A O L relay with inbuilt single phase preventor , selector switches etc as required. Main MDB as described above |  | Set | 1.000 | 0.00 | 0.00
4 |  | DISTRIBUTION BOARDS - Supply, erection, testing and commissioning of the following sheet steel clad wall recess mounting dust and vermin proof double door type distribution boards constructed from 16 SWG sheet steel IP 42 construction, finished with rust proof duly powder coated in approved shade with hinged gasketed door and housing the following complete with P.V.C. insulated copper busbars rated 200 amp with interconnections, neutral and earth bar assembly per phase, earthing terminals complete as approved by Architects. Note All MCBs in distribuition board for power circuits shall be of C curve |  |  | 0.000 | 0.00 | 0.00
5 |  | Type A - 1-63amp FP MCB with 3 single phase banks each comprising of 63A DP RCCB(100 mA) and 12 nos. 6 16 20 25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. |  | Set | 1.000 | 0.00 | 0.00
6 |  | Type B - 1-32amp FP MCB with 3 single phase banks each comprising of 32A DP RCCB(100 mA) and 6 nos. 6 16 20 25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. |  | Set | 1.000 | 0.00 | 0.00
7 |  | Type C - 1-32 amp DP MCB + DP RCCB ( 100mA) and 12 nos. 6 16 20 25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. |  | Set | 1.000 | 0.00 | 0.00
8 |  | Type D - 1-32 amp DP MCB + DP RCCB ( 100mA) and 8 nos. 6 16 20 25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. |  | Set | 1.000 | 0.00 | 0.00
9 |  | Supply installation testing and commisioning 3.0 kVA online ( 1ph input and 1ph output) UPS with 15 Min power back up complete with in buit Static by pass switch , Mannual external maintenance by pass switch , Rectifiers , Sealed MF batteries etc as required |  | No. | 1.000 | 0.00 | 0.00
10 |  | Supply, laying, testing commissioning of following sizes of Al Cu. conductor 1.1 kV grade, armoured, XLPE insulated FRLS LT Cables Control Cables including necessary cleats, clamps etc. (Cables shall be partly laid in Pipes, O H cable tray, on wall as required ) |  |  | 0.000 | 0.00 | 0.00
11 |  | 3.5C – 70.0 (Al.) FRLS Armoured XLPE Cable * |  | Mtrs | 40.000 | 0.00 | 0.00
12 |  | 3C – 4.0 (Cu.) FRLS Armoured XLPE Cable |  | Mtrs | 100.000 | 0.00 | 0.00
13 |  | 3C – 6.0 (Cu.) FRLS Armoured XLPE Cable |  | Mtrs | 10.000 | 0.00 | 0.00
14 |  | * Approximate and shall be as per point of supply from Airport Panel Isolator |  |  | 0.000 | 0.00 | 0.00
15 |  | Supply, erection, testing commissioning of following sizes of cable end terminations with Single compression gland for 1.1 kV grade, XLPE insulated, Al Cu Conductor cable |  |  | 0.000 | 0.00 | 0.00
16 |  | 3.5C – 70.0 (Al.) FRLS Armoured XLPE Cable *(Double Compression) |  | Nos. | 2.000 | 0.00 | 0.00
17 |  | 3C – 4.0 (Cu.) FRLS Armoured XLPE Cable |  | Nos. | 6.000 | 0.00 | 0.00
18 |  | 3C – 6.0 (Cu.) FRLS Armoured XLPE Cable |  | Nos. | 2.000 | 0.00 | 0.00
19 |  | Wiring for DB Submains with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in surface concealed MS surface concealed conduit including cost of providing saddles etc as required for surface conduiting and or cost of cutting and filling chases as required and making suitable end termination with copper lugs complete as required and as below |  |  | 0.000 | 0.00 | 0.00
20 |  | 4 x 16 sq.mm + 2 No. 6.0 Sq. mm in 40 mm dia MS Conduit |  | Mtrs | 20.000 | 0.00 | 0.00
21 |  | 4 x 10 sq.mm + 2 No. 4.0 Sq. mm in 32 mm dia MS Conduit |  | Mtrs | 20.000 | 0.00 | 0.00
22 |  | 4 x 6 sq.mm + 2 No. 2.5 Sq. mm in 32 mm dia MS Conduit |  | Mtrs | 10.000 | 0.00 | 0.00
23 |  | 2 x 6 sq.mm + 1 No. 4 Sq. mm in 25 mm dia MS Conduit |  | Mtrs | 60.000 | 0.00 | 0.00
24 |  | 2 x 4 sq.mm + 1 No. 2.5 Sq. mm in 25 mm dia MS Conduit |  | Mtrs | 210.000 | 0.00 | 0.00
25 |  | Supplying and laying of the following earthing clamped to wall with suitable clamps saddles and fixing bolts in ground including the cost of digging and back filling as required and complete as required to comply with IS 3043 1987. All copper joints shall be tinned. The rates shall be inclusive of making test joints where ever required |  |  | 0.000 | 0.00 | 0.00
26 |  | 25X6 mm GI Strip |  | Mtrs | 20.000 | 0.00 | 0.00
27 |  | 25X3 mm GI Strip |  | Mtrs | 30.000 | 0.00 | 0.00
28 |  | 8 SWG Copper Wire |  | Mtrs | 30.000 | 0.00 | 0.00
29 |  | 8 SWG GI Wire |  | Mtrs | 200.000 | 0.00 | 0.00
30 |  | 1 Core 6.0 Sq. Mm FRLS Green Wire |  | Mtrs | 30.000 | 0.00 | 0.00
31 |  | Supply, erection, testing commissioning of prefabricated GI Perforated type cable trays including Tees Bends Crossing Reducers Couping to be laid in cable trench, overhead on wall or hanged from ceiling complete with all accessories as required including support at every 1500mm as required |  |  | 0.000 | 0.00 | 0.00
32 |  | 300 mm x 40 x 40 x 2 mm thick with 2 Nos. 25X3mm GI Earth Strip |  | Mtrs | 25.000 | 0.00 | 0.00
33 |  | 150 mm x 40 x 40 x 2 mm thick with 2 Nos. 25X3mm GI Earth Strip |  | Mtrs | 60.000 | 0.00 | 0.00
34 |  | Wiring for MCB controlled normal primary light points Wall Point Floor Point with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm dia 16 SWG MS conduit in wall ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq. mm PVC insulated copper conductor wire for loop earthing etc. complete as required. (Cost of MCB included in the item for per DB). |  | Pt | 19.000 | 0.00 | 0.00
35 |  | Wiring for secondary MCB controlled normal light points Wall Point Floor Point( Looped from above point) with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm 16 SWG MS conduit in wall ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq mm PVC insulated copper conductor wire for loop earthing etc. complete as required. |  | Pt | 60.000 | 0.00 | 0.00
36 |  | Wiring for MCB controlled Emergency primary light points Wall Point Floor Point with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm dia 16 SWG MS conduit in wall ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq. mm PVC insulated copper conductor wire for loop earthing etc. complete as required. (Cost of MCB included in the item for per DB). |  | Pt | 2.000 | 0.00 | 0.00
37 |  | Wiring for secondary MCB controlled Emergency light points Wall Point Floor Point( Looped from above point) with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm 16 SWG MS conduit in wall ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq mm PVC insulated copper conductor wire for loop earthing etc. complete as required. |  | Pt | 12.000 | 0.00 | 0.00
38 |  | Wiring for a 5 pin 240 volt 6 amp single phase and neutral switch socket outlet with 2.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall ceiling including cost of providing circuit wiring with 2.5 sq mm PVC insulated stranded copper conductor 1100 volt grade wires and including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and providing and fixing of a combined 5 pin 240 volt 6 amp socket outlet with safety shutters and 6 amp 240 volt single pole grid plate mounted switch with moulded cover plate in recessed GI box and including earthing of the 3rd pin with 1.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wires complete as requied( Switch and socket shall be as approved by the architect Client) |  | Pt. | 7.000 | 0.00 | 0.00
39 |  | Wiring same as in Item 12 above looped from an adjacent 6 amp switch socket outlet as required and providing and fixing of a modular type 5 pin 240 Volt 6 amp shuttered socket outlet and a modular type 6 amp 240 Volt single pole switch in a recessed GI boxes with internal wiring and moulded front plates complete as required. ( Switch and socket shall be as approved by the architect Client) |  | Pt. | 16.000 | 0.00 | 0.00
40 |  | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (1 outlet wired on 1 circuit) with 2.5 sq. mm PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall Ceiling including the cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including providing and fixing 6 pin 240 volt 16 amp socket outlet with safety shutters and 16 amp 240 volt single pole grid plate mounted modular type switch with moulded cover plate in recessed GI box and including earthing of the 3rd pin with 1.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wires and complete as requied( Switch and socket shall be as approved by the architect Client) |  | Pt. | 2.000 | 0.00 | 0.00
41 |  | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (1 outlet wired on 1 circuit) with 4.0 sq. mm PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall Ceiling including the cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including providing and fixing 6 pin 240 volt 16 amp socket outlet with safety shutters and 16 amp 240 volt single pole grid plate mounted modular type switch with moulded cover plate in recessed GI box and including earthing of the 3rd pin with 2.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wires and complete as requied( Switch and socket shall be as approved by the architect Client) |  | Pt. | 16.000 | 0.00 | 0.00
42 |  | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (2 outlets wired on 1 circuit) with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS), 4.0 sq mm upto the first outlet and 2.5 sq mm from first to the second outlet in 25mm dia 16 SWG MS conduit in wall Ceiling including cost of providing saddles etc as required for surface conduiting and or cost of cutting and filling chases and including providing and fixing of two sets of 6 pin 240 volt 16 amp socket outlet with safety shutters and 16 amp 240 volt single pole grid plate mounted switches with moulded cover plate in a recessed GI box including earthing of the 3rd pin with 2.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wire complete as required. (Switch Socket Shall be as per approved sample by Architect) |  | Pt. | 6.000 | 0.00 | 0.00
43 |  | Wiring for primary switch board consisting of 3 Nos. 5 pin 240 volt 6 amp single phase and neutral switch socket outlets with 3 Nos. 6A switch with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS), 2.5 sq FRLS copper wire mm in 25mm dia 16 SWG MS conduit in wall Ceiling including cost of providing saddles etc as required for surface conduiting and or cost of cutting and filling chases and including providing and fixing prewired switch board each consisting of 3 Nos. 5 pin 240 volt 6 amp single phase and neutral switch socket outlets with 3 Nos. 6A modular switch , safety shutters in a recessed surface GI box including earthing of the 3rd pin with 1.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wire complete as required. (Switch Socket Shall be as per approved sample by Architect) Note- Conduits shall be 16 SWG MS on surface and FRLS PVC for wall concealed |  | Pt. | 3.000 | 0.00 | 0.00
44 |  | Supply installation testing and fixing 3 pin 20A , 240V , single Phase metal Clad industrial socket outlet with 20A DP MCB and complete in all respects( Wiring Excluded from scope of this item) |  | Nos. | 10.000 | 0.00 | 0.00
45 |  | Supply installation testing and fixing 3 pin 25A 32A , 240V , single Phase metal Clad industrial socket outlet with 25A 32A DP MCB and complete in all respects( Wiring Excluded from scope of this item) |  | Nos. | 2.000 | 0.00 | 0.00
46 |  | Supply installation testing and fixing 5 pin 25A 20A , 415V , single Phase metal Clad industrial socket outlet with 25A 20A FP MCB and complete in all respects( Wiring Excluded from scope of this item) |  | Nos. | 1.000 | 0.00 | 0.00
47 |  | Supply installation testing and fixing 5 pin 40A , 415V , single Phase metal Clad industrial socket outlet with 40A FP MCB and complete in all respects( Wiring Excluded from scope of this item) |  | Nos. | 1.000 | 0.00 | 0.00
48 |  | Supply , fixing Laying 2.0mm Thick FRLS PVC conduits on surface or concealed complete with PVC junction boxes, cover plates, PVC bends, PVC saddles, base and other accessories all made in PVC with GI screws as required to complete the job. . |  |  | 0.000 | 0.00 | 0.00
49 |  | 25 mm dia FRLS PVC conduit |  | Mtrs | 50.000 | 0.00 | 0.00
50 |  | 20 mm dia FRLS PVC conduit |  | Mtrs | 60.000 | 0.00 | 0.00
51 |  | Supply and installation of flush mounted (Enhanced Category 6T 568 A or B) outlets with 2 mm thick GI box complete including cutting, chases, fixing of GI boxes and making good. The plastic shall be high impact, flame-retardant, UL rate thermoplastic. Dust cover blank shall be provided to protect unused faceplate openings. Termination caps and plastic cover shall be provided to protect jack wiring. |  |  | 0.000 | 0.00 | 0.00
52 |  | Single outlet face plate with RJ-45 Jack with information outlet |  | Nos. | 2.000 | 0.00 | 0.00
53 |  | Duplex outlet face plate with RJ-45 Jack with information outlet |  | Nos. | 3.000 | 0.00 | 0.00
54 |  | Supply,installtion testing and commisioning of Cat-6A UTP cables in existing Conduit complete as required for Telephone and Data System |  | Mtrs | 150.000 | 0.00 | 0.00
55 |  | Supplying,installation and commisioning of CAT-6A patch cords 2 mtrs. |  | Nos | 8.000 | 0.00 | 0.00
56 |  | Supplying,installation and commisioning of CAT-6A patch cords 1 mtr. |  | Nos | 8.000 | 0.00 | 0.00
57 |  | Installation of following light fixtures including connections and complete in all respects |  |  | 0.000 | 0.00 | 0.00
58 |  | Ceiling Suspended Linear Lights |  | No. | 45.000 | 0.00 | 0.00
59 |  | LED Strip Light ( Per Meter) |  | Mtrs | 25.000 | 0.00 | 0.00
60 |  | Signage |  | No. | 2.000 | 0.00 | 0.00
61 |  | Hanging Pendant Light |  | No. | 12.000 | 0.00 | 0.00
62 |  | Wall Lights |  | No. | 15.000 | 0.00 | 0.00
63 |  | Tube Lights in BOH areas |  | No. | 6.000 | 0.00 | 0.00