## Price Comparison
|  | RFQ No: R1645 COST COMPARISON REPORT | RFQ No: R1645 COST COMPARISON REPORT | RFQ No: R1645 COST COMPARISON REPORT | Comp. Date : 10/09/2024 | Comp. Date : 10/09/2024 | Comp. Date : 10/09/2024 | Vendor Name : Nova Hvac Systems (India) Pvt Ltd. (RV232421916) | [5 empty] | Vendor Name : APC Air Control (RV232420221) | [5 empty] | Vendor Name : ANJLE MEP PROJECT PVT LTD (RV242523025)
|  | RFQ No: R1645 COST COMPARISON REPORT | RFQ No: R1645 COST COMPARISON REPORT | RFQ No: R1645 COST COMPARISON REPORT | RFQ #: R1645 | RFQ #: R1645 | RFQ #: R1645 | Contact Name : BILAL METKAR | [5 empty] | Contact Name : Rajvinder | [5 empty] | Contact Name : PREMKANT
|  | RFQ No: R1645 COST COMPARISON REPORT | RFQ No: R1645 COST COMPARISON REPORT | RFQ No: R1645 COST COMPARISON REPORT | RFQ Date : 09/09/2024 16:13:05 | RFQ Date : 09/09/2024 16:13:05 | RFQ Date : 09/09/2024 16:13:05 | Vendor City : | [5 empty] | Vendor City : | [5 empty] | Vendor City :
|  | RFQ No: R1645 COST COMPARISON REPORT | RFQ No: R1645 COST COMPARISON REPORT | RFQ No: R1645 COST COMPARISON REPORT | BCD Date : 10/09/2024 02:05:00 | BCD Date : 10/09/2024 02:05:00 | BCD Date : 10/09/2024 02:05:00 | Telephone # : | [5 empty] | Telephone # : | [5 empty] | Telephone # :
|  | RFQ No: R1645 COST COMPARISON REPORT | RFQ No: R1645 COST COMPARISON REPORT | RFQ No: R1645 COST COMPARISON REPORT |  |  |  | Mobile # : | [5 empty] | Mobile # : 7837249094 | [5 empty] | Mobile # :
PR Number : DCPL-2425-00104 | PR Number : DCPL-2425-00104 | PR Number : DCPL-2425-00104 | PR Number : DCPL-2425-00104 | PR Number : DCPL-2425-00104 | PR Number : DCPL-2425-00104 | PR Number : DCPL-2425-00104 | PR Number : DCPL-2425-00104 | Email : bilal.metkar@novainitiative.com | [5 empty] | Email : apcmumbai@gmail.com | [5 empty] | Email : anjlemepprojects@gmail.com
Package / RFQ Name : Ventilation Work- CC R City | Package / RFQ Name : Ventilation Work- CC R City | Package / RFQ Name : Ventilation Work- CC R City | Package / RFQ Name : Ventilation Work- CC R City | Package / RFQ Name : Ventilation Work- CC R City | Package / RFQ Name : Ventilation Work- CC R City | Package / RFQ Name : Ventilation Work- CC R City | Package / RFQ Name : Ventilation Work- CC R City | Round # : 6 (RFQ) | [5 empty] | Round # : 6 (RFQ) | [5 empty] | Round # : 6 (RFQ)
Buyer : Mrunal Joshi / Technical : / Approver : | Buyer : Mrunal Joshi / Technical : / Approver : | Buyer : Mrunal Joshi / Technical : / Approver : | Buyer : Mrunal Joshi / Technical : / Approver : | Buyer : Mrunal Joshi / Technical : / Approver : | Buyer : Mrunal Joshi / Technical : / Approver : | Buyer : Mrunal Joshi / Technical : / Approver : | Buyer : Mrunal Joshi / Technical : / Approver : | Quotation Date : |  |  | Quotation Validity Date : |  |  | Quotation Date : |  |  | Quotation Validity Date : |  |  | Quotation Date : |  |  | Quotation Validity Date :
Comp. # : 6 | Comp. # : 6 | Comp. # : 6 | Comp. # : 6 | Comp. # : 6 | Currency :INR | Currency :INR | Currency :INR | Buyer Remark : | [5 empty] | Buyer Remark : . | [5 empty] | Buyer Remark :
Comp. # : 6 | Comp. # : 6 | Comp. # : 6 | Comp. # : 6 | Comp. # : 6 | BUDGET PRICE : | .00 |  | Quote Currency : INR | [5 empty] | Quote Currency : INR | [5 empty] | Quote Currency : INR
# | Item Code | Item Description | Unit | Qty | Last PO Details | Lowest Unit Rate | Lowest Vendor | First Bid | Disc % | GST % | Technical | Unit Price | Total | First Bid | Disc % | GST % | Technical | Unit Price | Total | First Bid | Disc % | GST % | Technical | Unit Price | Total
1 |  | Ventilation system | EA | 1.00 |  | 1,260,000.00 | APC Air Control | 1277061.00 | 0.00 | 18.00 |  | 1,277,061.00 | 1,277,061.00 | 1314000.00 | 0.00 | 18.00 |  | 1,260,000.00 | 1,260,000.00 | 1763250.00 | 0.00 | 18.00 |  | 1,763,250.00 | 1,763,250.00
Item Total | [8 empty] | .00 | 229,870.98 |  |  | 1,277,061.00 |  | .00 | 226,800.00 |  |  | 1,260,000.00 |  | .00 | 317,385.00 |  |  | 1,763,250.00
Discount Total Value | [7 empty] | Grand Dis. Amt | .00 |  |  |  | .00 | Grand Dis. Amt | .00 |  |  |  | .00 | Grand Dis. Amt | .00 |  |  |  | .00
GST Total Amount | [12 empty] | 229,870.98 | [5 empty] | 226,800.00 | [5 empty] | 317,385.00
Net Landed Cost | [11 empty] | INR | 1,506,931.98 |  |  |  |  | INR | 1,486,800.00 |  |  |  |  | INR | 2,080,635.00
Vendor Status | [7 empty] | Round # : 6 (RFQ) | Round # : 6 (RFQ)
Sr No. | Vendor Code | Vendor Name | [5 empty] | Status | Remarks
1 | RV232421916 | Nova Hvac Systems (India) Pvt Ltd. | [5 empty] | Participate
2 | RV232420289 | CRYSTAL AIRCOOL | [5 empty] | Participate
3 | RV242523025 | ANJLE MEP PROJECT PVT LTD | [5 empty] | Participate
4 | RV232420171 | PIONEER PROJECT SOLUTION | [5 empty] | Participate
5 | RV232420221 | APC Air Control | [5 empty] | Participate
6 | RV242523197 | AD ASSOCIATES | [5 empty] | Participate

## BOQ Price Bid
|  | RFQ No: R1645 COST COMPARISON REPORT | RFQ No: R1645 COST COMPARISON REPORT | Comp. Date : 10/09/2024 | Comp. Date : 10/09/2024 | Comp. Date : 10/09/2024 | Vendor Name : Nova Hvac Systems (India) Pvt Ltd. | Vendor Name : Nova Hvac Systems (India) Pvt Ltd. | Vendor Name : APC Air Control | Vendor Name : APC Air Control | Vendor Name : ANJLE MEP PROJECT PVT LTD | Vendor Name : ANJLE MEP PROJECT PVT LTD
|  | RFQ No: R1645 COST COMPARISON REPORT | RFQ No: R1645 COST COMPARISON REPORT | RFQ #: R1645 | RFQ #: R1645 | RFQ #: R1645 | Contact Name : BILAL METKAR | Contact Name : BILAL METKAR | Contact Name : Rajvinder | Contact Name : Rajvinder | Contact Name : PREMKANT | Contact Name : PREMKANT
|  | RFQ No: R1645 COST COMPARISON REPORT | RFQ No: R1645 COST COMPARISON REPORT | RFQ Date : 09/09/2024 16:13:05 | RFQ Date : 09/09/2024 16:13:05 | RFQ Date : 09/09/2024 16:13:05 | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City :
|  | RFQ No: R1645 COST COMPARISON REPORT | RFQ No: R1645 COST COMPARISON REPORT | BCD Date : 10/09/2024 02:05:00 | BCD Date : 10/09/2024 02:05:00 | BCD Date : 10/09/2024 02:05:00 | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # :
|  | RFQ No: R1645 COST COMPARISON REPORT | RFQ No: R1645 COST COMPARISON REPORT |  |  |  | Mobile # : | Mobile # : | Mobile # : 7837249094 | Mobile # : 7837249094 | Mobile # : | Mobile # :
PR Number : DCPL-2425-00104 | PR Number : DCPL-2425-00104 | PR Number : DCPL-2425-00104 | PR Number : DCPL-2425-00104 | PR Number : DCPL-2425-00104 | PR Number : DCPL-2425-00104 | PR Number : DCPL-2425-00104 | Email : bilal.metkar@novainitiative.com | Email : bilal.metkar@novainitiative.com | Email : apcmumbai@gmail.com | Email : apcmumbai@gmail.com | Email : anjlemepprojects@gmail.com | Email : anjlemepprojects@gmail.com
Package / RFQ Name : Ventilation Work- CC R City | Package / RFQ Name : Ventilation Work- CC R City | Package / RFQ Name : Ventilation Work- CC R City | Package / RFQ Name : Ventilation Work- CC R City | Package / RFQ Name : Ventilation Work- CC R City | Package / RFQ Name : Ventilation Work- CC R City | Package / RFQ Name : Ventilation Work- CC R City | Round # : 6 (RFQ) | Round # : 6 (RFQ) | Round # : 6 (RFQ) | Round # : 6 (RFQ) | Round # : 6 (RFQ) | Round # : 6 (RFQ)
Buyer : Mrunal Joshi | Buyer : Mrunal Joshi | Buyer : Mrunal Joshi | Buyer : Mrunal Joshi | Buyer : Mrunal Joshi | Buyer : Mrunal Joshi | Buyer : Mrunal Joshi | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score :
Comp. # : 6 | Comp. # : 6 | Comp. # : 6 | Comp. # : 6 | Currency :INR | Currency :INR | Currency :INR | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date :
Comp. # : 6 | Comp. # : 6 | Comp. # : 6 | Comp. # : 6 | BUDGET PRICE :1,425,000.00 | BUDGET PRICE :1,425,000.00 | BUDGET PRICE :1,425,000.00 | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date :
Sr No. | Item Code | Item Name | Item Description | UOM | Qty | Minimum Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount
1 |  | Ventilation system | Purchase request for Ventilation system | EA | 1 |  |  | 1277061 |  | 1260000 |  | 1763250
1 |  | Air quantity Static 5700 CFM 70 mm Supply, Installation,testing commissioning of the following Centrifugal Blower would be used to supply Exhaust Air into the Kitchen, Fan to have Backward inclined Blades, Impeller Should be statically and Dynamically Balanced, Motor to have Squirrel cage, to operate on 3Phase 50Hz AC supply, TEFC Class F Insulation, IE2 Type Motor - Crompton Siemens Make, Fan would be supplied with Anti Vibration Pads | Air quantity Static 5700 CFM 70 mm Supply, Installation,testing commissioning of the following Centrifugal Blower would be used to supply Exhaust Air into the Kitchen, Fan to have Backward inclined Blades, Impeller Should be statically and Dynamically Balanced, Motor to have Squirrel cage, to operate on 3Phase 50Hz AC supply, TEFC Class F Insulation, IE2 Type Motor - Crompton Siemens Make, Fan would be supplied with Anti Vibration Pads | Nos | 1 | 143538 | 143538 | 143538 | 160000 | 160000 | 215000 | 215000
2 |  | Air quantity Static 4600 CFM 70 mm Supply, Installation,testing commissioning of the following Centrifugal Blower would be used to supply Exhaust Air into the Kitchen, Fan to have Backward inclined Blades, Impeller Should be statically and Dynamically Balanced, Motor to have Squirrel cage, to operate on 3Phase 50Hz AC supply, TEFC Class F Insulation, IE2 Type Motor - Crompton Siemens Make, Fan would be supplied with Anti Vibration Pads | Air quantity Static 4600 CFM 70 mm Supply, Installation,testing commissioning of the following Centrifugal Blower would be used to supply Exhaust Air into the Kitchen, Fan to have Backward inclined Blades, Impeller Should be statically and Dynamically Balanced, Motor to have Squirrel cage, to operate on 3Phase 50Hz AC supply, TEFC Class F Insulation, IE2 Type Motor - Crompton Siemens Make, Fan would be supplied with Anti Vibration Pads | Nos | 1 | 135000 | 143538 | 143538 | 135000 | 135000 | 195000 | 195000
3 |  | Air quantity Static 9000 CFM 60 mm Supply, Installation,testing commissioning of the following Centrifugal Blower would be used to supply Fresh Air into the Kitchen, Fan to have Backward inclined Blades, Impeller Should be statically and Dynamically Balanced, Motor to have Squirrel cage, to operate on 3Phase 50Hz AC supply, TEFC Class F Insulation, IE2 Type Motor - Crompton Siemens Make, Fan would be supplied with Anti Vibration Pads | Air quantity Static 9000 CFM 60 mm Supply, Installation,testing commissioning of the following Centrifugal Blower would be used to supply Fresh Air into the Kitchen, Fan to have Backward inclined Blades, Impeller Should be statically and Dynamically Balanced, Motor to have Squirrel cage, to operate on 3Phase 50Hz AC supply, TEFC Class F Insulation, IE2 Type Motor - Crompton Siemens Make, Fan would be supplied with Anti Vibration Pads | Nos | 1 | 170275 | 170275 | 170275 | 230000 | 230000 | 415000 | 415000
4 |  | Exhaust Air Qty -5700CFM (Approved make - APC-DS-3) - Construction Made of 16 gauge galvanized sheet, high bake epoxy powder coated or 2 mm mild steel plate oil proof of IP 54. - Operating Voltage 220V 1Ph 50Hz - Power consumption 50 watts per module unit up to 5000 cfm. - Pre Filter Washable type aluminum mesh pre-filter - Ionizer spring loaded Tungsten wires to create high voltage DC field 12-13 kV - Collector Plate High grade Aluminum collector plates which should be alternatively charged positive negative with large collecting area. Collector cell should be of permanent type and slide out facility for easy removal for cleaning. - Insulator Teaflon insulator. - Access door to filter section shall be equipped with safety limit switch. | Exhaust Air Qty -5700CFM (Approved make - APC-DS-3) - Construction Made of 16 gauge galvanized sheet, high bake epoxy powder coated or 2 mm mild steel plate oil proof of IP 54. - Operating Voltage 220V 1Ph 50Hz - Power consumption 50 watts per module unit up to 5000 cfm. - Pre Filter Washable type aluminum mesh pre-filter - Ionizer spring loaded Tungsten wires to create high voltage DC field 12-13 kV - Collector Plate High grade Aluminum collector plates which should be alternatively charged positive negative with large collecting area. Collector cell should be of permanent type and slide out facility for easy removal for cleaning. - Insulator Teaflon insulator. - Access door to filter section shall be equipped with safety limit switch. | Nos | 1 | 242400 | 242400 | 242400 | 245000 | 245000 | 315000 | 315000
5 |  | Exhaust Air Qty -4600CFM (Approved make - APC-DS-2) - Construction Made of 16 gauge galvanized sheet, high bake epoxy powder coated or 2 mm mild steel plate oil proof of IP 54. - Operating Voltage 220V 1Ph 50Hz - Power consumption 50 watts per module unit up to 5000 cfm. - Pre Filter Washable type aluminum mesh pre-filter - Ionizer spring loaded Tungsten wires to create high voltage DC field 12-13 kV - Collector Plate High grade Aluminum collector plates which should be alternatively charged positive negative with large collecting area. Collector cell should be of permanent type and slide out facility for easy removal for cleaning. - Insulator Teaflon insulator. - Access door to filter section shall be equipped with safety limit switch. | Exhaust Air Qty -4600CFM (Approved make - APC-DS-2) - Construction Made of 16 gauge galvanized sheet, high bake epoxy powder coated or 2 mm mild steel plate oil proof of IP 54. - Operating Voltage 220V 1Ph 50Hz - Power consumption 50 watts per module unit up to 5000 cfm. - Pre Filter Washable type aluminum mesh pre-filter - Ionizer spring loaded Tungsten wires to create high voltage DC field 12-13 kV - Collector Plate High grade Aluminum collector plates which should be alternatively charged positive negative with large collecting area. Collector cell should be of permanent type and slide out facility for easy removal for cleaning. - Insulator Teaflon insulator. - Access door to filter section shall be equipped with safety limit switch. | Nos | 1 | 170000 | 199124 | 199124 | 170000 | 170000 | 285000 | 285000
6 |  | 0.80 mm (22 SWG) GSS ducting (751mm-1500mm) Supply, fabrication, installation and testing of MS SS metal ducts as per IS-277 (120 GSM both sides, LFQ confirming to Class VIII) for MS SS Sheets and IS-655 for fabrication of following thicknesses including necessary G.I. hangers supports, volume control duct dampers, accessories, vanes, 3 mm neoprene rubber gasket etc. complete as per specifications in accordance with the approved shop drawings. No slip joints shall be allowed. Flanges shall be Rolamate or equivalent and ducts upto 1500 mm width shall be with rigid support (Gripple support to be provided wherever required) as per technical specifications. Ducts to be fabricated at the jobsite. Site Fabrication work shall be limited to assembly, installation and suit to site pieces and collars droppers The quoted costs should include i) Ducts with reinforcement strengthening ii) Air tight joints iii) Accessories such as splitter, damper, guide vane etc. iv) Hangers and supports (Gripple Supporting method to be used wherever required) v) Painting with Black color paint for duct sides behind the grills. vii) Ducts shall be fully sealed with Silicon Sealant for leak tight installation. Ducts shall be leak pressure tested leakages should be within acceptable limits as specified at Min. 500 Pa | 0.80 mm (22 SWG) GSS ducting (751mm-1500mm) Supply, fabrication, installation and testing of MS SS metal ducts as per IS-277 (120 GSM both sides, LFQ confirming to Class VIII) for MS SS Sheets and IS-655 for fabrication of following thicknesses including necessary G.I. hangers supports, volume control duct dampers, accessories, vanes, 3 mm neoprene rubber gasket etc. complete as per specifications in accordance with the approved shop drawings. No slip joints shall be allowed. Flanges shall be Rolamate or equivalent and ducts upto 1500 mm width shall be with rigid support (Gripple support to be provided wherever required) as per technical specifications. Ducts to be fabricated at the jobsite. Site Fabrication work shall be limited to assembly, installation and suit to site pieces and collars droppers The quoted costs should include i) Ducts with reinforcement strengthening ii) Air tight joints iii) Accessories such as splitter, damper, guide vane etc. iv) Hangers and supports (Gripple Supporting method to be used wherever required) v) Painting with Black color paint for duct sides behind the grills. vii) Ducts shall be fully sealed with Silicon Sealant for leak tight installation. Ducts shall be leak pressure tested leakages should be within acceptable limits as specified at Min. 500 Pa | Sqmt | 130 | 188500 | 1869 | 242970 | 1450 | 188500 | 1450 | 188500
7 |  | 13 mm thick - Supplying and fixing of following thickness duly laminated aluminum foil of mat finish. (Make - Hira Technologies) | 13 mm thick - Supplying and fixing of following thickness duly laminated aluminum foil of mat finish. (Make - Hira Technologies) | Sqmt | 65 | 45500 | 760 | 49400 | 700 | 45500 | 950 | 61750
8 |  | Supply, installation and adjusting of GSS Volume Control Damper within ducts complete as specified and with suitable links, levers. Blades should be opposed blade type. The blades should be mounted in nylon bushes operated by an interior wheel gear system. Manual quadrant control with position indicator to be provided to enable adjust volume of air as required. | Supply, installation and adjusting of GSS Volume Control Damper within ducts complete as specified and with suitable links, levers. Blades should be opposed blade type. The blades should be mounted in nylon bushes operated by an interior wheel gear system. Manual quadrant control with position indicator to be provided to enable adjust volume of air as required. | Sqmt | 2 | 12000 | 7673 | 15346 | 6000 | 12000 | 7250 | 14500
9 |  | Supplying fixing of black mat finish extruded aluminium opposed blade volume control dampers in supply air duct collars as per approved shop drawings and specifications | Supplying fixing of black mat finish extruded aluminium opposed blade volume control dampers in supply air duct collars as per approved shop drawings and specifications | Nos | 6 | 16278 | 2713 | 16278 | 5000 | 30000 | 9500 | 57000
10 |  | 300mmX300mm - Extruded Aluminum Powder Coated Grilles Of Required Airflow Angles Without V.C.D- EP -00 15 30 with four side flanges as following sizes.- | 300mmX300mm - Extruded Aluminum Powder Coated Grilles Of Required Airflow Angles Without V.C.D- EP -00 15 30 with four side flanges as following sizes.- | Nos | 2 | 1488 | 744 | 1488 | 2000 | 4000 | 2450 | 4900
11 |  | 150mm Width - Extruded Aluminum Powder Coated Continuous Linear Grilles Of Required Airflow Angles Without V.C.D- EP -00 15 30 with four side flanges as per requirements. | 150mm Width - Extruded Aluminum Powder Coated Continuous Linear Grilles Of Required Airflow Angles Without V.C.D- EP -00 15 30 with four side flanges as per requirements. | Rmt | 8 | 11600 | 6588 | 52704 | 5000 | 40000 | 1450 | 11600

## Technical Score Detail
|  | RFQ No: R1645 COST COMPARISON REPORT | RFQ No: R1645 COST COMPARISON REPORT | RFQ No: R1645 COST COMPARISON REPORT | Comp. Date : 10/09/2024 | Comp. Date : 10/09/2024 | Comp. Date : 10/09/2024 | Vendor Name : Nova Hvac Systems (India) Pvt Ltd. |  | Vendor Name : APC Air Control |  | Vendor Name : ANJLE MEP PROJECT PVT LTD
|  | RFQ No: R1645 COST COMPARISON REPORT | RFQ No: R1645 COST COMPARISON REPORT | RFQ No: R1645 COST COMPARISON REPORT | RFQ #: R1645 | RFQ #: R1645 | RFQ #: R1645 | Contact Name : BILAL METKAR |  | Contact Name : Rajvinder |  | Contact Name : PREMKANT
|  | RFQ No: R1645 COST COMPARISON REPORT | RFQ No: R1645 COST COMPARISON REPORT | RFQ No: R1645 COST COMPARISON REPORT | RFQ Date : 09/09/2024 16:13:05 | RFQ Date : 09/09/2024 16:13:05 | RFQ Date : 09/09/2024 16:13:05 | Vendor City : |  | Vendor City : |  | Vendor City :
|  | RFQ No: R1645 COST COMPARISON REPORT | RFQ No: R1645 COST COMPARISON REPORT | RFQ No: R1645 COST COMPARISON REPORT | BCD Date : 10/09/2024 02:05:00 | BCD Date : 10/09/2024 02:05:00 | BCD Date : 10/09/2024 02:05:00 | Telephone # : |  | Telephone # : |  | Telephone # :
|  | RFQ No: R1645 COST COMPARISON REPORT | RFQ No: R1645 COST COMPARISON REPORT | RFQ No: R1645 COST COMPARISON REPORT |  |  |  | Mobile # : |  | Mobile # : 7837249094 |  | Mobile # :
PR Number : DCPL-2425-00104 | PR Number : DCPL-2425-00104 | PR Number : DCPL-2425-00104 | PR Number : DCPL-2425-00104 | PR Number : DCPL-2425-00104 | PR Number : DCPL-2425-00104 | PR Number : DCPL-2425-00104 | PR Number : DCPL-2425-00104 | Email : bilal.metkar@novainitiative.com |  | Email : apcmumbai@gmail.com |  | Email : anjlemepprojects@gmail.com
Package / RFQ Name : Ventilation Work- CC R City | Package / RFQ Name : Ventilation Work- CC R City | Package / RFQ Name : Ventilation Work- CC R City | Package / RFQ Name : Ventilation Work- CC R City | Package / RFQ Name : Ventilation Work- CC R City | Package / RFQ Name : Ventilation Work- CC R City | Package / RFQ Name : Ventilation Work- CC R City | Package / RFQ Name : Ventilation Work- CC R City | Round # : 6 (RFQ) |  | Round # : 6 (RFQ) |  | Round # : 6 (RFQ)
Buyer : Mrunal Joshi | Buyer : Mrunal Joshi | Buyer : Mrunal Joshi | Buyer : Mrunal Joshi | Buyer : Mrunal Joshi | Buyer : Mrunal Joshi | Buyer : Mrunal Joshi | Buyer : Mrunal Joshi | Quotation Date : |  | Quotation Date : |  | Quotation Date :
Comp. # : 6 | Comp. # : 6 | Comp. # : 6 | Comp. # : 6 | Comp. # : 6 | Currency :INR | Currency :INR | Currency :INR | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date :
Comp. # : 6 | Comp. # : 6 | Comp. # : 6 | Comp. # : 6 | Comp. # : 6 | BUDGET PRICE : | 1,425,000.00 |  | Quote Currency : |  | Quote Currency : |  | Quote Currency :
# | Item Code | Item Description | Last PO Details | Unit | Qty | Last PO Unit Rate | Last PO Total Value | Score | Justification | Score | Justification | Score | Justification
1 |  | Ventilation system |  | EA | 1.000 | 1425000.00 | 0.00
2 |  | Air quantity Static 5700 CFM 70 mm Supply, Installation,testing commissioning of the following Centrifugal Blower would be used to supply Exhaust Air into the Kitchen, Fan to have Backward inclined Blades, Impeller Should be statically and Dynamically Balanced, Motor to have Squirrel cage, to operate on 3Phase 50Hz AC supply, TEFC Class F Insulation, IE2 Type Motor - Crompton Siemens Make, Fan would be supplied with Anti Vibration Pads |  | Nos | 1.000 | 0.00 | 0.00
3 |  | Air quantity Static 4600 CFM 70 mm Supply, Installation,testing commissioning of the following Centrifugal Blower would be used to supply Exhaust Air into the Kitchen, Fan to have Backward inclined Blades, Impeller Should be statically and Dynamically Balanced, Motor to have Squirrel cage, to operate on 3Phase 50Hz AC supply, TEFC Class F Insulation, IE2 Type Motor - Crompton Siemens Make, Fan would be supplied with Anti Vibration Pads |  | Nos | 1.000 | 0.00 | 0.00
4 |  | Air quantity Static 9000 CFM 60 mm Supply, Installation,testing commissioning of the following Centrifugal Blower would be used to supply Fresh Air into the Kitchen, Fan to have Backward inclined Blades, Impeller Should be statically and Dynamically Balanced, Motor to have Squirrel cage, to operate on 3Phase 50Hz AC supply, TEFC Class F Insulation, IE2 Type Motor - Crompton Siemens Make, Fan would be supplied with Anti Vibration Pads |  | Nos | 1.000 | 0.00 | 0.00
5 |  | Exhaust Air Qty -5700CFM (Approved make - APC-DS-3) - Construction Made of 16 gauge galvanized sheet, high bake epoxy powder coated or 2 mm mild steel plate oil proof of IP 54. - Operating Voltage 220V 1Ph 50Hz - Power consumption 50 watts per module unit up to 5000 cfm. - Pre Filter Washable type aluminum mesh pre-filter - Ionizer spring loaded Tungsten wires to create high voltage DC field 12-13 kV - Collector Plate High grade Aluminum collector plates which should be alternatively charged positive negative with large collecting area. Collector cell should be of permanent type and slide out facility for easy removal for cleaning. - Insulator Teaflon insulator. - Access door to filter section shall be equipped with safety limit switch. |  | Nos | 1.000 | 0.00 | 0.00
6 |  | Exhaust Air Qty -4600CFM (Approved make - APC-DS-2) - Construction Made of 16 gauge galvanized sheet, high bake epoxy powder coated or 2 mm mild steel plate oil proof of IP 54. - Operating Voltage 220V 1Ph 50Hz - Power consumption 50 watts per module unit up to 5000 cfm. - Pre Filter Washable type aluminum mesh pre-filter - Ionizer spring loaded Tungsten wires to create high voltage DC field 12-13 kV - Collector Plate High grade Aluminum collector plates which should be alternatively charged positive negative with large collecting area. Collector cell should be of permanent type and slide out facility for easy removal for cleaning. - Insulator Teaflon insulator. - Access door to filter section shall be equipped with safety limit switch. |  | Nos | 1.000 | 0.00 | 0.00
7 |  | 0.80 mm (22 SWG) GSS ducting (751mm-1500mm) Supply, fabrication, installation and testing of MS SS metal ducts as per IS-277 (120 GSM both sides, LFQ confirming to Class VIII) for MS SS Sheets and IS-655 for fabrication of following thicknesses including necessary G.I. hangers supports, volume control duct dampers, accessories, vanes, 3 mm neoprene rubber gasket etc. complete as per specifications in accordance with the approved shop drawings. No slip joints shall be allowed. Flanges shall be Rolamate or equivalent and ducts upto 1500 mm width shall be with rigid support (Gripple support to be provided wherever required) as per technical specifications. Ducts to be fabricated at the jobsite. Site Fabrication work shall be limited to assembly, installation and suit to site pieces and collars droppers The quoted costs should include i) Ducts with reinforcement strengthening ii) Air tight joints iii) Accessories such as splitter, damper, guide vane etc. iv) Hangers and supports (Gripple Supporting method to be used wherever required) v) Painting with Black color paint for duct sides behind the grills. vii) Ducts shall be fully sealed with Silicon Sealant for leak tight installation. Ducts shall be leak pressure tested leakages should be within acceptable limits as specified at Min. 500 Pa |  | Sqmt | 130.000 | 0.00 | 0.00
8 |  | 13 mm thick - Supplying and fixing of following thickness duly laminated aluminum foil of mat finish. (Make - Hira Technologies) |  | Sqmt | 65.000 | 0.00 | 0.00
9 |  | Supply, installation and adjusting of GSS Volume Control Damper within ducts complete as specified and with suitable links, levers. Blades should be opposed blade type. The blades should be mounted in nylon bushes operated by an interior wheel gear system. Manual quadrant control with position indicator to be provided to enable adjust volume of air as required. |  | Sqmt | 2.000 | 0.00 | 0.00
10 |  | Supplying fixing of black mat finish extruded aluminium opposed blade volume control dampers in supply air duct collars as per approved shop drawings and specifications |  | Nos | 6.000 | 0.00 | 0.00
11 |  | 300mmX300mm - Extruded Aluminum Powder Coated Grilles Of Required Airflow Angles Without V.C.D- EP -00 15 30 with four side flanges as following sizes.- |  | Nos | 2.000 | 0.00 | 0.00
12 |  | 150mm Width - Extruded Aluminum Powder Coated Continuous Linear Grilles Of Required Airflow Angles Without V.C.D- EP -00 15 30 with four side flanges as per requirements. |  | Rmt | 8.000 | 0.00 | 0.00