## Price Comparison
|  | RFQ No: R2568 COST COMPARISON REPORT | RFQ No: R2568 COST COMPARISON REPORT | RFQ No: R2568 COST COMPARISON REPORT | Comp. Date : 06/01/2025 | Comp. Date : 06/01/2025 | Comp. Date : 06/01/2025 | Vendor Name : PIONEER PROJECT SOLUTION (RV242523827) | [5 empty] | Vendor Name : ANJLE MEP PROJECT PVT LTD (RV242523025) | [5 empty] | Vendor Name : CRYSTAL AIRCOOL (RV242522537)
|  | RFQ No: R2568 COST COMPARISON REPORT | RFQ No: R2568 COST COMPARISON REPORT | RFQ No: R2568 COST COMPARISON REPORT | RFQ #: R2568 | RFQ #: R2568 | RFQ #: R2568 | Contact Name : MOHD ASHRAF | [5 empty] | Contact Name : PREMKANT | [5 empty] | Contact Name : JOHN
|  | RFQ No: R2568 COST COMPARISON REPORT | RFQ No: R2568 COST COMPARISON REPORT | RFQ No: R2568 COST COMPARISON REPORT | RFQ Date : 04/01/2025 16:20:08 | RFQ Date : 04/01/2025 16:20:08 | RFQ Date : 04/01/2025 16:20:08 | Vendor City : | [5 empty] | Vendor City : | [5 empty] | Vendor City :
|  | RFQ No: R2568 COST COMPARISON REPORT | RFQ No: R2568 COST COMPARISON REPORT | RFQ No: R2568 COST COMPARISON REPORT | BCD Date : | BCD Date : | BCD Date : | Telephone # : | [5 empty] | Telephone # : | [5 empty] | Telephone # :
|  | RFQ No: R2568 COST COMPARISON REPORT | RFQ No: R2568 COST COMPARISON REPORT | RFQ No: R2568 COST COMPARISON REPORT |  |  |  | Mobile # : | [5 empty] | Mobile # : | [5 empty] | Mobile # :
PR Number : TFS GURGAON-2425-00035,TFS GURGAON-2425-00036,TFS GURGAON-2425-00041 | PR Number : TFS GURGAON-2425-00035,TFS GURGAON-2425-00036,TFS GURGAON-2425-00041 | PR Number : TFS GURGAON-2425-00035,TFS GURGAON-2425-00036,TFS GURGAON-2425-00041 | PR Number : TFS GURGAON-2425-00035,TFS GURGAON-2425-00036,TFS GURGAON-2425-00041 | PR Number : TFS GURGAON-2425-00035,TFS GURGAON-2425-00036,TFS GURGAON-2425-00041 | PR Number : TFS GURGAON-2425-00035,TFS GURGAON-2425-00036,TFS GURGAON-2425-00041 | PR Number : TFS GURGAON-2425-00035,TFS GURGAON-2425-00036,TFS GURGAON-2425-00041 | PR Number : TFS GURGAON-2425-00035,TFS GURGAON-2425-00036,TFS GURGAON-2425-00041 | Email : projectspioneer@gmail.com | [5 empty] | Email : anjlemepprojects@gmail.com | [5 empty] | Email : crystalhvac002@gmail.com
Package / RFQ Name : PR for HVAC, Fire & FAS for DEL GORDON RAMSAY T1.... | Package / RFQ Name : PR for HVAC, Fire & FAS for DEL GORDON RAMSAY T1.... | Package / RFQ Name : PR for HVAC, Fire & FAS for DEL GORDON RAMSAY T1.... | Package / RFQ Name : PR for HVAC, Fire & FAS for DEL GORDON RAMSAY T1.... | Package / RFQ Name : PR for HVAC, Fire & FAS for DEL GORDON RAMSAY T1.... | Package / RFQ Name : PR for HVAC, Fire & FAS for DEL GORDON RAMSAY T1.... | Package / RFQ Name : PR for HVAC, Fire & FAS for DEL GORDON RAMSAY T1.... | Package / RFQ Name : PR for HVAC, Fire & FAS for DEL GORDON RAMSAY T1.... | Round # : 3 (Auction) | [5 empty] | Round # : 3 (Auction) | [5 empty] | Round # : 3 (Auction)
Buyer : Pushpak Mahesh Shewale / Technical : / Approver : | Buyer : Pushpak Mahesh Shewale / Technical : / Approver : | Buyer : Pushpak Mahesh Shewale / Technical : / Approver : | Buyer : Pushpak Mahesh Shewale / Technical : / Approver : | Buyer : Pushpak Mahesh Shewale / Technical : / Approver : | Buyer : Pushpak Mahesh Shewale / Technical : / Approver : | Buyer : Pushpak Mahesh Shewale / Technical : / Approver : | Buyer : Pushpak Mahesh Shewale / Technical : / Approver : | Quotation Date : |  |  | Quotation Validity Date : |  |  | Quotation Date : |  |  | Quotation Validity Date : |  |  | Quotation Date : |  |  | Quotation Validity Date :
Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Currency :INR | Currency :INR | Currency :INR | Buyer Remark : . | [5 empty] | Buyer Remark : | [5 empty] | Buyer Remark :
Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | BUDGET PRICE : | .00 |  | Quote Currency : INR | [5 empty] | Quote Currency : INR | [5 empty] | Quote Currency : INR
# | Item Code | Item Description | Unit | Qty | Last PO Details | Lowest Unit Rate | Lowest Vendor | First Bid | Disc % | GST % | Technical | Unit Price | Total | First Bid | Disc % | GST % | Technical | Unit Price | Total | First Bid | Disc % | GST % | Technical | Unit Price | Total
1 | Hvac - High Side | Hvac - High Side | NOS | 1.00 |  | 435000.00 | PIONEER PROJECT SOLUTION | 445000.00 | 0.00 | 18.00 |  | 435,000.00 | 435,000.00 | 655000.00 | 0.00 | 28.00 |  | 530,600.00 | 530,600.00 | 1040000.00 | 0.00 | 18.00 |  | 500,000.00 | 500,000.00
2 | Hvac - Low Side | Hvac - Low Side | NOS | 1.00 |  | 455670.00 | PIONEER PROJECT SOLUTION | 482230.00 | 0.00 | 18.00 |  | 455,670.00 | 455,670.00 | 699390.00 | 0.00 | 18.00 |  | 495,050.00 | 495,050.00 | 1599850.00 | 0.00 | 18.00 |  | 500,000.00 | 500,000.00
3 | Fire Sprinkler | Fire Sprinkler System | NOS | 1.00 |  | 177400.00 | PIONEER PROJECT SOLUTION | 179200.00 | 0.00 | 18.00 |  | 177,400.00 | 177,400.00 | 209300.00 | 0.00 | 18.00 |  | 187,300.00 | 187,300.00 | 513030.00 | 0.00 | 18.00 |  | 302,880.00 | 302,880.00
4 | FAS | FAS | % | 1.00 |  | 150700.00 | PIONEER PROJECT SOLUTION | 162000.00 | 0.00 | 18.00 |  | 150,700.00 | 150,700.00 | 163700.00 | 0.00 | 18.00 |  | 155,000.00 | 155,000.00 | 355850.00 | 0.00 | 18.00 |  | 200,350.00 | 200,350.00
Item Total | [8 empty] | .00 | 219,378.60 |  |  | 1,218,770.00 |  | .00 | 598,942.00 |  |  | 1,367,950.00 |  | .00 | 5,315,338.80 |  |  | 1,503,230.00
Discount Total Value | [7 empty] | Grand Dis. Amt | .00 |  |  |  | .00 | Grand Dis. Amt | .00 |  |  |  | .00 | Grand Dis. Amt | .00 |  |  |  | .00
GST Total Amount | [12 empty] | 219,378.60 | [5 empty] | 299,291.00 | [5 empty] | 270,581.40
Net Landed Cost | [11 empty] | INR | 1,438,148.60 |  |  |  |  | INR | 1,667,241.00 |  |  |  |  | INR | 1,773,811.40
Vendor Status | [7 empty] | Round # : 3 (Auction) | Round # : 3 (Auction)
Sr No. | Vendor Code | Vendor Name | [5 empty] | Status | Remarks
1 | RV242523827 | PIONEER PROJECT SOLUTION | [5 empty] | Participate
2 | RV242522537 | CRYSTAL AIRCOOL | [5 empty] | Participate
3 | RV242523025 | ANJLE MEP PROJECT PVT LTD | [5 empty] | Participate

## BOQ Price Bid
|  | RFQ No: R2568 COST COMPARISON REPORT | RFQ No: R2568 COST COMPARISON REPORT | Comp. Date : 06/01/2025 | Comp. Date : 06/01/2025 | Comp. Date : 06/01/2025 | Vendor Name : PIONEER PROJECT SOLUTION | Vendor Name : PIONEER PROJECT SOLUTION | Vendor Name : ANJLE MEP PROJECT PVT LTD | Vendor Name : ANJLE MEP PROJECT PVT LTD | Vendor Name : CRYSTAL AIRCOOL | Vendor Name : CRYSTAL AIRCOOL
|  | RFQ No: R2568 COST COMPARISON REPORT | RFQ No: R2568 COST COMPARISON REPORT | RFQ #: R2568 | RFQ #: R2568 | RFQ #: R2568 | Contact Name : MOHD ASHRAF | Contact Name : MOHD ASHRAF | Contact Name : PREMKANT | Contact Name : PREMKANT | Contact Name : JOHN | Contact Name : JOHN
|  | RFQ No: R2568 COST COMPARISON REPORT | RFQ No: R2568 COST COMPARISON REPORT | RFQ Date : 04/01/2025 16:20:08 | RFQ Date : 04/01/2025 16:20:08 | RFQ Date : 04/01/2025 16:20:08 | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City :
|  | RFQ No: R2568 COST COMPARISON REPORT | RFQ No: R2568 COST COMPARISON REPORT | BCD Date : | BCD Date : | BCD Date : | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # :
|  | RFQ No: R2568 COST COMPARISON REPORT | RFQ No: R2568 COST COMPARISON REPORT |  |  |  | Mobile # : | Mobile # : | Mobile # : | Mobile # : | Mobile # : | Mobile # :
PR Number : TFS GURGAON-2425-00035,TFS GURGAON-2425-00036,TFS GURGAON-2425-00041 | PR Number : TFS GURGAON-2425-00035,TFS GURGAON-2425-00036,TFS GURGAON-2425-00041 | PR Number : TFS GURGAON-2425-00035,TFS GURGAON-2425-00036,TFS GURGAON-2425-00041 | PR Number : TFS GURGAON-2425-00035,TFS GURGAON-2425-00036,TFS GURGAON-2425-00041 | PR Number : TFS GURGAON-2425-00035,TFS GURGAON-2425-00036,TFS GURGAON-2425-00041 | PR Number : TFS GURGAON-2425-00035,TFS GURGAON-2425-00036,TFS GURGAON-2425-00041 | PR Number : TFS GURGAON-2425-00035,TFS GURGAON-2425-00036,TFS GURGAON-2425-00041 | Email : projectspioneer@gmail.com | Email : projectspioneer@gmail.com | Email : anjlemepprojects@gmail.com | Email : anjlemepprojects@gmail.com | Email : crystalhvac002@gmail.com | Email : crystalhvac002@gmail.com
Package / RFQ Name : PR for HVAC, Fire & FAS for DEL GORDON RAMSAY T1.... | Package / RFQ Name : PR for HVAC, Fire & FAS for DEL GORDON RAMSAY T1.... | Package / RFQ Name : PR for HVAC, Fire & FAS for DEL GORDON RAMSAY T1.... | Package / RFQ Name : PR for HVAC, Fire & FAS for DEL GORDON RAMSAY T1.... | Package / RFQ Name : PR for HVAC, Fire & FAS for DEL GORDON RAMSAY T1.... | Package / RFQ Name : PR for HVAC, Fire & FAS for DEL GORDON RAMSAY T1.... | Package / RFQ Name : PR for HVAC, Fire & FAS for DEL GORDON RAMSAY T1.... | Round # : 3 (Auction) | Round # : 3 (Auction) | Round # : 3 (Auction) | Round # : 3 (Auction) | Round # : 3 (Auction) | Round # : 3 (Auction)
Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score :
Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Currency :INR | Currency :INR | Currency :INR | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date :
Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | BUDGET PRICE :.00 | BUDGET PRICE :.00 | BUDGET PRICE :.00 | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date :
Sr No. | Item Code | Item Name | Item Description | UOM | Qty | Minimum Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount
1 | Hvac - High Side | Hvac - High Side | Hvac - High Side | NOS | 1.000 |  |  | 435,000.00 |  | 530,600.00 |  | 1,020,000.00
1 | A | CONNECTING INTEGRATING UNIT MEP SERVICES TO AIRPORT MEP SERVICES BUILDING | CONNECTING INTEGRATING UNIT MEP SERVICES TO AIRPORT MEP SERVICES BUILDING
2 | A.1 | If any termination or connection of the unit services is required outside the site location (i.e., connection termination of the MEP unit to the airport MEP service or airport external façade or roof, etc.), then the contractor has to work in consultation with the airport to plan, design, and detail such connections. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor is to make good on any penetrations after installation, including providing fire seals as required as per airport requirements. | If any termination or connection of the unit services is required outside the site location (i.e., connection termination of the MEP unit to the airport MEP service or airport external façade or roof, etc.), then the contractor has to work in consultation with the airport to plan, design, and detail such connections. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor is to make good on any penetrations after installation, including providing fire seals as required as per airport requirements.
3 | B | HVAC EQUIPMENTS | HVAC EQUIPMENTS
4 |  | VENTILATION FANS | VENTILATION FANS
5 | B.1 | Supply, Installation, Testing and Commissioning of Double Skinned ceiling suspended Kitchen Exhaust Air Fan of approved make with minimum 25 mm thick panels of minimum 40 Kg m3 density with 0.60 mm precoated GSS outer skin and 0.60 plain inner skin, Motor shall be of IE 3, the fan motor should be located outside of the hot air stream, Class H insulation. Fans should be AMCA certified for Air Sound. Manufacturer shall submit “Certificate of conformity for 250 deg for 2 hours operation as per EN12101-3 2002 issued by Internationally recognized Independent Fire Laboratory should be submitted along with type test report. The Type test report should clearly indicate the make of motor used during the testing and the same make model of motor should be supplied by the fan manufacture at the site. The unit shall be suitable for 400 ± 15 volts, 50 Hz, 3 phase AC supply. Including control panel and all necessary cabling and terminations. Quote shall be inclusive of all necessary mounting and fixing arrangements for the fan, including hanging arrangements with vibration isolation as required based on the site condition. Note External Static Pressure (ESP) is calculated based on design drawing however contractor to select fan to match with actual pressure drop based on site condition. Pressure drop calculation and selection to be submitted to consultant for review approval. The procurement shall be processed only after pressure drop calculations selections duly verified from the consultants. | Supply, Installation, Testing and Commissioning of Double Skinned ceiling suspended Kitchen Exhaust Air Fan of approved make with minimum 25 mm thick panels of minimum 40 Kg m3 density with 0.60 mm precoated GSS outer skin and 0.60 plain inner skin, Motor shall be of IE 3, the fan motor should be located outside of the hot air stream, Class H insulation. Fans should be AMCA certified for Air Sound. Manufacturer shall submit “Certificate of conformity for 250 deg for 2 hours operation as per EN12101-3 2002 issued by Internationally recognized Independent Fire Laboratory should be submitted along with type test report. The Type test report should clearly indicate the make of motor used during the testing and the same make model of motor should be supplied by the fan manufacture at the site. The unit shall be suitable for 400 ± 15 volts, 50 Hz, 3 phase AC supply. Including control panel and all necessary cabling and terminations. Quote shall be inclusive of all necessary mounting and fixing arrangements for the fan, including hanging arrangements with vibration isolation as required based on the site condition. Note External Static Pressure (ESP) is calculated based on design drawing however contractor to select fan to match with actual pressure drop based on site condition. Pressure drop calculation and selection to be submitted to consultant for review approval. The procurement shall be processed only after pressure drop calculations selections duly verified from the consultants.
6 | B.1.1 | 3500 CFM @ 600 PASCAL - ESP. | 3500 CFM @ 600 PASCAL - ESP. | Nos | 1.000 | 145,000.00 | 145000.00 | 145,000.00 | 165000.00 | 165,000.00 | 365000.00 | 365,000.00
7 | B.2 | Supply, installation, testing and commissioning of Double Skinned Ceiling Suspended Air Washer Units of approved make with minimum 25 mm thick panels of minimum 40 Kg m3 density with 0.60 mm precoated GSS outer skin and 0.60 plain inner skin, filter section with EU4 Pre Filter, mist eliminator located on the air leaving end, drain tank shall be 20 gauge SS304 grade, inlet makeup overflow connections with pump also considered. Fan shall be ACMA certified direct driven backward curved Plenum plug fan with aerofoil design blades including control panel. The Fan shall be suitable for 400 ± 15 volts, 50 Hz, 3 phase AC supply. Quote shall be inclusive of all necessary mounting and fixing arrangements for the equipment, including hanging arrangements with vibration isolation as required based on the hanging structure above. Note External Static Pressure (ESP) is calculated based on design drawing however contractor to select fan to match with actual pressure drop based on site condition. Pressure drop calculation and selection to be submitted to consultant for review approval. The procurement shall be processed only after pressure drop calculations selections duly verified from the consultants. | Supply, installation, testing and commissioning of Double Skinned Ceiling Suspended Air Washer Units of approved make with minimum 25 mm thick panels of minimum 40 Kg m3 density with 0.60 mm precoated GSS outer skin and 0.60 plain inner skin, filter section with EU4 Pre Filter, mist eliminator located on the air leaving end, drain tank shall be 20 gauge SS304 grade, inlet makeup overflow connections with pump also considered. Fan shall be ACMA certified direct driven backward curved Plenum plug fan with aerofoil design blades including control panel. The Fan shall be suitable for 400 ± 15 volts, 50 Hz, 3 phase AC supply. Quote shall be inclusive of all necessary mounting and fixing arrangements for the equipment, including hanging arrangements with vibration isolation as required based on the hanging structure above. Note External Static Pressure (ESP) is calculated based on design drawing however contractor to select fan to match with actual pressure drop based on site condition. Pressure drop calculation and selection to be submitted to consultant for review approval. The procurement shall be processed only after pressure drop calculations selections duly verified from the consultants.
8 | B.2.1 | 2800 CFM @ 300 PASCAL - ESP. | 2800 CFM @ 300 PASCAL - ESP. | Nos | 1.000 | 130,000.00 | 130000.00 | 130,000.00 | 155600.00 | 155,600.00 | 360000.00 | 360,000.00
9 |  | AIR CLEANING EQUIPMENTS | AIR CLEANING EQUIPMENTS
10 | B.3 | Supply, installation, testing and commissioning of Double Skinned ceiling suspended Dry Scrubber of approved make with minimum 25 mm thick panels of minimum 40 Kg m3 density with 0.60 mm precoated GSS outer skin and 0.60 plain inner skin, including EU4 Pre Filter, ionizer, collection plate .The Unit shall be suitable for 230V, 1 Phase, 50 Hz AC supply. Auto power cut-off when door is opened, short circuit, arc protection and auto restore power supply, Quote shall be inclusive of all necessary mounting and fixing arrangements for the equipment, including hanging arrangements with vibration isolation as required based on the hanging structure above. | Supply, installation, testing and commissioning of Double Skinned ceiling suspended Dry Scrubber of approved make with minimum 25 mm thick panels of minimum 40 Kg m3 density with 0.60 mm precoated GSS outer skin and 0.60 plain inner skin, including EU4 Pre Filter, ionizer, collection plate .The Unit shall be suitable for 230V, 1 Phase, 50 Hz AC supply. Auto power cut-off when door is opened, short circuit, arc protection and auto restore power supply, Quote shall be inclusive of all necessary mounting and fixing arrangements for the equipment, including hanging arrangements with vibration isolation as required based on the hanging structure above.
11 | B.3.1 | 3500 CFM | 3500 CFM | Nos | 1.000 | 160,000.00 | 160000.00 | 160,000.00 | 210000.00 | 210,000.00 | 295000.00 | 295,000.00
12 |  | General Guidelines Ducting 1) Ducting shall be in accordance with IS 655, Galvanised Iron sheet to be used for all ducting works. Thermal insulation on ducts shall be 19 mm thick. Closed cell Class “O” BS 476 Part 6-7 FM Approved nitrile rubber elastomeric insulation thermal conductivity 0.033 watts per meter-kelvin (W (M·K)) at 0°C for air conditioning ducting. 2) Thermal insulation on kitchen exhaust ducting shall be 80 mm thick Aluminium foil faced resin bonded fiber Glass wool of density not less than 48 kg m33) Thermal Insulation on Fresh air, Supply Air and Return Air shall be 19mm thick closed cell antimicrobial Class “O” BS 476 and part 6 7 FM approved nitrile rubber elastomeric insulation thermal conductivity 0.033 watts per meter-kelvin (W (M·K)) at 0°C.4) Appropriate number of trap doors shall be provided in kitchen exhaust ducting for oil grease cleaning purpose.5) Ducting installation with respect to fresh air intake, kitchen exhaust out from location up to louvers at façade shall be in the scope of concessioner including air washer, exhaust fan section dry scrubber etc.6) Each and every kitchen exhaust hood should be equipped with UL listed, wet chemical based, mechanically operated, automatic fire suppression system. Separate drawing to be submitted for Hood suppression system.8) Post completion of onsite work, concessionaire has to share testing and commissioning report with DIAL.9) Integration with Fire alarm system, so that AHU get switched off in case of any fire incident. 7) Supporting of ducting to be done with using angle 50x 50 x 5mm and tie rod of size minimum 10 mm dia As per duct size.10) For equipment placement structural details to be approved by structural consultant and same to be share with DIAL.11) Trap door with proper access to be provided for filter and copper coil cleaning.12) Kitchen ventilation shall comply to NFPA 96 guideline.Chilled Water Piping - 1. Chilled water piping shall be confirming to IS 1239 Part I class ‘C’ heavy and fitting shall be conforming to ASTM A-105,3000lbs socket weld end (up to 50mm) 1S 1239 Part-II HEAVY ASTM A-234 WPB, Gr.B butt weld fitting ( above 50nb pipe size)2. Piping connection should be socket welded up to 50nb size and shall be butt weld above 50nb pipe size. Pipe flanges should be confirming to ASTM A-105 # 150 SORF and flange dimension should be in accordance with ASME ANSI B 16.5 (150 SORF), fitting to fitting welding is not allowed. Nozzle connections thredolets weldolets are not allowed by puncturing the pipe. Only equal unequal Tee’s shall be used for branch connection from header. Socket weld end Tee should be used for branch connection (up-to -50nb pipe size) w.r.t to pressure gauge temperature gauge Air vent Drain point etc.3. Post installation clearance by DIAL, CHW piping shall be tested @15kgf cm2 hydrostatics pressure for 24hrs hold time and Testing should be witnessed to DIAL Team.4. Thermal insulation on CHW and condensate drain piping line shall be 25mm thick. Closed cell antimicrobial Class “O” BS 476 and part 6 7 FM approved nitrile rubber elastomeric insulation thermal conductivity 0.033 watts per meter-kelvin (W (M·K)) at 0°C.5. Condensate drain piping shall be complying to IS 4985 Class 3 UPVC pipe. Solvent cement complying with ASTM D2564 shall be used for joints.6. For ceiling suspended chilled water pipe Pipe should be hanged with tie rod of size minimum 10 mm dia. 7. Attached CHW P ID drawing sketch to be followed during onsite work. | General Guidelines Ducting 1) Ducting shall be in accordance with IS 655, Galvanised Iron sheet to be used for all ducting works. Thermal insulation on ducts shall be 19 mm thick. Closed cell Class “O” BS 476 Part 6-7 FM Approved nitrile rubber elastomeric insulation thermal conductivity 0.033 watts per meter-kelvin (W (M·K)) at 0°C for air conditioning ducting. 2) Thermal insulation on kitchen exhaust ducting shall be 80 mm thick Aluminium foil faced resin bonded fiber Glass wool of density not less than 48 kg m33) Thermal Insulation on Fresh air, Supply Air and Return Air shall be 19mm thick closed cell antimicrobial Class “O” BS 476 and part 6 7 FM approved nitrile rubber elastomeric insulation thermal conductivity 0.033 watts per meter-kelvin (W (M·K)) at 0°C.4) Appropriate number of trap doors shall be provided in kitchen exhaust ducting for oil grease cleaning purpose.5) Ducting installation with respect to fresh air intake, kitchen exhaust out from location up to louvers at façade shall be in the scope of concessioner including air washer, exhaust fan section dry scrubber etc.6) Each and every kitchen exhaust hood should be equipped with UL listed, wet chemical based, mechanically operated, automatic fire suppression system. Separate drawing to be submitted for Hood suppression system.8) Post completion of onsite work, concessionaire has to share testing and commissioning report with DIAL.9) Integration with Fire alarm system, so that AHU get switched off in case of any fire incident. 7) Supporting of ducting to be done with using angle 50x 50 x 5mm and tie rod of size minimum 10 mm dia As per duct size.10) For equipment placement structural details to be approved by structural consultant and same to be share with DIAL.11) Trap door with proper access to be provided for filter and copper coil cleaning.12) Kitchen ventilation shall comply to NFPA 96 guideline.Chilled Water Piping - 1. Chilled water piping shall be confirming to IS 1239 Part I class ‘C’ heavy and fitting shall be conforming to ASTM A-105,3000lbs socket weld end (up to 50mm) 1S 1239 Part-II HEAVY ASTM A-234 WPB, Gr.B butt weld fitting ( above 50nb pipe size)2. Piping connection should be socket welded up to 50nb size and shall be butt weld above 50nb pipe size. Pipe flanges should be confirming to ASTM A-105 # 150 SORF and flange dimension should be in accordance with ASME ANSI B 16.5 (150 SORF), fitting to fitting welding is not allowed. Nozzle connections thredolets weldolets are not allowed by puncturing the pipe. Only equal unequal Tee’s shall be used for branch connection from header. Socket weld end Tee should be used for branch connection (up-to -50nb pipe size) w.r.t to pressure gauge temperature gauge Air vent Drain point etc.3. Post installation clearance by DIAL, CHW piping shall be tested @15kgf cm2 hydrostatics pressure for 24hrs hold time and Testing should be witnessed to DIAL Team.4. Thermal insulation on CHW and condensate drain piping line shall be 25mm thick. Closed cell antimicrobial Class “O” BS 476 and part 6 7 FM approved nitrile rubber elastomeric insulation thermal conductivity 0.033 watts per meter-kelvin (W (M·K)) at 0°C.5. Condensate drain piping shall be complying to IS 4985 Class 3 UPVC pipe. Solvent cement complying with ASTM D2564 shall be used for joints.6. For ceiling suspended chilled water pipe Pipe should be hanged with tie rod of size minimum 10 mm dia. 7. Attached CHW P ID drawing sketch to be followed during onsite work.
2 | Hvac - Low Side | Hvac - Low Side | Hvac - Low Side | NOS | 1.000 |  |  | 455,670.00 |  | 495,050.00 |  | 1,522,900.00
13 | C | AC PIPING AND ACCESSORIES | AC PIPING AND ACCESSORIES
14 |  | AC CONDENSATE DRAIN PIPE | AC CONDENSATE DRAIN PIPE
15 | C.1 | Supply, installation and testing of Rigid uPVC drain water piping of approved make with necessary supports and fittings like, U-traps, elbows, tees and reducers. | Supply, installation and testing of Rigid uPVC drain water piping of approved make with necessary supports and fittings like, U-traps, elbows, tees and reducers.
16 | C.1.1 | 32 mm Ø | 32 mm Ø | Mtr | 8.000 | 1,120.00 | 140.00 | 1,120.00 | 250.00 | 2,000.00 | 300.00 | 2,400.00
17 | D | AIR DISTRIBUTION DUCTS | AIR DISTRIBUTION DUCTS
18 |  | RECTANGULAR DUCTS | RECTANGULAR DUCTS
19 | D.1 | Supply, installation and testing of Galvanized Iron (GI) Galvanized Steel (GS) 120GSM Zinc coated factory fabricated Square Rectangular Ducts of approved make with all necessary fittings, connections, vanes, flanges, bracings, gaskets, duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, slotted rails, threaded rods, anchor bolts, nuts, bolts, structural beam clamps as applicable. The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport local regulatory or approval body having jurisdiction. | Supply, installation and testing of Galvanized Iron (GI) Galvanized Steel (GS) 120GSM Zinc coated factory fabricated Square Rectangular Ducts of approved make with all necessary fittings, connections, vanes, flanges, bracings, gaskets, duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, slotted rails, threaded rods, anchor bolts, nuts, bolts, structural beam clamps as applicable. The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport local regulatory or approval body having jurisdiction.
20 | D.1.1 | 24 Gauge - (0.70 mm Thick) - Supply Air Duct | 24 Gauge - (0.70 mm Thick) - Supply Air Duct | Sq.mtr | 55.000 | 63,250.00 | 1250.00 | 68,750.00 | 1150.00 | 63,250.00 | 2650.00 | 145,750.00
21 | D.1.2 | 24 Gauge - (0.70 mm Thick) - Return Air Duct | 24 Gauge - (0.70 mm Thick) - Return Air Duct | Sq.mtr | 6.000 | 6,900.00 | 1250.00 | 7,500.00 | 1150.00 | 6,900.00 | 2650.00 | 15,900.00
22 | D.1.3 | 24 Gauge - (0.70 mm Thick) - Fresh Air Duct | 24 Gauge - (0.70 mm Thick) - Fresh Air Duct | Sq.mtr | 45.000 | 51,750.00 | 1250.00 | 56,250.00 | 1150.00 | 51,750.00 | 2750.00 | 123,750.00
23 | D.1.4 | 22 Gauge - (0.85 mm Thick) - Fresh Air Duct | 22 Gauge - (0.85 mm Thick) - Fresh Air Duct | Sq.mtr | 4.000 | 5,400.00 | 1350.00 | 5,400.00 | 1350.00 | 5,400.00 | 3650.00 | 14,600.00
24 | D.2 | Supply, installation and testing of Mild Steel (MS) Ducts fabricated with hot rolled or cold rolled black steel sheets Square Rectangular Ducts of approved make with fully welded leak proof construction with Fire rated spay coat conforming to NFPA 96 Standards. with all necessary fittings, connections, vanes, flanges, bracings, gaskets, duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, threaded rods, anchor bolts, nuts, bolts, structural beam clamps as applicable. Duct and all other accessories shall be fire resistant, The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport local regulatory or approval body having jurisdiction. | Supply, installation and testing of Mild Steel (MS) Ducts fabricated with hot rolled or cold rolled black steel sheets Square Rectangular Ducts of approved make with fully welded leak proof construction with Fire rated spay coat conforming to NFPA 96 Standards. with all necessary fittings, connections, vanes, flanges, bracings, gaskets, duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, threaded rods, anchor bolts, nuts, bolts, structural beam clamps as applicable. Duct and all other accessories shall be fire resistant, The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport local regulatory or approval body having jurisdiction.
25 | D.2.1 | 18 Gauge - (1.21 mm Thick) - Kitchen Exhaust Air Duct | 18 Gauge - (1.21 mm Thick) - Kitchen Exhaust Air Duct | Sq.mtr | 39.000 | 56,550.00 | 1550.00 | 60,450.00 | 1450.00 | 56,550.00 | 3750.00 | 146,250.00
26 |  | ROUND DUCTS | ROUND DUCTS
27 | D.3 | Supply, installation, and testing of Galvanized Iron (GI) Galvanized Steel (GS) 120GSM Zinc coated factory fabricated Round Ducts of approved makes with all necessary fittings, round connectors, duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, slotted rails, threaded rods, anchor bolts, nuts, bolts, structural beam clamps as applicable. The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport local regulatory or approval body having jurisdiction. | Supply, installation, and testing of Galvanized Iron (GI) Galvanized Steel (GS) 120GSM Zinc coated factory fabricated Round Ducts of approved makes with all necessary fittings, round connectors, duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, slotted rails, threaded rods, anchor bolts, nuts, bolts, structural beam clamps as applicable. The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport local regulatory or approval body having jurisdiction.
28 | D.3.1 | 24 Gauge - (0.70 mm Thick) - Supply Air Duct | 24 Gauge - (0.70 mm Thick) - Supply Air Duct | Sq.mtr | 7.000 | 8,050.00 | 1550.00 | 10,850.00 | 1150.00 | 8,050.00 | 3750.00 | 26,250.00
29 |  | DUCT ACCESS DOORS | DUCT ACCESS DOORS
30 | D.4 | Supply, installation, and testing of Hinged type Duct Access Doors as per drawings and to allow easy and convenient access to equipment or any other component within ductwork with all necessary fittings, accessories and airtight gaskets etc. | Supply, installation, and testing of Hinged type Duct Access Doors as per drawings and to allow easy and convenient access to equipment or any other component within ductwork with all necessary fittings, accessories and airtight gaskets etc.
31 | D.4.1 | 300 mm X 300 mm - (MS) | 300 mm X 300 mm - (MS) | Nos | 5.000 | 7,000.00 | 1400.00 | 7,000.00 | 1650.00 | 8,250.00 | 8500.00 | 42,500.00
32 |  | FLEXIBLE DUCTS | FLEXIBLE DUCTS
33 | D.5 | Supply, installation, and testing of aluminum-polyester casing Round Insulated Flexible Duct of approved make reinforced with spiral wound steel wire, Temperature range -20° C to +140° C, with a standard Insulation with a 25mm thick mineral wool, covered with aluminum-polyester film casing and with all necessary connections, fixing and support arrangements. | Supply, installation, and testing of aluminum-polyester casing Round Insulated Flexible Duct of approved make reinforced with spiral wound steel wire, Temperature range -20° C to +140° C, with a standard Insulation with a 25mm thick mineral wool, covered with aluminum-polyester film casing and with all necessary connections, fixing and support arrangements.
34 | D.5.1 | 250 mm Ø | 250 mm Ø | Mtr | 5.000 | 2,750.00 | 550.00 | 2,750.00 | 1050.00 | 5,250.00 | 2950.00 | 14,750.00
35 | D.6 | Supply, installation, and testing of Flexible Duct Connectors (Canvas connection) of approved make to isolate vibrations and noises caused by fans or any other equipment s connected to the duct with air tight fittings with all necessary accessories. | Supply, installation, and testing of Flexible Duct Connectors (Canvas connection) of approved make to isolate vibrations and noises caused by fans or any other equipment s connected to the duct with air tight fittings with all necessary accessories.
36 | D.6.1 | For Air Washer Unit | For Air Washer Unit | Nos | 2.000 | 5,300.00 | 2650.00 | 5,300.00 | 2650.00 | 5,300.00 | 15500.00 | 31,000.00
37 | D.6.2 | For Kitchen Exhaust air Fan | For Kitchen Exhaust air Fan | Nos | 2.000 | 5,300.00 | 2650.00 | 5,300.00 | 2650.00 | 5,300.00 | 18500.00 | 37,000.00
38 | E | AIR DISTRIBUTION DUCT - THERMAL INSULATIONS ACCOUSTIC LINNINGS | AIR DISTRIBUTION DUCT - THERMAL INSULATIONS ACCOUSTIC LINNINGS
39 |  | AIR DISTRIBUTION DUCT - THERMAL INSULATIONS | AIR DISTRIBUTION DUCT - THERMAL INSULATIONS
40 | E.1 | Supply, installation of Thermal Insulation of approved make for duct insulation using closed-cell elastomeric nitrile rubber Class O rated as per BS 476 Part 6 1989 for fire propagation test and for Class 1 as per BS 476 Part 7, 1987 for surface spread of flame test. Water vapour permeability shall be not less than 0.024 per inch (2.48 x 10-13 Kg m.s.Pa i.e. µ>7000 Water Vapor diffusion resistance) as per DIN 53122 part 2, DIN 52615 EN 12086 EN13469. Insulaton shall be black Colour with having a density of 50 ± 10 Kg M3. Quote shall be inclusive of necessary Adhesive. | Supply, installation of Thermal Insulation of approved make for duct insulation using closed-cell elastomeric nitrile rubber Class O rated as per BS 476 Part 6 1989 for fire propagation test and for Class 1 as per BS 476 Part 7, 1987 for surface spread of flame test. Water vapour permeability shall be not less than 0.024 per inch (2.48 x 10-13 Kg m.s.Pa i.e. µ>7000 Water Vapor diffusion resistance) as per DIN 53122 part 2, DIN 52615 EN 12086 EN13469. Insulaton shall be black Colour with having a density of 50 ± 10 Kg M3. Quote shall be inclusive of necessary Adhesive.
41 | E.1.1 | 25 mm thicknesses | 25 mm thicknesses | Sq.mtr | 117.000 | 76,050.00 | 650.00 | 76,050.00 | 850.00 | 99,450.00 | 2450.00 | 286,650.00
42 | E.2 | Supply, installation of Thermal Insulation of approved make for Kitchen exhaust ducting using Resin Bonded Fibre Glass Wool (Asbestos Free) with Aluminum Foil covering, density of not less than 48 Kg m3. Quoute shall be inclusive of necessary Adhesive. | Supply, installation of Thermal Insulation of approved make for Kitchen exhaust ducting using Resin Bonded Fibre Glass Wool (Asbestos Free) with Aluminum Foil covering, density of not less than 48 Kg m3. Quoute shall be inclusive of necessary Adhesive.
43 | E.2.1 | 80 mm thicknesses - For Kitchen Exhaust | 80 mm thicknesses - For Kitchen Exhaust | Sq.mtr | 39.000 | 40,950.00 | 1050.00 | 40,950.00 | 1050.00 | 40,950.00 | 2900.00 | 113,100.00
44 | F | AIR DISTRIBUTION DUCT - DAMPERS | AIR DISTRIBUTION DUCT - DAMPERS
45 |  | DUCT AIR CONTROL DAMPERS | DUCT AIR CONTROL DAMPERS
46 | F.1 | Supply, installation, testing and commissioning of aluminum powder coated Opposed Blade Damper Collar Damper of approved make. | Supply, installation, testing and commissioning of aluminum powder coated Opposed Blade Damper Collar Damper of approved make.
47 | F.1.1 | Size - 300 x 300 mm | Size - 300 x 300 mm | Nos | 9.000 | 10,800.00 | 1200.00 | 10,800.00 | 1450.00 | 13,050.00 | 7000.00 | 63,000.00
48 | F.1.2 | Size - 375 x 375 mm | Size - 375 x 375 mm | Nos | 4.000 | 5,600.00 | 1400.00 | 5,600.00 | 1850.00 | 7,400.00 | 8000.00 | 32,000.00
49 | F.2 | Supply, installation, testing and commissioning of Aluminium powder coated Low Leakage Square Rectangular Volume Control Damper of approved make with aero-foil opposed blades and nylon gears system outside air stream with adjustable handle with position arresting bolt. | Supply, installation, testing and commissioning of Aluminium powder coated Low Leakage Square Rectangular Volume Control Damper of approved make with aero-foil opposed blades and nylon gears system outside air stream with adjustable handle with position arresting bolt.
50 | F.2.1 | Size - 350 x 200 mm | Size - 350 x 200 mm | Nos | 2.000 | 3,000.00 | 1500.00 | 3,000.00 | 2050.00 | 4,100.00 | 7000.00 | 14,000.00
51 | F.2.2 | Size - 550 x 250 mm | Size - 550 x 250 mm | Nos | 2.000 | 3,600.00 | 1800.00 | 3,600.00 | 2250.00 | 4,500.00 | 8000.00 | 16,000.00
52 | F.2.3 | Size - 300 x 200 mm | Size - 300 x 200 mm | Nos | 2.000 | 2,800.00 | 1400.00 | 2,800.00 | 1650.00 | 3,300.00 | 6500.00 | 13,000.00
53 | F.3 | Supply, installation, testing and commissioning of MS powder coated Low Leakage Square Rectangular Volume Control Damper of approved make with aero-foil opposed blades and nylon gears system outside air stream with adjustable handle with position arresting bolt. (For Kitchen Exhaust MS duct) | Supply, installation, testing and commissioning of MS powder coated Low Leakage Square Rectangular Volume Control Damper of approved make with aero-foil opposed blades and nylon gears system outside air stream with adjustable handle with position arresting bolt. (For Kitchen Exhaust MS duct)
54 | F.3.1 | Size - 500 x 400 mm | Size - 500 x 400 mm | Nos | 1.000 | 2,400.00 | 2400.00 | 2,400.00 | 2850.00 | 2,850.00 | 7000.00 | 7,000.00
55 | F.3.2 | Size - 450 x 250 mm | Size - 450 x 250 mm | Nos | 4.000 | 8,800.00 | 2200.00 | 8,800.00 | 2600.00 | 10,400.00 | 9000.00 | 36,000.00
56 | F.4 | Supply, installation, testing and commissioning of Circular Volume Control Damper of approved make with high quality Galvanized steel and Flap Blade fixed with nylon bushes, with hand locking quadrant. | Supply, installation, testing and commissioning of Circular Volume Control Damper of approved make with high quality Galvanized steel and Flap Blade fixed with nylon bushes, with hand locking quadrant.
57 | F.4.1 | Size - 250 mm Ø | Size - 250 mm Ø | Nos | 2.000 | 2,400.00 | 1200.00 | 2,400.00 | 1600.00 | 3,200.00 | 6000.00 | 12,000.00
58 | G | AIR TERMINALS - (GRILLES, REGISTERS, DIFFUSERS LOUVERS) | AIR TERMINALS - (GRILLES, REGISTERS, DIFFUSERS LOUVERS)
59 |  | DIFFUSERS | DIFFUSERS
60 | G.1 | Supply, installation, testing and commissioning of Extruded Aluminium Square Ceiling Diffuser of approved make with Four way throw with all necessary fixing arrangements. Powder coated finish with RAL Colour as required by ID Designer Architect. | Supply, installation, testing and commissioning of Extruded Aluminium Square Ceiling Diffuser of approved make with Four way throw with all necessary fixing arrangements. Powder coated finish with RAL Colour as required by ID Designer Architect.
61 | G.1.1 | Neck Size - 300 mm X 300 mm (Outer Size - 440 mm X 440 mm) | Neck Size - 300 mm X 300 mm (Outer Size - 440 mm X 440 mm) | Nos | 17.000 | 30,600.00 | 1800.00 | 30,600.00 | 2050.00 | 34,850.00 | 5000.00 | 85,000.00
62 | G.1.2 | Neck Size - 375 mm X 375 mm (Outer Size - 600 mm X 600 mm) | Neck Size - 375 mm X 375 mm (Outer Size - 600 mm X 600 mm) | Nos | 4.000 | 8,000.00 | 2000.00 | 8,000.00 | 2250.00 | 9,000.00 | 5000.00 | 20,000.00
63 | H | DISMANTLING OF EXISTING DUCTS | DISMANTLING OF EXISTING DUCTS
64 | H.1 | Remove and dispose of the existing supply air duct branch, fittings, insulation, and supports etc. and install new duct sections to match the new design, including necessary supports and hangers. | Remove and dispose of the existing supply air duct branch, fittings, insulation, and supports etc. and install new duct sections to match the new design, including necessary supports and hangers.
65 | H.1.1 | Dismantling of existing ducts | Dismantling of existing ducts | Lot | 1.000 | 25,000.00 | 25000.00 | 25,000.00 | 25000.00 | 25,000.00 | 100000.00 | 100,000.00
66 | J | HVAC SERVICE IDENTIFICATION LABELS, SIGNS TAGS | HVAC SERVICE IDENTIFICATION LABELS, SIGNS TAGS
67 | J.1 | All services like Ducts, Pipes need to be clearly labelled or tagged at site with service identification flow direction etc. And all equipment needs to tagged as per Airport requirements. | All services like Ducts, Pipes need to be clearly labelled or tagged at site with service identification flow direction etc. And all equipment needs to tagged as per Airport requirements.
68 | J.1.1 | Labelling Tagging for Services and Equipment s | Labelling Tagging for Services and Equipment s | Lot | 1.000 | 5,000.00 | 5000.00 | 5,000.00 | 10000.00 | 10,000.00 | 125000.00 | 125,000.00
69 | K | TESTING AND BALANCING | TESTING AND BALANCING
70 | K.1 | Air balancing of Supply, Return, Fresh air and Exhaust air system to arrive as per design air flow rates | Air balancing of Supply, Return, Fresh air and Exhaust air system to arrive as per design air flow rates
71 | L | SHOP DRAWINGS APPROVALS | SHOP DRAWINGS APPROVALS
72 | L.1 | Preparation and submission of a detailed shop drawing for the HVAC system after a thorough study of design drawings, site surveys, and relevant airport standards with correct routing, size, and elevations. The drawings also need to be coordinated with other MEP services like Electrical, Plumbing, and fire services, with the latest Architectural and Interior design drawings, before construction. Necessary amendments to the drawings are to be made and resubmitted in case of any variations on site while at the construction stage of the project. Also prepare relevant detailed connection drawings as per selected manufacturer details and Airport standards, with necessary approval to be obtained from consultants and authority regulatory bodies having jurisdiction, along with material submission approval with airport authorities. | Preparation and submission of a detailed shop drawing for the HVAC system after a thorough study of design drawings, site surveys, and relevant airport standards with correct routing, size, and elevations. The drawings also need to be coordinated with other MEP services like Electrical, Plumbing, and fire services, with the latest Architectural and Interior design drawings, before construction. Necessary amendments to the drawings are to be made and resubmitted in case of any variations on site while at the construction stage of the project. Also prepare relevant detailed connection drawings as per selected manufacturer details and Airport standards, with necessary approval to be obtained from consultants and authority regulatory bodies having jurisdiction, along with material submission approval with airport authorities.
73 | M | MISCELLANEOUS OR ANY ADDITIONAL ITEMS | MISCELLANEOUS OR ANY ADDITIONAL ITEMS
74 | M.1 | The contractor needs to mention any additional items or missing items that are not mentioned in the above BOQ after a detailed site survey or inspection and to be validated by consultants. | The contractor needs to mention any additional items or missing items that are not mentioned in the above BOQ after a detailed site survey or inspection and to be validated by consultants.
75 | M.1.1 | Item 1 - (Contractor to describe only if there are any) | Item 1 - (Contractor to describe only if there are any) | Unit | 1.000 | .00 | 0.00 | .00 | 2500.00 | 2,500.00 | 0.00 | .00
76 | M.1.2 | Item 2 - (Contractor to describe only if there are any) | Item 2 - (Contractor to describe only if there are any) | Unit | 1.000 | .00 | 0.00 | .00 | 3500.00 | 3,500.00 | 0.00 | .00
77 | M.1.3 | Item 3 - (Contractor to describe only if there are any) | Item 3 - (Contractor to describe only if there are any) | Unit | 1.000 | .00 | 0.00 | .00 | 3000.00 | 3,000.00 | 0.00 | .00
3 | Fire Sprinkler | Fire Sprinkler System | Fire Sprinkler System | NOS | 1.000 |  |  | 177,400.00 |  | 189,300.00 |  | 472,880.00
78 | A | CONNECTING INTEGRATING UNIT MEP SERVICES TO AIRPORT MEP SERVICES BUILDING | CONNECTING INTEGRATING UNIT MEP SERVICES TO AIRPORT MEP SERVICES BUILDING
79 | A.1 | If any termination or connection of the unit services is required outside the site location (i.e., connection termination of the MEP unit to the airport MEP service or airport external façade or roof, etc.), then the contractor has to work in consultation with the airport to plan, design, and detail such connections. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor is to make good on any penetrations after installation, including providing fire seals as required as per airport requirements. | If any termination or connection of the unit services is required outside the site location (i.e., connection termination of the MEP unit to the airport MEP service or airport external façade or roof, etc.), then the contractor has to work in consultation with the airport to plan, design, and detail such connections. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor is to make good on any penetrations after installation, including providing fire seals as required as per airport requirements.
80 | C | FIRE SPRINKLER SYSTEM AUTOMATIC FIRE SPRINKLER HEADS ACCESSORIES | FIRE SPRINKLER SYSTEM AUTOMATIC FIRE SPRINKLER HEADS ACCESSORIES
81 | C.1 | Supply, Installation, Testing Commissioning of Automatic Fire Sprinkler Heads (Bulb-type Sprinklers) of approved make with a standard temperature response with 5mm glass bulb, Temperature rating of 68° C 93° C, Nominal Thread size of 1 2 NPT (15mm) and a Orifice size of 13mm with a Max. Working Pressure of 12 Bar (Factory hydrostatic test pressure of 35 Bar) and to be Manufactured Certified to UL 199. The quote shall also include suspending arrangements with the ceiling, wall etc. | Supply, Installation, Testing Commissioning of Automatic Fire Sprinkler Heads (Bulb-type Sprinklers) of approved make with a standard temperature response with 5mm glass bulb, Temperature rating of 68° C 93° C, Nominal Thread size of 1 2 NPT (15mm) and a Orifice size of 13mm with a Max. Working Pressure of 12 Bar (Factory hydrostatic test pressure of 35 Bar) and to be Manufactured Certified to UL 199. The quote shall also include suspending arrangements with the ceiling, wall etc.
82 | C.1.1 | Pendant type of 79° C (Finishing - Chrome Plated) | Pendant type of 79° C (Finishing - Chrome Plated) | Nos | 4.000 | 4,200.00 | 1450.00 | 5,800.00 | 1050.00 | 4,200.00 | 2750.00 | 11,000.00
83 | C.2 | Supply, Installation, Testing Commissioning of Automatic Concealed Fire Sprinkler Heads (Bulb-type Sprinklers) of approved make with adjustable Escutcheon plates (Rosette plates). standard temperature response with 5mm glass bulb, Temperature rating of 68° C, Nominal Thread size of 1 2 NPT (15mm) and an Orifice size of 13mm with a Max. Working Pressure of 12 Bar (Factory hydrostatic test pressure of 35 Bar) and to be Manufactured Certified to UL 199. The quote shall also include suspending arrangements with the ceiling, wall etc. | Supply, Installation, Testing Commissioning of Automatic Concealed Fire Sprinkler Heads (Bulb-type Sprinklers) of approved make with adjustable Escutcheon plates (Rosette plates). standard temperature response with 5mm glass bulb, Temperature rating of 68° C, Nominal Thread size of 1 2 NPT (15mm) and an Orifice size of 13mm with a Max. Working Pressure of 12 Bar (Factory hydrostatic test pressure of 35 Bar) and to be Manufactured Certified to UL 199. The quote shall also include suspending arrangements with the ceiling, wall etc.
84 | C.2.1 | Concealed Pendant type of 68° C (Chrome Finish Plate Cover) | Concealed Pendant type of 68° C (Chrome Finish Plate Cover) | Nos | 25.000 | 56,250.00 | 2250.00 | 56,250.00 | 2250.00 | 56,250.00 | 2650.00 | 66,250.00
85 | C.3 | Supply, Installation, Testing Commissioning of Automatic Fire Sprinkler Heads (Bulb-type Sprinklers) of approved make with a standard temperature response with 5mm glass bulb, Temperature rating of 68° C 93° C, Nominal Thread size of 1 2 NPT (15mm) and a Orifice size of 13mm with a Max. Working Pressure of 12 Bar (Factory hydrostatic test pressure of 35 Bar) and to be Manufactured Certified to UL 199. The quote shall also include suspending arrangements with the ceiling, wall etc. | Supply, Installation, Testing Commissioning of Automatic Fire Sprinkler Heads (Bulb-type Sprinklers) of approved make with a standard temperature response with 5mm glass bulb, Temperature rating of 68° C 93° C, Nominal Thread size of 1 2 NPT (15mm) and a Orifice size of 13mm with a Max. Working Pressure of 12 Bar (Factory hydrostatic test pressure of 35 Bar) and to be Manufactured Certified to UL 199. The quote shall also include suspending arrangements with the ceiling, wall etc.
86 | C.3.1 | Upright type of 68° C (Finishing - Chrome Plated) | Upright type of 68° C (Finishing - Chrome Plated) | Nos | 5.000 | 4,750.00 | 1250.00 | 6,250.00 | 950.00 | 4,750.00 | 2300.00 | 11,500.00
87 |  | FIRE SPRINKLER PIPING | FIRE SPRINKLER PIPING
88 | C.4 | Supply, Installation, Testing Commissioning of MS C Class Fire Sprinkler Pipe confirming to IS 1239 with all fittings like bends, tees, flanges, nut, bolt and washers etc, and proper pipe supports to not more than 3 meter apart of the pipe length. The pipe work shall be hydrostatically tested for not less than 2 hours at 15 Bar (or 1.5 times the working) pressure without leak. The pipes are to be applied with 2 coats of primer (indicated film thickness, dry 50 microns) and 2 coats of enamel finish paint of approved colour (indicated film thickness, dry 30 microns) | Supply, Installation, Testing Commissioning of MS C Class Fire Sprinkler Pipe confirming to IS 1239 with all fittings like bends, tees, flanges, nut, bolt and washers etc, and proper pipe supports to not more than 3 meter apart of the pipe length. The pipe work shall be hydrostatically tested for not less than 2 hours at 15 Bar (or 1.5 times the working) pressure without leak. The pipes are to be applied with 2 coats of primer (indicated film thickness, dry 50 microns) and 2 coats of enamel finish paint of approved colour (indicated film thickness, dry 30 microns)
89 | C.4.1 | 25 mm Dia | 25 mm Dia | Mtr | 10.000 | 7,500.00 | 750.00 | 7,500.00 | 750.00 | 7,500.00 | 1280.00 | 12,800.00
90 | C.4.2 | 32 mm Dia | 32 mm Dia | Mtr | 5.000 | 4,750.00 | 950.00 | 4,750.00 | 950.00 | 4,750.00 | 1490.00 | 7,450.00
91 | C.4.3 | 50 mm Dia | 50 mm Dia | Mtr | 8.000 | 10,000.00 | 1250.00 | 10,000.00 | 1250.00 | 10,000.00 | 1860.00 | 14,880.00
92 | C.5 | Supply Fixing of UL Listed Stainless Steal Braided Flexible Sprinkler Hose with a working pressure of 12 Bar, Inlet Nipple(1 (25mm) BSPT NPT connection),Outlet Reducer (1 2 (15mm) BSPT NPT connection), Isolation Ring, Gasket, Snap Clamp, T-bar bracket (TBL or TBS),Stock bar and Nuts etc. | Supply Fixing of UL Listed Stainless Steal Braided Flexible Sprinkler Hose with a working pressure of 12 Bar, Inlet Nipple(1 (25mm) BSPT NPT connection),Outlet Reducer (1 2 (15mm) BSPT NPT connection), Isolation Ring, Gasket, Snap Clamp, T-bar bracket (TBL or TBS),Stock bar and Nuts etc.
93 | C.5.1 | Assembly Length of (1500 mm) | Assembly Length of (1500 mm) | Nos | 29.000 | 76,850.00 | 2650.00 | 76,850.00 | 2650.00 | 76,850.00 | 6000.00 | 174,000.00
94 | F | DISMANTLING OF EXISTING FIRE SPRINKLER PIPES | DISMANTLING OF EXISTING FIRE SPRINKLER PIPES
95 | F.1 | Remove and dispose of the existing fire sprinkler pipe branch, fittings and supports etc. and install new fire sprinkler pipe sections to match the new design, including necessary supports. | Remove and dispose of the existing fire sprinkler pipe branch, fittings and supports etc. and install new fire sprinkler pipe sections to match the new design, including necessary supports.
96 | F.1.1 | Dismantling of existing fire sprinkler pipe | Dismantling of existing fire sprinkler pipe | Lot | 1.000 | 10,000.00 | 10000.00 | 10,000.00 | 10000.00 | 10,000.00 | 65000.00 | 65,000.00
97 | G | TESTING AND BALANCING | TESTING AND BALANCING
98 | G.1 | Checking the functionality of all installed devices, conducting alarm tests, verifying proper communication between control panels and devices, and other systems. Testing should be done in the presence of Airport Concerned Persons. | Checking the functionality of all installed devices, conducting alarm tests, verifying proper communication between control panels and devices, and other systems. Testing should be done in the presence of Airport Concerned Persons. | LS | 1.000 | .00 | 0.00 | .00 | 5000.00 | 5,000.00 | 35000.00 | 35,000.00
99 | G.2 | Sprinkler pipe Pressure testing hydrostatic pressure test of no less than 14 bar (200PSI) for 2 hours with zero loss in pressure at the reference gauge or visual observation of a leak. Testing should be done in the presence of Airport Concerned Persons. | Sprinkler pipe Pressure testing hydrostatic pressure test of no less than 14 bar (200PSI) for 2 hours with zero loss in pressure at the reference gauge or visual observation of a leak. Testing should be done in the presence of Airport Concerned Persons. | LS | 1.000 | .00 | 0.00 | .00 | 5000.00 | 5,000.00 | 25000.00 | 25,000.00
100 | G.3 | Ensure all extinguishers are properly labelled, mounted, and ready for use. Training for staff on correct usage should be included. Testing should be done in the presence of Airport Concerned Persons. | Ensure all extinguishers are properly labelled, mounted, and ready for use. Training for staff on correct usage should be included. Testing should be done in the presence of Airport Concerned Persons. | LS | 1.000 | .00 | 0.00 | .00 | 5000.00 | 5,000.00 | 50000.00 | 50,000.00
4 | FAS | FAS | FAS | % | 1.000 |  |  | 150,700.00 |  | 155,000.00 |  | 338,350.00
101 | A | CONNECTING INTEGRATING UNIT MEP SERVICES TO AIRPORT MEP SERVICES BUILDING | CONNECTING INTEGRATING UNIT MEP SERVICES TO AIRPORT MEP SERVICES BUILDING
102 | A.1 | If any termination or connection of the unit services is required outside the site location (i.e., connection termination of the MEP unit to the airport MEP service or airport external façade or roof, etc.), then the contractor has to work in consultation with the airport to plan, design, and detail such connections. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor is to make good on any penetrations after installation, including providing fire seals as required as per airport requirements. | If any termination or connection of the unit services is required outside the site location (i.e., connection termination of the MEP unit to the airport MEP service or airport external façade or roof, etc.), then the contractor has to work in consultation with the airport to plan, design, and detail such connections. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor is to make good on any penetrations after installation, including providing fire seals as required as per airport requirements.
103 |  | FIRE ALARM SYSTEM - DETECTION DEVICES | FIRE ALARM SYSTEM - DETECTION DEVICES
104 | B.1 | Supply, Installation, Testing, and Commissioning of Addressable Type Optical Smoke Detector of approved make conforming by local fire authorities, with standard detector mounting Base, IP30 Ingress Protection, suitable area coverage (subject to local standard), 360° Angle Visibility, Operating Temperature (-10°C to +50°C), Approved by LPCB, with all necessary mounting and fixing arrangements. | Supply, Installation, Testing, and Commissioning of Addressable Type Optical Smoke Detector of approved make conforming by local fire authorities, with standard detector mounting Base, IP30 Ingress Protection, suitable area coverage (subject to local standard), 360° Angle Visibility, Operating Temperature (-10°C to +50°C), Approved by LPCB, with all necessary mounting and fixing arrangements.
105 | B.1.1 | Optical Smoke Detector | Optical Smoke Detector | Nos | 9.000 | 45,450.00 | 5050.00 | 45,450.00 | 5050.00 | 45,450.00 | 12000.00 | 108,000.00
106 | B.1.2 | Optical Smoke Detector (Above Ceiling) | Optical Smoke Detector (Above Ceiling) | Nos | 8.000 | 40,400.00 | 5050.00 | 40,400.00 | 5050.00 | 40,400.00 | 8000.00 | 64,000.00
107 | B.2 | Supply, Installation, Testing, and Commissioning of Addressable Type Fixed Temperature Heat Detector of approved make conforming by local fire authorities, with standard detector mounting base, IP30 Ingress Protection, suitable area coverage (subject to local standard), 360° Angle Visibility with suitable class approved by LPCB, with all necessary mounting and fixing arrangements. | Supply, Installation, Testing, and Commissioning of Addressable Type Fixed Temperature Heat Detector of approved make conforming by local fire authorities, with standard detector mounting base, IP30 Ingress Protection, suitable area coverage (subject to local standard), 360° Angle Visibility with suitable class approved by LPCB, with all necessary mounting and fixing arrangements.
108 | B.2.1 | Heat Detector - 79°C fixed temperature | Heat Detector - 79°C fixed temperature | Nos | 2.000 | 10,500.00 | 5250.00 | 10,500.00 | 5250.00 | 10,500.00 | 9000.00 | 18,000.00
109 | B.2.2 | Heat Detector - 79°C fixed temperature (Above Ceiling) | Heat Detector - 79°C fixed temperature (Above Ceiling) | Nos | 2.000 | 10,500.00 | 5250.00 | 10,500.00 | 5250.00 | 10,500.00 | 8000.00 | 16,000.00
110 | B.3 | Supply, Installation, Testing, and Commissioning of Addressable Type Manual Call Point Conforming to EN54 with Break glass, ABS material enclosure, IP30 Ingress Protection, Operating Temperature (-10°C to +50°C) of approved make along with suitable size 2 core cable clipped to structure wall ceiling through GI or Heavy Duty PVC Conduits with suitable cable clips saddles suitable for flush and surface mounting with all necessary mounting, termination and fixing arrangements. | Supply, Installation, Testing, and Commissioning of Addressable Type Manual Call Point Conforming to EN54 with Break glass, ABS material enclosure, IP30 Ingress Protection, Operating Temperature (-10°C to +50°C) of approved make along with suitable size 2 core cable clipped to structure wall ceiling through GI or Heavy Duty PVC Conduits with suitable cable clips saddles suitable for flush and surface mounting with all necessary mounting, termination and fixing arrangements.
111 | B.3.1 | Manual Call Point - (Wall Partition Mounted) | Manual Call Point - (Wall Partition Mounted) | Nos | 1.000 | 5,200.00 | 5200.00 | 5,200.00 | 5650.00 | 5,650.00 | 8000.00 | 8,000.00
112 |  | FIRE ALARM SYSTEM - AUDIBLE AND VISUAL NOTIFICATION DEVICES | FIRE ALARM SYSTEM - AUDIBLE AND VISUAL NOTIFICATION DEVICES
113 | B.4 | Supply, Installation, Testing and commissioning of Addressable type Sounder Strobe with inbuilt Isolator and operating temp (- 10 degrees to + 55 degrees) complete as required and duly approved by LPCB EN54 along with suitable size 2 core cable clipped to structure wall ceiling through GI or Heavy Duty PVC Conduits with suitable cable clips saddles. | Supply, Installation, Testing and commissioning of Addressable type Sounder Strobe with inbuilt Isolator and operating temp (- 10 degrees to + 55 degrees) complete as required and duly approved by LPCB EN54 along with suitable size 2 core cable clipped to structure wall ceiling through GI or Heavy Duty PVC Conduits with suitable cable clips saddles.
114 | B.4.1 | Sounder Strobe - (Wall Partition Mounted) | Sounder Strobe - (Wall Partition Mounted) | Nos | 1.000 | 5,500.00 | 5500.00 | 5,500.00 | 7250.00 | 7,250.00 | 12000.00 | 12,000.00
115 | B.5 | Supply, Installation, Testing, and Commissioning of Addressable Type Response Indicator of approved make conforming by local fire authorities with high bright LED, for Fire Detectors to indicate quickly the source of an alarm signal from detectors, which are not easily accessible or visible with IP30 Ingress Protection, Operating Temperature (-10°C to +50°C) approved by LPCB, with all necessary mounting and fixing arrangements. | Supply, Installation, Testing, and Commissioning of Addressable Type Response Indicator of approved make conforming by local fire authorities with high bright LED, for Fire Detectors to indicate quickly the source of an alarm signal from detectors, which are not easily accessible or visible with IP30 Ingress Protection, Operating Temperature (-10°C to +50°C) approved by LPCB, with all necessary mounting and fixing arrangements.
116 | B.5.1 | Response Indicator Remote Indicator | Response Indicator Remote Indicator | Nos | 10.000 | 2,500.00 | 350.00 | 3,500.00 | 250.00 | 2,500.00 | 3000.00 | 30,000.00
117 |  | FIRE ALARM SYSTEM - MODULE DEVICES | FIRE ALARM SYSTEM - MODULE DEVICES
118 | B.6 | Supply, Installation, Testing, and Commissioning of Addressable Type Isolator Module of approved make to identify the shorted and de-wired detectors and devices in the circuit duly approved by LPCB EN54, with all necessary mounting, termination and fixing arrangements. | Supply, Installation, Testing, and Commissioning of Addressable Type Isolator Module of approved make to identify the shorted and de-wired detectors and devices in the circuit duly approved by LPCB EN54, with all necessary mounting, termination and fixing arrangements.
119 | B.6.1 | Isolator Module | Isolator Module | Nos | 1.000 | 5,400.00 | 5400.00 | 5,400.00 | 5400.00 | 5,400.00 | 9000.00 | 9,000.00
120 | B.7 | Supply, Installation, Testing, and Commissioning of Addressable Type Control Module of approved make for connect other sources from fire Alarm Control Panel for evacuation purpose, Address Switch to program the modules, complete approved by LPCB EN54, with all necessary mounting, termination and fixing arrangements. | Supply, Installation, Testing, and Commissioning of Addressable Type Control Module of approved make for connect other sources from fire Alarm Control Panel for evacuation purpose, Address Switch to program the modules, complete approved by LPCB EN54, with all necessary mounting, termination and fixing arrangements.
121 | B.7.1 | Control Module | Control Module | Nos | 1.000 | 5,400.00 | 5400.00 | 5,400.00 | 8500.00 | 8,500.00 | 9000.00 | 9,000.00
122 |  | FIRE ALARM SYSTEM - CABLING | FIRE ALARM SYSTEM - CABLING
123 | B.8 | Supply, Installation, Testing and Commissioning FRLS FP200 PVC insulated and PVC sheathed armoured multi-stranded Copper conductor of approved make RED coloured cable clipped to structure wall ceiling through approved make GI or Heavy Duty PVC Conduits with suitable cable clips saddles suitable for flush and surface mounting with all necessary mounting, termination, tap-off connections and fixing arrangements. | Supply, Installation, Testing and Commissioning FRLS FP200 PVC insulated and PVC sheathed armoured multi-stranded Copper conductor of approved make RED coloured cable clipped to structure wall ceiling through approved make GI or Heavy Duty PVC Conduits with suitable cable clips saddles suitable for flush and surface mounting with all necessary mounting, termination, tap-off connections and fixing arrangements.
124 | B.8.1 | 2C x 1.5 Sq. mm Cu Cable | 2C x 1.5 Sq. mm Cu Cable | Mtr | 130.000 | 18,850.00 | 145.00 | 18,850.00 | 145.00 | 18,850.00 | 495.00 | 64,350.00

## Technical Score Detail
|  | RFQ No: R2568 COST COMPARISON REPORT | RFQ No: R2568 COST COMPARISON REPORT | RFQ No: R2568 COST COMPARISON REPORT | Comp. Date : 06/01/2025 | Comp. Date : 06/01/2025 | Comp. Date : 06/01/2025 | Vendor Name : PIONEER PROJECT SOLUTION |  | Vendor Name : ANJLE MEP PROJECT PVT LTD |  | Vendor Name : CRYSTAL AIRCOOL
|  | RFQ No: R2568 COST COMPARISON REPORT | RFQ No: R2568 COST COMPARISON REPORT | RFQ No: R2568 COST COMPARISON REPORT | RFQ #: R2568 | RFQ #: R2568 | RFQ #: R2568 | Contact Name : MOHD ASHRAF |  | Contact Name : PREMKANT |  | Contact Name : JOHN
|  | RFQ No: R2568 COST COMPARISON REPORT | RFQ No: R2568 COST COMPARISON REPORT | RFQ No: R2568 COST COMPARISON REPORT | RFQ Date : 04/01/2025 16:20:08 | RFQ Date : 04/01/2025 16:20:08 | RFQ Date : 04/01/2025 16:20:08 | Vendor City : |  | Vendor City : |  | Vendor City :
|  | RFQ No: R2568 COST COMPARISON REPORT | RFQ No: R2568 COST COMPARISON REPORT | RFQ No: R2568 COST COMPARISON REPORT | BCD Date : | BCD Date : | BCD Date : | Telephone # : |  | Telephone # : |  | Telephone # :
|  | RFQ No: R2568 COST COMPARISON REPORT | RFQ No: R2568 COST COMPARISON REPORT | RFQ No: R2568 COST COMPARISON REPORT |  |  |  | Mobile # : |  | Mobile # : |  | Mobile # :
PR Number : TFS GURGAON-2425-00035,TFS GURGAON-2425-00036,TFS GURGAON-2425-00041 | PR Number : TFS GURGAON-2425-00035,TFS GURGAON-2425-00036,TFS GURGAON-2425-00041 | PR Number : TFS GURGAON-2425-00035,TFS GURGAON-2425-00036,TFS GURGAON-2425-00041 | PR Number : TFS GURGAON-2425-00035,TFS GURGAON-2425-00036,TFS GURGAON-2425-00041 | PR Number : TFS GURGAON-2425-00035,TFS GURGAON-2425-00036,TFS GURGAON-2425-00041 | PR Number : TFS GURGAON-2425-00035,TFS GURGAON-2425-00036,TFS GURGAON-2425-00041 | PR Number : TFS GURGAON-2425-00035,TFS GURGAON-2425-00036,TFS GURGAON-2425-00041 | PR Number : TFS GURGAON-2425-00035,TFS GURGAON-2425-00036,TFS GURGAON-2425-00041 | Email : projectspioneer@gmail.com |  | Email : anjlemepprojects@gmail.com |  | Email : crystalhvac002@gmail.com
Package / RFQ Name : PR for HVAC, Fire & FAS for DEL GORDON RAMSAY T1.... | Package / RFQ Name : PR for HVAC, Fire & FAS for DEL GORDON RAMSAY T1.... | Package / RFQ Name : PR for HVAC, Fire & FAS for DEL GORDON RAMSAY T1.... | Package / RFQ Name : PR for HVAC, Fire & FAS for DEL GORDON RAMSAY T1.... | Package / RFQ Name : PR for HVAC, Fire & FAS for DEL GORDON RAMSAY T1.... | Package / RFQ Name : PR for HVAC, Fire & FAS for DEL GORDON RAMSAY T1.... | Package / RFQ Name : PR for HVAC, Fire & FAS for DEL GORDON RAMSAY T1.... | Package / RFQ Name : PR for HVAC, Fire & FAS for DEL GORDON RAMSAY T1.... | Round # : 3 (Auction) |  | Round # : 3 (Auction) |  | Round # : 3 (Auction)
Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Quotation Date : |  | Quotation Date : |  | Quotation Date :
Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Currency :INR | Currency :INR | Currency :INR | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date :
Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | Comp. # : 3 | BUDGET PRICE : | .00 |  | Quote Currency : |  | Quote Currency : |  | Quote Currency :
# | Item Code | Item Description | Last PO Details | Unit | Qty | Last PO Unit Rate | Last PO Total Value | Score | Justification | Score | Justification | Score | Justification
1 | Hvac - High Side | Hvac - High Side |  | NOS | 1.000 | 0.00 | 0.00
2 | A | CONNECTING INTEGRATING UNIT MEP SERVICES TO AIRPORT MEP SERVICES BUILDING |  |  | 0.000 | 0.00 | 0.00
3 | A.1 | If any termination or connection of the unit services is required outside the site location (i.e., connection termination of the MEP unit to the airport MEP service or airport external façade or roof, etc.), then the contractor has to work in consultation with the airport to plan, design, and detail such connections. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor is to make good on any penetrations after installation, including providing fire seals as required as per airport requirements. |  |  | 0.000 | 0.00 | 0.00
4 | B | HVAC EQUIPMENTS |  |  | 0.000 | 0.00 | 0.00
5 |  | VENTILATION FANS |  |  | 0.000 | 0.00 | 0.00
6 | B.1 | Supply, Installation, Testing and Commissioning of Double Skinned ceiling suspended Kitchen Exhaust Air Fan of approved make with minimum 25 mm thick panels of minimum 40 Kg m3 density with 0.60 mm precoated GSS outer skin and 0.60 plain inner skin, Motor shall be of IE 3, the fan motor should be located outside of the hot air stream, Class H insulation. Fans should be AMCA certified for Air Sound. Manufacturer shall submit “Certificate of conformity for 250 deg for 2 hours operation as per EN12101-3 2002 issued by Internationally recognized Independent Fire Laboratory should be submitted along with type test report. The Type test report should clearly indicate the make of motor used during the testing and the same make model of motor should be supplied by the fan manufacture at the site. The unit shall be suitable for 400 ± 15 volts, 50 Hz, 3 phase AC supply. Including control panel and all necessary cabling and terminations. Quote shall be inclusive of all necessary mounting and fixing arrangements for the fan, including hanging arrangements with vibration isolation as required based on the site condition. Note External Static Pressure (ESP) is calculated based on design drawing however contractor to select fan to match with actual pressure drop based on site condition. Pressure drop calculation and selection to be submitted to consultant for review approval. The procurement shall be processed only after pressure drop calculations selections duly verified from the consultants. |  |  | 0.000 | 0.00 | 0.00
7 | B.1.1 | 3500 CFM @ 600 PASCAL - ESP. |  | Nos | 1.000 | 0.00 | 0.00
8 | B.2 | Supply, installation, testing and commissioning of Double Skinned Ceiling Suspended Air Washer Units of approved make with minimum 25 mm thick panels of minimum 40 Kg m3 density with 0.60 mm precoated GSS outer skin and 0.60 plain inner skin, filter section with EU4 Pre Filter, mist eliminator located on the air leaving end, drain tank shall be 20 gauge SS304 grade, inlet makeup overflow connections with pump also considered. Fan shall be ACMA certified direct driven backward curved Plenum plug fan with aerofoil design blades including control panel. The Fan shall be suitable for 400 ± 15 volts, 50 Hz, 3 phase AC supply. Quote shall be inclusive of all necessary mounting and fixing arrangements for the equipment, including hanging arrangements with vibration isolation as required based on the hanging structure above. Note External Static Pressure (ESP) is calculated based on design drawing however contractor to select fan to match with actual pressure drop based on site condition. Pressure drop calculation and selection to be submitted to consultant for review approval. The procurement shall be processed only after pressure drop calculations selections duly verified from the consultants. |  |  | 0.000 | 0.00 | 0.00
9 | B.2.1 | 2800 CFM @ 300 PASCAL - ESP. |  | Nos | 1.000 | 0.00 | 0.00
10 |  | AIR CLEANING EQUIPMENTS |  |  | 0.000 | 0.00 | 0.00
11 | B.3 | Supply, installation, testing and commissioning of Double Skinned ceiling suspended Dry Scrubber of approved make with minimum 25 mm thick panels of minimum 40 Kg m3 density with 0.60 mm precoated GSS outer skin and 0.60 plain inner skin, including EU4 Pre Filter, ionizer, collection plate .The Unit shall be suitable for 230V, 1 Phase, 50 Hz AC supply. Auto power cut-off when door is opened, short circuit, arc protection and auto restore power supply, Quote shall be inclusive of all necessary mounting and fixing arrangements for the equipment, including hanging arrangements with vibration isolation as required based on the hanging structure above. |  |  | 0.000 | 0.00 | 0.00
12 | B.3.1 | 3500 CFM |  | Nos | 1.000 | 0.00 | 0.00
13 |  | General Guidelines Ducting 1) Ducting shall be in accordance with IS 655, Galvanised Iron sheet to be used for all ducting works. Thermal insulation on ducts shall be 19 mm thick. Closed cell Class “O” BS 476 Part 6-7 FM Approved nitrile rubber elastomeric insulation thermal conductivity 0.033 watts per meter-kelvin (W (M·K)) at 0°C for air conditioning ducting. 2) Thermal insulation on kitchen exhaust ducting shall be 80 mm thick Aluminium foil faced resin bonded fiber Glass wool of density not less than 48 kg m33) Thermal Insulation on Fresh air, Supply Air and Return Air shall be 19mm thick closed cell antimicrobial Class “O” BS 476 and part 6 7 FM approved nitrile rubber elastomeric insulation thermal conductivity 0.033 watts per meter-kelvin (W (M·K)) at 0°C.4) Appropriate number of trap doors shall be provided in kitchen exhaust ducting for oil grease cleaning purpose.5) Ducting installation with respect to fresh air intake, kitchen exhaust out from location up to louvers at façade shall be in the scope of concessioner including air washer, exhaust fan section dry scrubber etc.6) Each and every kitchen exhaust hood should be equipped with UL listed, wet chemical based, mechanically operated, automatic fire suppression system. Separate drawing to be submitted for Hood suppression system.8) Post completion of onsite work, concessionaire has to share testing and commissioning report with DIAL.9) Integration with Fire alarm system, so that AHU get switched off in case of any fire incident. 7) Supporting of ducting to be done with using angle 50x 50 x 5mm and tie rod of size minimum 10 mm dia As per duct size.10) For equipment placement structural details to be approved by structural consultant and same to be share with DIAL.11) Trap door with proper access to be provided for filter and copper coil cleaning.12) Kitchen ventilation shall comply to NFPA 96 guideline.Chilled Water Piping - 1. Chilled water piping shall be confirming to IS 1239 Part I class ‘C’ heavy and fitting shall be conforming to ASTM A-105,3000lbs socket weld end (up to 50mm) 1S 1239 Part-II HEAVY ASTM A-234 WPB, Gr.B butt weld fitting ( above 50nb pipe size)2. Piping connection should be socket welded up to 50nb size and shall be butt weld above 50nb pipe size. Pipe flanges should be confirming to ASTM A-105 # 150 SORF and flange dimension should be in accordance with ASME ANSI B 16.5 (150 SORF), fitting to fitting welding is not allowed. Nozzle connections thredolets weldolets are not allowed by puncturing the pipe. Only equal unequal Tee’s shall be used for branch connection from header. Socket weld end Tee should be used for branch connection (up-to -50nb pipe size) w.r.t to pressure gauge temperature gauge Air vent Drain point etc.3. Post installation clearance by DIAL, CHW piping shall be tested @15kgf cm2 hydrostatics pressure for 24hrs hold time and Testing should be witnessed to DIAL Team.4. Thermal insulation on CHW and condensate drain piping line shall be 25mm thick. Closed cell antimicrobial Class “O” BS 476 and part 6 7 FM approved nitrile rubber elastomeric insulation thermal conductivity 0.033 watts per meter-kelvin (W (M·K)) at 0°C.5. Condensate drain piping shall be complying to IS 4985 Class 3 UPVC pipe. Solvent cement complying with ASTM D2564 shall be used for joints.6. For ceiling suspended chilled water pipe Pipe should be hanged with tie rod of size minimum 10 mm dia. 7. Attached CHW P ID drawing sketch to be followed during onsite work. |  |  | 0.000 | 0.00 | 0.00
14 | Hvac - Low Side | Hvac - Low Side |  | NOS | 1.000 | 0.00 | 0.00
15 | C | AC PIPING AND ACCESSORIES |  |  | 0.000 | 0.00 | 0.00
16 |  | AC CONDENSATE DRAIN PIPE |  |  | 0.000 | 0.00 | 0.00
17 | C.1 | Supply, installation and testing of Rigid uPVC drain water piping of approved make with necessary supports and fittings like, U-traps, elbows, tees and reducers. |  |  | 0.000 | 0.00 | 0.00
18 | C.1.1 | 32 mm Ø |  | Mtr | 8.000 | 0.00 | 0.00
19 | D | AIR DISTRIBUTION DUCTS |  |  | 0.000 | 0.00 | 0.00
20 |  | RECTANGULAR DUCTS |  |  | 0.000 | 0.00 | 0.00
21 | D.1 | Supply, installation and testing of Galvanized Iron (GI) Galvanized Steel (GS) 120GSM Zinc coated factory fabricated Square Rectangular Ducts of approved make with all necessary fittings, connections, vanes, flanges, bracings, gaskets, duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, slotted rails, threaded rods, anchor bolts, nuts, bolts, structural beam clamps as applicable. The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport local regulatory or approval body having jurisdiction. |  |  | 0.000 | 0.00 | 0.00
22 | D.1.1 | 24 Gauge - (0.70 mm Thick) - Supply Air Duct |  | Sq.mtr | 55.000 | 0.00 | 0.00
23 | D.1.2 | 24 Gauge - (0.70 mm Thick) - Return Air Duct |  | Sq.mtr | 6.000 | 0.00 | 0.00
24 | D.1.3 | 24 Gauge - (0.70 mm Thick) - Fresh Air Duct |  | Sq.mtr | 45.000 | 0.00 | 0.00
25 | D.1.4 | 22 Gauge - (0.85 mm Thick) - Fresh Air Duct |  | Sq.mtr | 4.000 | 0.00 | 0.00
26 | D.2 | Supply, installation and testing of Mild Steel (MS) Ducts fabricated with hot rolled or cold rolled black steel sheets Square Rectangular Ducts of approved make with fully welded leak proof construction with Fire rated spay coat conforming to NFPA 96 Standards. with all necessary fittings, connections, vanes, flanges, bracings, gaskets, duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, threaded rods, anchor bolts, nuts, bolts, structural beam clamps as applicable. Duct and all other accessories shall be fire resistant, The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport local regulatory or approval body having jurisdiction. |  |  | 0.000 | 0.00 | 0.00
27 | D.2.1 | 18 Gauge - (1.21 mm Thick) - Kitchen Exhaust Air Duct |  | Sq.mtr | 39.000 | 0.00 | 0.00
28 |  | ROUND DUCTS |  |  | 0.000 | 0.00 | 0.00
29 | D.3 | Supply, installation, and testing of Galvanized Iron (GI) Galvanized Steel (GS) 120GSM Zinc coated factory fabricated Round Ducts of approved makes with all necessary fittings, round connectors, duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, slotted rails, threaded rods, anchor bolts, nuts, bolts, structural beam clamps as applicable. The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport local regulatory or approval body having jurisdiction. |  |  | 0.000 | 0.00 | 0.00
30 | D.3.1 | 24 Gauge - (0.70 mm Thick) - Supply Air Duct |  | Sq.mtr | 7.000 | 0.00 | 0.00
31 |  | DUCT ACCESS DOORS |  |  | 0.000 | 0.00 | 0.00
32 | D.4 | Supply, installation, and testing of Hinged type Duct Access Doors as per drawings and to allow easy and convenient access to equipment or any other component within ductwork with all necessary fittings, accessories and airtight gaskets etc. |  |  | 0.000 | 0.00 | 0.00
33 | D.4.1 | 300 mm X 300 mm - (MS) |  | Nos | 5.000 | 0.00 | 0.00
34 |  | FLEXIBLE DUCTS |  |  | 0.000 | 0.00 | 0.00
35 | D.5 | Supply, installation, and testing of aluminum-polyester casing Round Insulated Flexible Duct of approved make reinforced with spiral wound steel wire, Temperature range -20° C to +140° C, with a standard Insulation with a 25mm thick mineral wool, covered with aluminum-polyester film casing and with all necessary connections, fixing and support arrangements. |  |  | 0.000 | 0.00 | 0.00
36 | D.5.1 | 250 mm Ø |  | Mtr | 5.000 | 0.00 | 0.00
37 | D.6 | Supply, installation, and testing of Flexible Duct Connectors (Canvas connection) of approved make to isolate vibrations and noises caused by fans or any other equipment s connected to the duct with air tight fittings with all necessary accessories. |  |  | 0.000 | 0.00 | 0.00
38 | D.6.1 | For Air Washer Unit |  | Nos | 2.000 | 0.00 | 0.00
39 | D.6.2 | For Kitchen Exhaust air Fan |  | Nos | 2.000 | 0.00 | 0.00
40 | E | AIR DISTRIBUTION DUCT - THERMAL INSULATIONS ACCOUSTIC LINNINGS |  |  | 0.000 | 0.00 | 0.00
41 |  | AIR DISTRIBUTION DUCT - THERMAL INSULATIONS |  |  | 0.000 | 0.00 | 0.00
42 | E.1 | Supply, installation of Thermal Insulation of approved make for duct insulation using closed-cell elastomeric nitrile rubber Class O rated as per BS 476 Part 6 1989 for fire propagation test and for Class 1 as per BS 476 Part 7, 1987 for surface spread of flame test. Water vapour permeability shall be not less than 0.024 per inch (2.48 x 10-13 Kg m.s.Pa i.e. µ>7000 Water Vapor diffusion resistance) as per DIN 53122 part 2, DIN 52615 EN 12086 EN13469. Insulaton shall be black Colour with having a density of 50 ± 10 Kg M3. Quote shall be inclusive of necessary Adhesive. |  |  | 0.000 | 0.00 | 0.00
43 | E.1.1 | 25 mm thicknesses |  | Sq.mtr | 117.000 | 0.00 | 0.00
44 | E.2 | Supply, installation of Thermal Insulation of approved make for Kitchen exhaust ducting using Resin Bonded Fibre Glass Wool (Asbestos Free) with Aluminum Foil covering, density of not less than 48 Kg m3. Quoute shall be inclusive of necessary Adhesive. |  |  | 0.000 | 0.00 | 0.00
45 | E.2.1 | 80 mm thicknesses - For Kitchen Exhaust |  | Sq.mtr | 39.000 | 0.00 | 0.00
46 | F | AIR DISTRIBUTION DUCT - DAMPERS |  |  | 0.000 | 0.00 | 0.00
47 |  | DUCT AIR CONTROL DAMPERS |  |  | 0.000 | 0.00 | 0.00
48 | F.1 | Supply, installation, testing and commissioning of aluminum powder coated Opposed Blade Damper Collar Damper of approved make. |  |  | 0.000 | 0.00 | 0.00
49 | F.1.1 | Size - 300 x 300 mm |  | Nos | 9.000 | 0.00 | 0.00
50 | F.1.2 | Size - 375 x 375 mm |  | Nos | 4.000 | 0.00 | 0.00
51 | F.2 | Supply, installation, testing and commissioning of Aluminium powder coated Low Leakage Square Rectangular Volume Control Damper of approved make with aero-foil opposed blades and nylon gears system outside air stream with adjustable handle with position arresting bolt. |  |  | 0.000 | 0.00 | 0.00
52 | F.2.1 | Size - 350 x 200 mm |  | Nos | 2.000 | 0.00 | 0.00
53 | F.2.2 | Size - 550 x 250 mm |  | Nos | 2.000 | 0.00 | 0.00
54 | F.2.3 | Size - 300 x 200 mm |  | Nos | 2.000 | 0.00 | 0.00
55 | F.3 | Supply, installation, testing and commissioning of MS powder coated Low Leakage Square Rectangular Volume Control Damper of approved make with aero-foil opposed blades and nylon gears system outside air stream with adjustable handle with position arresting bolt. (For Kitchen Exhaust MS duct) |  |  | 0.000 | 0.00 | 0.00
56 | F.3.1 | Size - 500 x 400 mm |  | Nos | 1.000 | 0.00 | 0.00
57 | F.3.2 | Size - 450 x 250 mm |  | Nos | 4.000 | 0.00 | 0.00
58 | F.4 | Supply, installation, testing and commissioning of Circular Volume Control Damper of approved make with high quality Galvanized steel and Flap Blade fixed with nylon bushes, with hand locking quadrant. |  |  | 0.000 | 0.00 | 0.00
59 | F.4.1 | Size - 250 mm Ø |  | Nos | 2.000 | 0.00 | 0.00
60 | G | AIR TERMINALS - (GRILLES, REGISTERS, DIFFUSERS LOUVERS) |  |  | 0.000 | 0.00 | 0.00
61 |  | DIFFUSERS |  |  | 0.000 | 0.00 | 0.00
62 | G.1 | Supply, installation, testing and commissioning of Extruded Aluminium Square Ceiling Diffuser of approved make with Four way throw with all necessary fixing arrangements. Powder coated finish with RAL Colour as required by ID Designer Architect. |  |  | 0.000 | 0.00 | 0.00
63 | G.1.1 | Neck Size - 300 mm X 300 mm (Outer Size - 440 mm X 440 mm) |  | Nos | 17.000 | 0.00 | 0.00
64 | G.1.2 | Neck Size - 375 mm X 375 mm (Outer Size - 600 mm X 600 mm) |  | Nos | 4.000 | 0.00 | 0.00
65 | H | DISMANTLING OF EXISTING DUCTS |  |  | 0.000 | 0.00 | 0.00
66 | H.1 | Remove and dispose of the existing supply air duct branch, fittings, insulation, and supports etc. and install new duct sections to match the new design, including necessary supports and hangers. |  |  | 0.000 | 0.00 | 0.00
67 | H.1.1 | Dismantling of existing ducts |  | Lot | 1.000 | 0.00 | 0.00
68 | J | HVAC SERVICE IDENTIFICATION LABELS, SIGNS TAGS |  |  | 0.000 | 0.00 | 0.00
69 | J.1 | All services like Ducts, Pipes need to be clearly labelled or tagged at site with service identification flow direction etc. And all equipment needs to tagged as per Airport requirements. |  |  | 0.000 | 0.00 | 0.00
70 | J.1.1 | Labelling Tagging for Services and Equipment s |  | Lot | 1.000 | 0.00 | 0.00
71 | K | TESTING AND BALANCING |  |  | 0.000 | 0.00 | 0.00
72 | K.1 | Air balancing of Supply, Return, Fresh air and Exhaust air system to arrive as per design air flow rates |  |  | 0.000 | 0.00 | 0.00
73 | L | SHOP DRAWINGS APPROVALS |  |  | 0.000 | 0.00 | 0.00
74 | L.1 | Preparation and submission of a detailed shop drawing for the HVAC system after a thorough study of design drawings, site surveys, and relevant airport standards with correct routing, size, and elevations. The drawings also need to be coordinated with other MEP services like Electrical, Plumbing, and fire services, with the latest Architectural and Interior design drawings, before construction. Necessary amendments to the drawings are to be made and resubmitted in case of any variations on site while at the construction stage of the project. Also prepare relevant detailed connection drawings as per selected manufacturer details and Airport standards, with necessary approval to be obtained from consultants and authority regulatory bodies having jurisdiction, along with material submission approval with airport authorities. |  |  | 0.000 | 0.00 | 0.00
75 | M | MISCELLANEOUS OR ANY ADDITIONAL ITEMS |  |  | 0.000 | 0.00 | 0.00
76 | M.1 | The contractor needs to mention any additional items or missing items that are not mentioned in the above BOQ after a detailed site survey or inspection and to be validated by consultants. |  |  | 0.000 | 0.00 | 0.00
77 | M.1.1 | Item 1 - (Contractor to describe only if there are any) |  | Unit | 1.000 | 0.00 | 0.00
78 | M.1.2 | Item 2 - (Contractor to describe only if there are any) |  | Unit | 1.000 | 0.00 | 0.00
79 | M.1.3 | Item 3 - (Contractor to describe only if there are any) |  | Unit | 1.000 | 0.00 | 0.00
80 | Fire Sprinkler | Fire Sprinkler System |  | NOS | 1.000 | 0.00 | 0.00
81 | A | CONNECTING INTEGRATING UNIT MEP SERVICES TO AIRPORT MEP SERVICES BUILDING |  |  | 0.000 | 0.00 | 0.00
82 | A.1 | If any termination or connection of the unit services is required outside the site location (i.e., connection termination of the MEP unit to the airport MEP service or airport external façade or roof, etc.), then the contractor has to work in consultation with the airport to plan, design, and detail such connections. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor is to make good on any penetrations after installation, including providing fire seals as required as per airport requirements. |  |  | 0.000 | 0.00 | 0.00
83 | C | FIRE SPRINKLER SYSTEM AUTOMATIC FIRE SPRINKLER HEADS ACCESSORIES |  |  | 0.000 | 0.00 | 0.00
84 | C.1 | Supply, Installation, Testing Commissioning of Automatic Fire Sprinkler Heads (Bulb-type Sprinklers) of approved make with a standard temperature response with 5mm glass bulb, Temperature rating of 68° C 93° C, Nominal Thread size of 1 2 NPT (15mm) and a Orifice size of 13mm with a Max. Working Pressure of 12 Bar (Factory hydrostatic test pressure of 35 Bar) and to be Manufactured Certified to UL 199. The quote shall also include suspending arrangements with the ceiling, wall etc. |  |  | 0.000 | 0.00 | 0.00
85 | C.1.1 | Pendant type of 79° C (Finishing - Chrome Plated) |  | Nos | 4.000 | 0.00 | 0.00
86 | C.2 | Supply, Installation, Testing Commissioning of Automatic Concealed Fire Sprinkler Heads (Bulb-type Sprinklers) of approved make with adjustable Escutcheon plates (Rosette plates). standard temperature response with 5mm glass bulb, Temperature rating of 68° C, Nominal Thread size of 1 2 NPT (15mm) and an Orifice size of 13mm with a Max. Working Pressure of 12 Bar (Factory hydrostatic test pressure of 35 Bar) and to be Manufactured Certified to UL 199. The quote shall also include suspending arrangements with the ceiling, wall etc. |  |  | 0.000 | 0.00 | 0.00
87 | C.2.1 | Concealed Pendant type of 68° C (Chrome Finish Plate Cover) |  | Nos | 25.000 | 0.00 | 0.00
88 | C.3 | Supply, Installation, Testing Commissioning of Automatic Fire Sprinkler Heads (Bulb-type Sprinklers) of approved make with a standard temperature response with 5mm glass bulb, Temperature rating of 68° C 93° C, Nominal Thread size of 1 2 NPT (15mm) and a Orifice size of 13mm with a Max. Working Pressure of 12 Bar (Factory hydrostatic test pressure of 35 Bar) and to be Manufactured Certified to UL 199. The quote shall also include suspending arrangements with the ceiling, wall etc. |  |  | 0.000 | 0.00 | 0.00
89 | C.3.1 | Upright type of 68° C (Finishing - Chrome Plated) |  | Nos | 5.000 | 0.00 | 0.00
90 |  | FIRE SPRINKLER PIPING |  |  | 0.000 | 0.00 | 0.00
91 | C.4 | Supply, Installation, Testing Commissioning of MS C Class Fire Sprinkler Pipe confirming to IS 1239 with all fittings like bends, tees, flanges, nut, bolt and washers etc, and proper pipe supports to not more than 3 meter apart of the pipe length. The pipe work shall be hydrostatically tested for not less than 2 hours at 15 Bar (or 1.5 times the working) pressure without leak. The pipes are to be applied with 2 coats of primer (indicated film thickness, dry 50 microns) and 2 coats of enamel finish paint of approved colour (indicated film thickness, dry 30 microns) |  |  | 0.000 | 0.00 | 0.00
92 | C.4.1 | 25 mm Dia |  | Mtr | 10.000 | 0.00 | 0.00
93 | C.4.2 | 32 mm Dia |  | Mtr | 5.000 | 0.00 | 0.00
94 | C.4.3 | 50 mm Dia |  | Mtr | 8.000 | 0.00 | 0.00
95 | C.5 | Supply Fixing of UL Listed Stainless Steal Braided Flexible Sprinkler Hose with a working pressure of 12 Bar, Inlet Nipple(1 (25mm) BSPT NPT connection),Outlet Reducer (1 2 (15mm) BSPT NPT connection), Isolation Ring, Gasket, Snap Clamp, T-bar bracket (TBL or TBS),Stock bar and Nuts etc. |  |  | 0.000 | 0.00 | 0.00
96 | C.5.1 | Assembly Length of (1500 mm) |  | Nos | 29.000 | 0.00 | 0.00
97 | F | DISMANTLING OF EXISTING FIRE SPRINKLER PIPES |  |  | 0.000 | 0.00 | 0.00
98 | F.1 | Remove and dispose of the existing fire sprinkler pipe branch, fittings and supports etc. and install new fire sprinkler pipe sections to match the new design, including necessary supports. |  |  | 0.000 | 0.00 | 0.00
99 | F.1.1 | Dismantling of existing fire sprinkler pipe |  | Lot | 1.000 | 0.00 | 0.00
100 | G | TESTING AND BALANCING |  |  | 0.000 | 0.00 | 0.00
101 | G.1 | Checking the functionality of all installed devices, conducting alarm tests, verifying proper communication between control panels and devices, and other systems. Testing should be done in the presence of Airport Concerned Persons. |  | LS | 1.000 | 0.00 | 0.00
102 | G.2 | Sprinkler pipe Pressure testing hydrostatic pressure test of no less than 14 bar (200PSI) for 2 hours with zero loss in pressure at the reference gauge or visual observation of a leak. Testing should be done in the presence of Airport Concerned Persons. |  | LS | 1.000 | 0.00 | 0.00
103 | G.3 | Ensure all extinguishers are properly labelled, mounted, and ready for use. Training for staff on correct usage should be included. Testing should be done in the presence of Airport Concerned Persons. |  | LS | 1.000 | 0.00 | 0.00
104 | FAS | FAS |  | % | 1.000 | 0.00 | 0.00
105 | A | CONNECTING INTEGRATING UNIT MEP SERVICES TO AIRPORT MEP SERVICES BUILDING |  |  | 0.000 | 0.00 | 0.00
106 | A.1 | If any termination or connection of the unit services is required outside the site location (i.e., connection termination of the MEP unit to the airport MEP service or airport external façade or roof, etc.), then the contractor has to work in consultation with the airport to plan, design, and detail such connections. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor is to make good on any penetrations after installation, including providing fire seals as required as per airport requirements. |  |  | 0.000 | 0.00 | 0.00
107 |  | FIRE ALARM SYSTEM - DETECTION DEVICES |  |  | 0.000 | 0.00 | 0.00
108 | B.1 | Supply, Installation, Testing, and Commissioning of Addressable Type Optical Smoke Detector of approved make conforming by local fire authorities, with standard detector mounting Base, IP30 Ingress Protection, suitable area coverage (subject to local standard), 360° Angle Visibility, Operating Temperature (-10°C to +50°C), Approved by LPCB, with all necessary mounting and fixing arrangements. |  |  | 0.000 | 0.00 | 0.00
109 | B.1.1 | Optical Smoke Detector |  | Nos | 9.000 | 0.00 | 0.00
110 | B.1.2 | Optical Smoke Detector (Above Ceiling) |  | Nos | 8.000 | 0.00 | 0.00
111 | B.2 | Supply, Installation, Testing, and Commissioning of Addressable Type Fixed Temperature Heat Detector of approved make conforming by local fire authorities, with standard detector mounting base, IP30 Ingress Protection, suitable area coverage (subject to local standard), 360° Angle Visibility with suitable class approved by LPCB, with all necessary mounting and fixing arrangements. |  |  | 0.000 | 0.00 | 0.00
112 | B.2.1 | Heat Detector - 79°C fixed temperature |  | Nos | 2.000 | 0.00 | 0.00
113 | B.2.2 | Heat Detector - 79°C fixed temperature (Above Ceiling) |  | Nos | 2.000 | 0.00 | 0.00
114 | B.3 | Supply, Installation, Testing, and Commissioning of Addressable Type Manual Call Point Conforming to EN54 with Break glass, ABS material enclosure, IP30 Ingress Protection, Operating Temperature (-10°C to +50°C) of approved make along with suitable size 2 core cable clipped to structure wall ceiling through GI or Heavy Duty PVC Conduits with suitable cable clips saddles suitable for flush and surface mounting with all necessary mounting, termination and fixing arrangements. |  |  | 0.000 | 0.00 | 0.00
115 | B.3.1 | Manual Call Point - (Wall Partition Mounted) |  | Nos | 1.000 | 0.00 | 0.00
116 |  | FIRE ALARM SYSTEM - AUDIBLE AND VISUAL NOTIFICATION DEVICES |  |  | 0.000 | 0.00 | 0.00
117 | B.4 | Supply, Installation, Testing and commissioning of Addressable type Sounder Strobe with inbuilt Isolator and operating temp (- 10 degrees to + 55 degrees) complete as required and duly approved by LPCB EN54 along with suitable size 2 core cable clipped to structure wall ceiling through GI or Heavy Duty PVC Conduits with suitable cable clips saddles. |  |  | 0.000 | 0.00 | 0.00
118 | B.4.1 | Sounder Strobe - (Wall Partition Mounted) |  | Nos | 1.000 | 0.00 | 0.00
119 | B.5 | Supply, Installation, Testing, and Commissioning of Addressable Type Response Indicator of approved make conforming by local fire authorities with high bright LED, for Fire Detectors to indicate quickly the source of an alarm signal from detectors, which are not easily accessible or visible with IP30 Ingress Protection, Operating Temperature (-10°C to +50°C) approved by LPCB, with all necessary mounting and fixing arrangements. |  |  | 0.000 | 0.00 | 0.00
120 | B.5.1 | Response Indicator Remote Indicator |  | Nos | 10.000 | 0.00 | 0.00
121 |  | FIRE ALARM SYSTEM - MODULE DEVICES |  |  | 0.000 | 0.00 | 0.00
122 | B.6 | Supply, Installation, Testing, and Commissioning of Addressable Type Isolator Module of approved make to identify the shorted and de-wired detectors and devices in the circuit duly approved by LPCB EN54, with all necessary mounting, termination and fixing arrangements. |  |  | 0.000 | 0.00 | 0.00
123 | B.6.1 | Isolator Module |  | Nos | 1.000 | 0.00 | 0.00
124 | B.7 | Supply, Installation, Testing, and Commissioning of Addressable Type Control Module of approved make for connect other sources from fire Alarm Control Panel for evacuation purpose, Address Switch to program the modules, complete approved by LPCB EN54, with all necessary mounting, termination and fixing arrangements. |  |  | 0.000 | 0.00 | 0.00
125 | B.7.1 | Control Module |  | Nos | 1.000 | 0.00 | 0.00
126 |  | FIRE ALARM SYSTEM - CABLING |  |  | 0.000 | 0.00 | 0.00
127 | B.8 | Supply, Installation, Testing and Commissioning FRLS FP200 PVC insulated and PVC sheathed armoured multi-stranded Copper conductor of approved make RED coloured cable clipped to structure wall ceiling through approved make GI or Heavy Duty PVC Conduits with suitable cable clips saddles suitable for flush and surface mounting with all necessary mounting, termination, tap-off connections and fixing arrangements. |  |  | 0.000 | 0.00 | 0.00
128 | B.8.1 | 2C x 1.5 Sq. mm Cu Cable |  | Mtr | 130.000 | 0.00 | 0.00