## Price Comparison
|  | RFQ No: R2569 COST COMPARISON REPORT | RFQ No: R2569 COST COMPARISON REPORT | RFQ No: R2569 COST COMPARISON REPORT | Comp. Date : 06/01/2025 | Comp. Date : 06/01/2025 | Comp. Date : 06/01/2025 | Vendor Name : CHIRAG ELECTRICAL (RV242524030) | [5 empty] | Vendor Name : Arrow Electrical (RV242522534) | [5 empty] | Vendor Name : Electech Enterprises (RV232422514)
|  | RFQ No: R2569 COST COMPARISON REPORT | RFQ No: R2569 COST COMPARISON REPORT | RFQ No: R2569 COST COMPARISON REPORT | RFQ #: R2569 | RFQ #: R2569 | RFQ #: R2569 | Contact Name : MOHD AKIL | [5 empty] | Contact Name : SANTOSH KHAKE | [5 empty] | Contact Name : Alam
|  | RFQ No: R2569 COST COMPARISON REPORT | RFQ No: R2569 COST COMPARISON REPORT | RFQ No: R2569 COST COMPARISON REPORT | RFQ Date : 06/01/2025 13:21:47 | RFQ Date : 06/01/2025 13:21:47 | RFQ Date : 06/01/2025 13:21:47 | Vendor City : | [5 empty] | Vendor City : | [5 empty] | Vendor City :
|  | RFQ No: R2569 COST COMPARISON REPORT | RFQ No: R2569 COST COMPARISON REPORT | RFQ No: R2569 COST COMPARISON REPORT | BCD Date : 06/01/2025 15:01:00 | BCD Date : 06/01/2025 15:01:00 | BCD Date : 06/01/2025 15:01:00 | Telephone # : | [5 empty] | Telephone # : | [5 empty] | Telephone # :
|  | RFQ No: R2569 COST COMPARISON REPORT | RFQ No: R2569 COST COMPARISON REPORT | RFQ No: R2569 COST COMPARISON REPORT |  |  |  | Mobile # : 9560263557 | [5 empty] | Mobile # : | [5 empty] | Mobile # :
PR Number : TFS GURGAON-2425-00039 | PR Number : TFS GURGAON-2425-00039 | PR Number : TFS GURGAON-2425-00039 | PR Number : TFS GURGAON-2425-00039 | PR Number : TFS GURGAON-2425-00039 | PR Number : TFS GURGAON-2425-00039 | PR Number : TFS GURGAON-2425-00039 | PR Number : TFS GURGAON-2425-00039 | Email : pushpak.shewale@k-corp.in | [5 empty] | Email : project.arrowelectricals@gmail.com | [5 empty] | Email : alam@electechenterprises.net
Package / RFQ Name : PR for Electrical for DEL GORDON RAMSAY T1. | Package / RFQ Name : PR for Electrical for DEL GORDON RAMSAY T1. | Package / RFQ Name : PR for Electrical for DEL GORDON RAMSAY T1. | Package / RFQ Name : PR for Electrical for DEL GORDON RAMSAY T1. | Package / RFQ Name : PR for Electrical for DEL GORDON RAMSAY T1. | Package / RFQ Name : PR for Electrical for DEL GORDON RAMSAY T1. | Package / RFQ Name : PR for Electrical for DEL GORDON RAMSAY T1. | Package / RFQ Name : PR for Electrical for DEL GORDON RAMSAY T1. | Round # : 4 (Auction) | [5 empty] | Round # : 4 (Auction) | [5 empty] | Round # : 4 (Auction)
Buyer : Pushpak Mahesh Shewale / Technical : / Approver : | Buyer : Pushpak Mahesh Shewale / Technical : / Approver : | Buyer : Pushpak Mahesh Shewale / Technical : / Approver : | Buyer : Pushpak Mahesh Shewale / Technical : / Approver : | Buyer : Pushpak Mahesh Shewale / Technical : / Approver : | Buyer : Pushpak Mahesh Shewale / Technical : / Approver : | Buyer : Pushpak Mahesh Shewale / Technical : / Approver : | Buyer : Pushpak Mahesh Shewale / Technical : / Approver : | Quotation Date : |  |  | Quotation Validity Date : |  |  | Quotation Date : |  |  | Quotation Validity Date : |  |  | Quotation Date : |  |  | Quotation Validity Date :
Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Currency :INR | Currency :INR | Currency :INR | Buyer Remark : . | [5 empty] | Buyer Remark : | [5 empty] | Buyer Remark :
Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | BUDGET PRICE : | .00 |  | Quote Currency : INR | [5 empty] | Quote Currency : INR | [5 empty] | Quote Currency : INR
# | Item Code | Item Description | Unit | Qty | Last PO Details | Lowest Unit Rate | Lowest Vendor | First Bid | Disc % | GST % | Technical | Unit Price | Total | First Bid | Disc % | GST % | Technical | Unit Price | Total | First Bid | Disc % | GST % | Technical | Unit Price | Total
1 | Electrical | Interior Electrical | EA | 1.00 |  | 1130410.00 | CHIRAG ELECTRICAL | 1213800.00 | 0.00 | 18.00 |  | 1,130,410.00 | 1,130,410.00 | 1697600.00 | 0.00 | 18.00 |  | 1,394,130.00 | 1,394,130.00 | 1729311.00 | 0.00 | 18.00 |  | 1,651,789.00 | 1,651,789.00
Item Total | [8 empty] | .00 | 203,473.80 |  |  | 1,130,410.00 |  | .00 | 250,943.40 |  |  | 1,394,130.00 |  | .00 | 597,647.34 |  |  | 1,651,789.00
Discount Total Value | [7 empty] | Grand Dis. Amt | .00 |  |  |  | .00 | Grand Dis. Amt | .00 |  |  |  | .00 | Grand Dis. Amt | .00 |  |  |  | .00
GST Total Amount | [12 empty] | 203,473.80 | [5 empty] | 250,943.40 | [5 empty] | 297,322.02
Net Landed Cost | [11 empty] | INR | 1,333,883.80 |  |  |  |  | INR | 1,645,073.40 |  |  |  |  | INR | 1,949,111.02
Vendor Status | [7 empty] | Round # : 4 (Auction) | Round # : 4 (Auction)
Sr No. | Vendor Code | Vendor Name | [5 empty] | Status | Remarks
1 | RV242524030 | CHIRAG ELECTRICAL | [5 empty] | Participate
2 | RV232422514 | Electech Enterprises | [5 empty] | Participate
3 | RV242522534 | Arrow Electrical | [5 empty] | Participate

## BOQ Price Bid
|  | RFQ No: R2569 COST COMPARISON REPORT | RFQ No: R2569 COST COMPARISON REPORT | Comp. Date : 06/01/2025 | Comp. Date : 06/01/2025 | Comp. Date : 06/01/2025 | Vendor Name : CHIRAG ELECTRICAL | Vendor Name : CHIRAG ELECTRICAL | Vendor Name : Arrow Electrical | Vendor Name : Arrow Electrical | Vendor Name : Electech Enterprises | Vendor Name : Electech Enterprises
|  | RFQ No: R2569 COST COMPARISON REPORT | RFQ No: R2569 COST COMPARISON REPORT | RFQ #: R2569 | RFQ #: R2569 | RFQ #: R2569 | Contact Name : MOHD AKIL | Contact Name : MOHD AKIL | Contact Name : SANTOSH KHAKE | Contact Name : SANTOSH KHAKE | Contact Name : Alam | Contact Name : Alam
|  | RFQ No: R2569 COST COMPARISON REPORT | RFQ No: R2569 COST COMPARISON REPORT | RFQ Date : 06/01/2025 13:21:47 | RFQ Date : 06/01/2025 13:21:47 | RFQ Date : 06/01/2025 13:21:47 | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City :
|  | RFQ No: R2569 COST COMPARISON REPORT | RFQ No: R2569 COST COMPARISON REPORT | BCD Date : 06/01/2025 15:01:00 | BCD Date : 06/01/2025 15:01:00 | BCD Date : 06/01/2025 15:01:00 | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # :
|  | RFQ No: R2569 COST COMPARISON REPORT | RFQ No: R2569 COST COMPARISON REPORT |  |  |  | Mobile # : 9560263557 | Mobile # : 9560263557 | Mobile # : | Mobile # : | Mobile # : | Mobile # :
PR Number : TFS GURGAON-2425-00039 | PR Number : TFS GURGAON-2425-00039 | PR Number : TFS GURGAON-2425-00039 | PR Number : TFS GURGAON-2425-00039 | PR Number : TFS GURGAON-2425-00039 | PR Number : TFS GURGAON-2425-00039 | PR Number : TFS GURGAON-2425-00039 | Email : pushpak.shewale@k-corp.in | Email : pushpak.shewale@k-corp.in | Email : project.arrowelectricals@gmail.com | Email : project.arrowelectricals@gmail.com | Email : alam@electechenterprises.net | Email : alam@electechenterprises.net
Package / RFQ Name : PR for Electrical for DEL GORDON RAMSAY T1. | Package / RFQ Name : PR for Electrical for DEL GORDON RAMSAY T1. | Package / RFQ Name : PR for Electrical for DEL GORDON RAMSAY T1. | Package / RFQ Name : PR for Electrical for DEL GORDON RAMSAY T1. | Package / RFQ Name : PR for Electrical for DEL GORDON RAMSAY T1. | Package / RFQ Name : PR for Electrical for DEL GORDON RAMSAY T1. | Package / RFQ Name : PR for Electrical for DEL GORDON RAMSAY T1. | Round # : 4 (Auction) | Round # : 4 (Auction) | Round # : 4 (Auction) | Round # : 4 (Auction) | Round # : 4 (Auction) | Round # : 4 (Auction)
Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score :
Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Currency :INR | Currency :INR | Currency :INR | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date :
Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | BUDGET PRICE :.00 | BUDGET PRICE :.00 | BUDGET PRICE :.00 | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date :
Sr No. | Item Code | Item Name | Item Description | UOM | Qty | Minimum Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount
1 | Electrical | Interior Electrical | Interior Electrical | EA | 1.000 |  |  | 1,130,410.00 |  | 1,394,130.00 |  | 1,668,474.00
1 | A | CONNECTING INTEGRATING UNIT M E SERVICES TO AIRPORT M E SERVICES BUILDING | CONNECTING INTEGRATING UNIT M E SERVICES TO AIRPORT M E SERVICES BUILDING
2 | A.1 | If any termination connection of the unit services are required outside the site location (i.e. connection of the unit M E to the airport M E or service termination to the airport external façade roof etc.); then the contractor has to work in consultation with the airport to plan, design detail for such connections. The contractor to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor to make good after installation any penetrations including providing fire seals as requried as per airport requirement. | If any termination connection of the unit services are required outside the site location (i.e. connection of the unit M E to the airport M E or service termination to the airport external façade roof etc.); then the contractor has to work in consultation with the airport to plan, design detail for such connections. The contractor to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor to make good after installation any penetrations including providing fire seals as requried as per airport requirement.
3 | C.1 | Supply and Laying of approved make Fire Rated LSZH XLPE insulated PVC sheathed, Copper conductor, Steel Tape Wire Armoured, 1100V grade cable, Number of Cable Core as per SLD Load Calculation Sheet (Main Cable) Unarmoured Single Core Wire (ECC). The cable shall be laid Underground on Cable Tray through Cable Trunking in Pipe on Wall Trench using necessary supporting clamping arrangements.The cable shall be provided with cable identification tags made out of Aluminium strip, engraved with cable size and the routing. Make - Polycab, KEI, RR, Havells, Gemco | Supply and Laying of approved make Fire Rated LSZH XLPE insulated PVC sheathed, Copper conductor, Steel Tape Wire Armoured, 1100V grade cable, Number of Cable Core as per SLD Load Calculation Sheet (Main Cable) Unarmoured Single Core Wire (ECC). The cable shall be laid Underground on Cable Tray through Cable Trunking in Pipe on Wall Trench using necessary supporting clamping arrangements.The cable shall be provided with cable identification tags made out of Aluminium strip, engraved with cable size and the routing. Make - Polycab, KEI, RR, Havells, Gemco
4 | C.1.1 | 3.5C x120 SQ.MM XLPE AL. CABLE | 3.5C x120 SQ.MM XLPE AL. CABLE | Mtr | 20.000 | 15,800.00 | 950.00 | 19,000.00 | 790.00 | 15,800.00 | 1100.00 | 22,000.00
5 | C.1.2 | 4C X 25 SQ.MM XLPE AL. CABLE | 4C X 25 SQ.MM XLPE AL. CABLE | Mtr | 12.000 | 4,680.00 | 450.00 | 5,400.00 | 390.00 | 4,680.00 | 425.00 | 5,100.00
6 | C.1.3 | 4C X 6 SQ.MM XLPE CU. CABLE | 4C X 6 SQ.MM XLPE CU. CABLE | Mtr | 200.000 | 90,000.00 | 450.00 | 90,000.00 | 488.00 | 97,600.00 | 850.00 | 170,000.00
7 | D | CABLE END TERMINATIONS | CABLE END TERMINATIONS
8 | D.1 | Supply and Installation of approved make cable end Termination for the following cables using Single Compression Brass Glands, Solderless Tinned Copper Lugs, Gland earthing of adequate size, etc.complete. | Supply and Installation of approved make cable end Termination for the following cables using Single Compression Brass Glands, Solderless Tinned Copper Lugs, Gland earthing of adequate size, etc.complete.
9 | D.1.1 | 3.5C x120 SQ.MM XLPE AL. CABLE | 3.5C x120 SQ.MM XLPE AL. CABLE | Nos | 4.000 | 3,800.00 | 1000.00 | 4,000.00 | 950.00 | 3,800.00 | 1100.00 | 4,400.00
10 | D.1.2 | 4C X 25 SQ.MM XLPE AL. CABLE | 4C X 25 SQ.MM XLPE AL. CABLE | Nos | 2.000 | 850.00 | 800.00 | 1,600.00 | 450.00 | 900.00 | 425.00 | 850.00
11 | D.1.3 | 4C X 6 SQ.MM XLPE CU. CABLE | 4C X 6 SQ.MM XLPE CU. CABLE | Nos | 16.000 | 8,800.00 | 550.00 | 8,800.00 | 550.00 | 8,800.00 | 850.00 | 13,600.00
12 | E | DISTRIBUTION BOARDS | DISTRIBUTION BOARDS
13 | E.1 | Supply, Installation, Testing Commissioning of approved make Surface Flush Floor mounting 10kA 25kA Distribution Boards, Devices, Relays and all accessories. The RYB sequence should be provided at the incomer entry, followed by on off and trip indicators. The DB shall be made out of 1.2 mm CRCA sheet steel enclosure and powder coated complete with cable gland plate knock out at the top and bottom. The DB shall have hinged lockable door. The busbar shall be tinned copper, for phases mounted on suitable type Insulator, Independent neutral busbar including inter connecting wiring earth bus on insulation mount, complete with Protective devices (MCCB, MCB, RCCB, RCBO, etc.) The Contractor shall be responsible to supply materials and equipment complying with the green building specification if required. All DB s must named as per the SLD Load Calculation Sheet. Laminated SLD Load Calculation Sheet shall be placed near to DB Locations. The RCCB RCBO shall be Hpi Si series MCB s shall be B C Curve (As per Airport requirement). LT Siwitchgear (MCCB, MCB, RCBO, RCCB) -Legrand, ABB, Schneider, Siemens MFM meter shall be of Digital kVAH Type of approved make or any other make with kVAH option with Approval from TS Department. 160 5A CT with Energy Meter as per the scheme. | Supply, Installation, Testing Commissioning of approved make Surface Flush Floor mounting 10kA 25kA Distribution Boards, Devices, Relays and all accessories. The RYB sequence should be provided at the incomer entry, followed by on off and trip indicators. The DB shall be made out of 1.2 mm CRCA sheet steel enclosure and powder coated complete with cable gland plate knock out at the top and bottom. The DB shall have hinged lockable door. The busbar shall be tinned copper, for phases mounted on suitable type Insulator, Independent neutral busbar including inter connecting wiring earth bus on insulation mount, complete with Protective devices (MCCB, MCB, RCCB, RCBO, etc.) The Contractor shall be responsible to supply materials and equipment complying with the green building specification if required. All DB s must named as per the SLD Load Calculation Sheet. Laminated SLD Load Calculation Sheet shall be placed near to DB Locations. The RCCB RCBO shall be Hpi Si series MCB s shall be B C Curve (As per Airport requirement). LT Siwitchgear (MCCB, MCB, RCBO, RCCB) -Legrand, ABB, Schneider, Siemens MFM meter shall be of Digital kVAH Type of approved make or any other make with kVAH option with Approval from TS Department. 160 5A CT with Energy Meter as per the scheme.
14 | E.1.1 | SMDBIncomer 160A 4P MCCB - 1 No.Outgoings63A 4P MCB - 1No.32A 4P RCBO - 10 Nos.20A 2P RCBO - 3 Nos. | SMDBIncomer 160A 4P MCCB - 1 No.Outgoings63A 4P MCB - 1No.32A 4P RCBO - 10 Nos.20A 2P RCBO - 3 Nos. | Each | 1.000 | 70,000.00 | 70000.00 | 70,000.00 | 243200.00 | 243,200.00 | 315000.00 | 315,000.00
15 | E.1.2 | LPDB16 Way PPI TPN DBIncomer 63A 4P MCB-1 No.40A 30mA 2P RCBO - 3 Nos.Outgoings10 16 20 25 32A SP MCB- 48 Nos.16 Way PPI TPN DBIncomer 63A 4P MCB-1 No.40A 30mA 2P RCBO - 3 Nos.Outgoings10 16 20 25 32A SP MCB- 48 Nos. | LPDB16 Way PPI TPN DBIncomer 63A 4P MCB-1 No.40A 30mA 2P RCBO - 3 Nos.Outgoings10 16 20 25 32A SP MCB- 48 Nos.16 Way PPI TPN DBIncomer 63A 4P MCB-1 No.40A 30mA 2P RCBO - 3 Nos.Outgoings10 16 20 25 32A SP MCB- 48 Nos. | Each | 1.000 | 36,000.00 | 37000.00 | 37,000.00 | 36000.00 | 36,000.00 | 50000.00 | 50,000.00
16 | E.1.3 | LDB16 Way SPN DBIncomer 32A 30mA DP RCCB-1 No.Outgoings10 16 20 25A SP MCB- 12 Nos. | LDB16 Way SPN DBIncomer 32A 30mA DP RCCB-1 No.Outgoings10 16 20 25A SP MCB- 12 Nos. | Each | 1.000 | 13,000.00 | 13500.00 | 13,500.00 | 13000.00 | 13,000.00 | 14500.00 | 14,500.00
17 | E.1.4 | UPS DB | UPS DB | Each | 1.000 | 9,500.00 | 9500.00 | 9,500.00 | 11500.00 | 11,500.00 | 11000.00 | 11,000.00
18 | F | EARTHING | EARTHING
19 | F.1 | Supply laying testing and commissioning of strip and round conductor (Copper Aluminium GI) as per IS3043 on surface or recess of through conduit of suitable size as required. All body part should be double earthed. | Supply laying testing and commissioning of strip and round conductor (Copper Aluminium GI) as per IS3043 on surface or recess of through conduit of suitable size as required. All body part should be double earthed.
20 | F.1.1 | 25x6 GI Strip | 25x6 GI Strip | Nos | 50.000 | 6,500.00 | 180.00 | 9,000.00 | 210.00 | 10,500.00 | 130.00 | 6,500.00
21 | F.1.2 | 10 SWG Copper conductor | 10 SWG Copper conductor | Nos | 24.000 | 1,488.00 | 80.00 | 1,920.00 | 95.00 | 2,280.00 | 62.00 | 1,488.00
22 | F.1.3 | 12 SWG Copper conductor | 12 SWG Copper conductor | Nos | 80.000 | 4,640.00 | 80.00 | 6,400.00 | 75.00 | 6,000.00 | 58.00 | 4,640.00
23 | F.1.4 | 16 SWG Copper conductor | 16 SWG Copper conductor | Nos | 10.000 | 540.00 | 80.00 | 800.00 | 65.00 | 650.00 | 54.00 | 540.00
24 | G | LIGHT POINT WIRING | LIGHT POINT WIRING
25 | G.1 | Supply, Installation, Testing Commissioning of Point wiring (Light Fixtures to be as approved by Architect Design BOQ) with approved makes Switches Lighting Control Switch Board with FRLSH PVC insulated Flexible Copper Wires 660 1100V grade using 2 X 1.5 Sq mm PVC insulated fine stranded single core FRLSH copper conductor wires phase and neutral and with 1.5 Sq mm PVC insulated, green coloured, fine stranded single core copper cable as earth continuity, earth wire crimped to copper socket, fastened using brass bolt and nut etc through suitable size GI Conduit Heavy Duty PVC Conduit GI Trunking (Containment size Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. carrying out Surface Concealed wiring as per site condition maintain aesthetic of the unit.Wiring shall be as per IS 732. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports brackets for conduit and Trunking suspension. Wire Make - Polycab, KEI, RR, Havells, Gemco Modular Switches, Sockets - Legrand, ABB, Schneider, Siemens GI PVC Conduit Make -AKG, BEC (ISI marked) | Supply, Installation, Testing Commissioning of Point wiring (Light Fixtures to be as approved by Architect Design BOQ) with approved makes Switches Lighting Control Switch Board with FRLSH PVC insulated Flexible Copper Wires 660 1100V grade using 2 X 1.5 Sq mm PVC insulated fine stranded single core FRLSH copper conductor wires phase and neutral and with 1.5 Sq mm PVC insulated, green coloured, fine stranded single core copper cable as earth continuity, earth wire crimped to copper socket, fastened using brass bolt and nut etc through suitable size GI Conduit Heavy Duty PVC Conduit GI Trunking (Containment size Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. carrying out Surface Concealed wiring as per site condition maintain aesthetic of the unit.Wiring shall be as per IS 732. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports brackets for conduit and Trunking suspension. Wire Make - Polycab, KEI, RR, Havells, Gemco Modular Switches, Sockets - Legrand, ABB, Schneider, Siemens GI PVC Conduit Make -AKG, BEC (ISI marked)
26 | G.1.1 | 1 No. light point controlled by 1 No 10A, SP Switch. | 1 No. light point controlled by 1 No 10A, SP Switch. | Nos | 21.000 | 46,200.00 | 2200.00 | 46,200.00 | 2850.00 | 59,850.00 | 2550.00 | 53,550.00
27 | G.1.2 | Secondary light points. (from the first light point without supply and installation of switches.) | Secondary light points. (from the first light point without supply and installation of switches.) | Nos | 109.000 | 114,450.00 | 1350.00 | 147,150.00 | 1200.00 | 130,800.00 | 1050.00 | 114,450.00
28 | H | CIRCUIT WIRING | CIRCUIT WIRING
29 | H.1 | Supply, Installation, Testing Commissioning of approved makes FRLSH PVC insulated Flexible Copper Cable Wires 660 1100V grade through suitable size GI Conduit Heavy Duty PVC Conduit GI Trunking (Containment size Type selection as per site requirement) for the following types of wires. For dummy sockets wiring considered. Wire Make - Polycab, KEI, RR, Havells, Gemco GI PVC Conduit Make -AKG, BEC (ISI marked) | Supply, Installation, Testing Commissioning of approved makes FRLSH PVC insulated Flexible Copper Cable Wires 660 1100V grade through suitable size GI Conduit Heavy Duty PVC Conduit GI Trunking (Containment size Type selection as per site requirement) for the following types of wires. For dummy sockets wiring considered. Wire Make - Polycab, KEI, RR, Havells, Gemco GI PVC Conduit Make -AKG, BEC (ISI marked)
30 | H.1.1 | Circuit wiring for light points using 2 Runs of 2.5 sq.mm PVC insulated copper wires along with 1 Run of 1.5 sqmm pvc copper wire (Green) for continuous earthing, through suitable GI Conduit Heavy Duty PVC Conduit GI Trunking from DB to Light control switch box Normal Sockets. | Circuit wiring for light points using 2 Runs of 2.5 sq.mm PVC insulated copper wires along with 1 Run of 1.5 sqmm pvc copper wire (Green) for continuous earthing, through suitable GI Conduit Heavy Duty PVC Conduit GI Trunking from DB to Light control switch box Normal Sockets. | Mtr | 900.000 | 216,000.00 | 250.00 | 225,000.00 | 240.00 | 216,000.00 | 350.00 | 315,000.00
31 | H.1.2 | Power points using 2 Runs of 4 sq.mm PVC insulated copper wires along with 1 Run of 2.5 sqmm pvc copper wire (Green) for continuous earthing, through suitable GI Conduit Heavy Duty PVC Conduit GI Trunking from DB to Power points. | Power points using 2 Runs of 4 sq.mm PVC insulated copper wires along with 1 Run of 2.5 sqmm pvc copper wire (Green) for continuous earthing, through suitable GI Conduit Heavy Duty PVC Conduit GI Trunking from DB to Power points. | Mtr | 300.000 | 93,000.00 | 310.00 | 93,000.00 | 332.00 | 99,600.00 | 465.00 | 139,500.00
32 | H.1.3 | Power points using 2 Runs of 4 sq.mm PVC insulated copper wires along with 1 Run of 4 sqmm pvc copper wire (Green) for continuous earthing, through suitable GI Conduit Heavy Duty PVC Conduit GI Trunking from Main DB to UPS DB | Power points using 2 Runs of 4 sq.mm PVC insulated copper wires along with 1 Run of 4 sqmm pvc copper wire (Green) for continuous earthing, through suitable GI Conduit Heavy Duty PVC Conduit GI Trunking from Main DB to UPS DB | Mtr | 30.000 | 9,300.00 | 310.00 | 9,300.00 | 352.00 | 10,560.00 | 620.00 | 18,600.00
33 | H.1.4 | Power points using 2 Runs of 6 sq.mm PVC insulated copper wires along with 1 Run of 4 sqmm pvc copper wire (Green) for continuous earthing, through suitable GI Conduit Heavy Duty PVC Conduit GI Trunking from Main DB to LDB | Power points using 2 Runs of 6 sq.mm PVC insulated copper wires along with 1 Run of 4 sqmm pvc copper wire (Green) for continuous earthing, through suitable GI Conduit Heavy Duty PVC Conduit GI Trunking from Main DB to LDB | Mtr | 10.000 | 3,800.00 | 380.00 | 3,800.00 | 380.00 | 3,800.00 | 660.00 | 6,600.00
34 | J | POWER POINTS (SWITCHES SOCKETS) | POWER POINTS (SWITCHES SOCKETS)
35 | J.1 | Supply, Installation, Testing Commissioning of approved makes Devices (Switches Sockets - Face Plate Finish as approved by Architect Matching to Architecture interior Finishes) complete with suitable GI Back boxes, Earthing, accessories, glands, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. on Surface Concealed as per site condition maintain aesthetic of the unit.Type annd IP rating should be as per Airport requirements. The rate shall include wall chasing, chipping of floors, rough plastering. The unit shall be suitable for 400 ± 15 volts 3 phase and 230 ± 10 volts 1 phase, 50 60 Hz, AC supply as per Airport Country power supply. Modular Switches, Sockets - Legrand, ABB, Schneider, Siemens | Supply, Installation, Testing Commissioning of approved makes Devices (Switches Sockets - Face Plate Finish as approved by Architect Matching to Architecture interior Finishes) complete with suitable GI Back boxes, Earthing, accessories, glands, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. on Surface Concealed as per site condition maintain aesthetic of the unit.Type annd IP rating should be as per Airport requirements. The rate shall include wall chasing, chipping of floors, rough plastering. The unit shall be suitable for 400 ± 15 volts 3 phase and 230 ± 10 volts 1 phase, 50 60 Hz, AC supply as per Airport Country power supply. Modular Switches, Sockets - Legrand, ABB, Schneider, Siemens
36 | J.1.1 | 13A Single Switched Socket Outlet | 13A Single Switched Socket Outlet | Nos | 10.000 | 7,900.00 | 1200.00 | 12,000.00 | 790.00 | 7,900.00 | 790.00 | 7,900.00
37 | J.1.2 | 13A Dual Switched Socket Outlet | 13A Dual Switched Socket Outlet | Nos | 4.000 | 5,280.00 | 2000.00 | 8,000.00 | 1320.00 | 5,280.00 | 1500.00 | 6,000.00
38 | J.1.3 | 13A Single Unswitched Socket Outlet | 13A Single Unswitched Socket Outlet | Nos | 2.000 | 1,200.00 | 600.00 | 1,200.00 | 600.00 | 1,200.00 | 700.00 | 1,400.00
39 | J.1.4 | 13A Dual Switched Socket Outlet + Dual USB Port | 13A Dual Switched Socket Outlet + Dual USB Port | Nos | 10.000 | 25,000.00 | 3500.00 | 35,000.00 | 3150.00 | 31,500.00 | 2500.00 | 25,000.00
40 | J.1.5 | 16A Single Switched Socket Outlet | 16A Single Switched Socket Outlet | Nos | 33.000 | 26,730.00 | 810.00 | 26,730.00 | 810.00 | 26,730.00 | 875.00 | 28,875.00
41 | J.1.6 | 16A Single Unswitched Socket Outlet | 16A Single Unswitched Socket Outlet | Nos | 1.000 | 600.00 | 600.00 | 600.00 | 600.00 | 600.00 | 600.00 | 600.00
42 | J.1.7 | 13A One Gang One Way Switch | 13A One Gang One Way Switch | Nos | 2.000 | 510.00 | 255.00 | 510.00 | 255.00 | 510.00 | 700.00 | 1,400.00
43 | J.1.8 | Double Pole Switch With Neon Indicator | Double Pole Switch With Neon Indicator | Nos | 1.000 | 600.00 | 600.00 | 600.00 | 600.00 | 600.00 | 900.00 | 900.00
44 | J.1.9 | 16A Single Phase Industrial Switched Socket (3 pin) ((wall mounted metal clad socket) | 16A Single Phase Industrial Switched Socket (3 pin) ((wall mounted metal clad socket) | Nos | 3.000 | 8,400.00 | 3000.00 | 9,000.00 | 2800.00 | 8,400.00 | 3000.00 | 9,000.00
45 | J.1.10 | 20A Single Phase Industrial Switched Socket (3 pin) ((wall mounted metal clad socket) | 20A Single Phase Industrial Switched Socket (3 pin) ((wall mounted metal clad socket) | Nos | 7.000 | 21,000.00 | 3200.00 | 22,400.00 | 3000.00 | 21,000.00 | 3200.00 | 22,400.00
46 | J.1.11 | 32A Three Phase Industrial Switched Socket (5 pin) ((wall mounted metal clad socket) | 32A Three Phase Industrial Switched Socket (5 pin) ((wall mounted metal clad socket) | Nos | 6.000 | 32,400.00 | 5400.00 | 32,400.00 | 8500.00 | 51,000.00 | 11176.00 | 67,056.00
47 | J.1.12 | 20A Three Phase Isolator with Enclosure | 20A Three Phase Isolator with Enclosure | Nos | 2.000 | 3,150.00 | 1575.00 | 3,150.00 | 4700.00 | 9,400.00 | 1575.00 | 3,150.00
48 | K | CONTAINMENT | CONTAINMENT
49 | K.1 | Supply Installation of approved makes GI Conduit Heavy Duty PVC Conduit, through Wall Ceiling Floor as per drawings, complete with ISI standard accessories factory made fittings. GI PVC Conduit Make -AKG, BEC (ISI marked) Cable tray- MEM, Profab (ISI marked) | Supply Installation of approved makes GI Conduit Heavy Duty PVC Conduit, through Wall Ceiling Floor as per drawings, complete with ISI standard accessories factory made fittings. GI PVC Conduit Make -AKG, BEC (ISI marked) Cable tray- MEM, Profab (ISI marked)
50 | K.1.1 | 250x 50 mm Cable Tray | 250x 50 mm Cable Tray | Mtr | 20.000 | 11,000.00 | 550.00 | 11,000.00 | 1030.00 | 20,600.00 | 1200.00 | 24,000.00
51 | K.1.2 | 200x 50 mm Cable Tray | 200x 50 mm Cable Tray | Mtr | 5.000 | 2,500.00 | 500.00 | 2,500.00 | 910.00 | 4,550.00 | 900.00 | 4,500.00
52 | K.1.3 | 100x 50 mm Cable Tray | 100x 50 mm Cable Tray | Mtr | 55.000 | 19,250.00 | 350.00 | 19,250.00 | 950.00 | 52,250.00 | 525.00 | 28,875.00
53 | L | UPS SYSTEM | UPS SYSTEM
54 | L.1 | Supply, Installation, Testing Commissioning of approved makes UPS along with required Battery for specified back-up time, complete with Battery Stand (If required) standard accessories equipments required for complete functioning of the system, earthing, support system (if required), etc. The Contractor shall be responsible to supply materials and equipment complying with the green building specification if required. | Supply, Installation, Testing Commissioning of approved makes UPS along with required Battery for specified back-up time, complete with Battery Stand (If required) standard accessories equipments required for complete functioning of the system, earthing, support system (if required), etc. The Contractor shall be responsible to supply materials and equipment complying with the green building specification if required.
55 | L.1.1 | 2 KVA Single phase UPS with 30 Minute Back-up | 2 KVA Single phase UPS with 30 Minute Back-up | Nos. | 1.000 | 55,000.00 | 55000.00 | 55,000.00 | 65000.00 | 65,000.00 | 57000.00 | 57,000.00
56 | M | CCTV SYSTEM | CCTV SYSTEM
57 | M.1 | Supply, Installation, Testing Commissioning of approved makes CCTV System with suitable required cabling through suitable size GI Conduit GI Trunking (Containment size Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with CCTV console DVR with Power Box , Suitable POE with Port switch Surveillance hard disk,etc. carrying out Surface Concealed wiring as per site condition maintain aesthetic of the unit. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports brackets for conduit and Trunking suspension. | Supply, Installation, Testing Commissioning of approved makes CCTV System with suitable required cabling through suitable size GI Conduit GI Trunking (Containment size Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with CCTV console DVR with Power Box , Suitable POE with Port switch Surveillance hard disk,etc. carrying out Surface Concealed wiring as per site condition maintain aesthetic of the unit. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports brackets for conduit and Trunking suspension.
58 | M.1.1 | CCTV Ceiling Mount Dome Camera, As approved or confirmed by client with all neccessary accessories, etc. | CCTV Ceiling Mount Dome Camera, As approved or confirmed by client with all neccessary accessories, etc. | Nos | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
59 | M.1.2 | Suitable size IDF RACK with Necessary Patch Panel Network switch as required. | Suitable size IDF RACK with Necessary Patch Panel Network switch as required. | Nos | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
60 | M.1.3 | 16-Channel DVR | 16-Channel DVR | Nos | 0.000 | .00 | 0.00 | .00 | 0.00 | .00 | 0.00 | .00
61 | M.1.4 | 3+ 1 cable on surface concealed wall, including suitable conduits, fittings, accessories, etc. | 3+ 1 cable on surface concealed wall, including suitable conduits, fittings, accessories, etc. | Mtr. | 150.000 | 12,000.00 | 80.00 | 12,000.00 | 180.00 | 27,000.00 | 255.00 | 38,250.00
62 | N | DATA NETWORK SYSTEM | DATA NETWORK SYSTEM
63 | N.1 | Supply, Installation, Testing Commissioning of approved makes Data Telephone Network System with required cabling through suitable size GI Conduit Heavy Duty PVC Conduit GI Trunking (Containment size Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with IDF SERVER Rack using patch cordes, etc. carrying out Surface Concealed wiring as per site condition maintain aesthetic of the unit. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports brackets for conduit and Trunking suspension. | Supply, Installation, Testing Commissioning of approved makes Data Telephone Network System with required cabling through suitable size GI Conduit Heavy Duty PVC Conduit GI Trunking (Containment size Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with IDF SERVER Rack using patch cordes, etc. carrying out Surface Concealed wiring as per site condition maintain aesthetic of the unit. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports brackets for conduit and Trunking suspension.
64 | N.1.1 | Single Data outlet (RJ45) Jack | Single Data outlet (RJ45) Jack | Nos | 4.000 | 2,160.00 | 600.00 | 2,400.00 | 580.00 | 2,320.00 | 540.00 | 2,160.00
65 | N.1.2 | Dual Data outlet (RJ45) Jack | Dual Data outlet (RJ45) Jack | Nos | 2.000 | 1,290.00 | 1200.00 | 2,400.00 | 1210.00 | 2,420.00 | 645.00 | 1,290.00
66 | N.1.3 | WIFI Router | WIFI Router | Nos | 1.000 | .00 | 4500.00 | 4,500.00 | 0.00 | .00 | 0.00 | .00
67 | N.1.4 | SITC of CAT6 cable on surface concealed wall, including suitable conduits, fittings, accessories, etc.(For dummy points cabling considered) | SITC of CAT6 cable on surface concealed wall, including suitable conduits, fittings, accessories, etc.(For dummy points cabling considered) | Mtr. | 220.000 | 17,600.00 | 80.00 | 17,600.00 | 210.00 | 46,200.00 | 220.00 | 48,400.00
68 | O | PA SYSTEM | PA SYSTEM
69 | O.1 | Supply, Installation, Testing Commissioning of approved makes PA System with required cabling through suitable size GI Conduit GI Trunking (Containment size Type selection as per site requirement), complete with suitable GI back boxes, Earthing, EOLR, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with IDF Rack, etc. carrying out Surface Concealed wiring as per site condition maintain aesthetic of the unit. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports brackets for conduit and Trunking suspension. | Supply, Installation, Testing Commissioning of approved makes PA System with required cabling through suitable size GI Conduit GI Trunking (Containment size Type selection as per site requirement), complete with suitable GI back boxes, Earthing, EOLR, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with IDF Rack, etc. carrying out Surface Concealed wiring as per site condition maintain aesthetic of the unit. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports brackets for conduit and Trunking suspension.
70 | O.1.1 | 6 Watts ceiling mount Speaker with all the necessary accessories | 6 Watts ceiling mount Speaker with all the necessary accessories | Nos | 5.000 | .00 | 2500.00 | 12,500.00 | 2850.00 | 14,250.00 | 0.00 | .00
71 | O.1.2 | Volume Controller | Volume Controller | Nos | 1.000 | .00 | 1200.00 | 1,200.00 | 4500.00 | 4,500.00 | 0.00 | .00
72 | O.1.3 | PA Controller with Amplifier | PA Controller with Amplifier | Nos | 1.000 | .00 | 25000.00 | 25,000.00 | 0.00 | .00 | 0.00 | .00
73 | O.1.4 | SITC of 2C 1.5 Sq mm Cu multi-stranded PVC insulated shielded FRLS cable | SITC of 2C 1.5 Sq mm Cu multi-stranded PVC insulated shielded FRLS cable | Mtr. | 50.000 | 6,000.00 | 120.00 | 6,000.00 | 120.00 | 6,000.00 | 265.00 | 13,250.00
74 | P | ELECTRICAL SERVICE IDENTIFICATION LABELS, SIGNS TAGS | ELECTRICAL SERVICE IDENTIFICATION LABELS, SIGNS TAGS
75 | P.1 | All services like Panels, Cables, Pipes etc need to be clearly labelled or tagged at site with service identification, direction etc. And all equipment needs to tagged as per Airport requirements. | All services like Panels, Cables, Pipes etc need to be clearly labelled or tagged at site with service identification, direction etc. And all equipment needs to tagged as per Airport requirements.
76 | P.1.1 | Labelling Tagging for Services and Equipment s | Labelling Tagging for Services and Equipment s | Lot | 1.000 | 5,000.00 | 5000.00 | 5,000.00 | 5000.00 | 5,000.00 | 5000.00 | 5,000.00
77 | Q | MISCELLANEOUS | MISCELLANEOUS
78 | Q.1 | The contractor needs to mention any additional items or missing items that are not mentioned in the above BOQ after a detailed site survey or inspection and to be validated by consultants. | The contractor needs to mention any additional items or missing items that are not mentioned in the above BOQ after a detailed site survey or inspection and to be validated by consultants.
79 | Q.1.1 | Providing and Fixing of Electrical Standard Grade Rubber Mat suitable for LT Volts | Providing and Fixing of Electrical Standard Grade Rubber Mat suitable for LT Volts | Unit | 1.000 | 700.00 | 700.00 | 700.00 | 3000.00 | 3,000.00 | 3150.00 | 3,150.00
80 | Q.1.2 | Provide and Fixing Shock Treatment Chart | Provide and Fixing Shock Treatment Chart | Unit | 1.000 | 200.00 | 200.00 | 200.00 | 1250.00 | 1,250.00 | 1200.00 | 1,200.00
81 | Q.1.3 | Provide and Fixing of L.T. danger sign boards in Panel side | Provide and Fixing of L.T. danger sign boards in Panel side | Unit | 1.000 | 200.00 | 200.00 | 200.00 | 350.00 | 350.00 | 400.00 | 400.00
82 | R | SHOP DRAWINGS APPROVALS | SHOP DRAWINGS APPROVALS
83 | R.1 | Preparation and submission of a detailed shop drawing for the electrical system after a thorough study of design drawings, site surveys, and relevant airport standards with correct routing, size, and elevations. The drawings also need to be coordinated with other MEP services like HVAC, plumbing, and fire services, along with updating SLD, load calculation sheets, and power layouts as per approved, selected, or supplied equipment power and phase requirements, this also needs to be coordinated with latest architectural, structural and interior design drawings, before construction. Necessary amendments to the drawings are to be made and resubmitted in case of any variations on site while at the construction stage of the project. Also prepare relevant detailed connection drawings as per selected manufacturer details and airport standards, with necessary approval to be obtained from consultants and authority regulatory bodies having jurisdiction, along with material submission approval with airport authorities. | Preparation and submission of a detailed shop drawing for the electrical system after a thorough study of design drawings, site surveys, and relevant airport standards with correct routing, size, and elevations. The drawings also need to be coordinated with other MEP services like HVAC, plumbing, and fire services, along with updating SLD, load calculation sheets, and power layouts as per approved, selected, or supplied equipment power and phase requirements, this also needs to be coordinated with latest architectural, structural and interior design drawings, before construction. Necessary amendments to the drawings are to be made and resubmitted in case of any variations on site while at the construction stage of the project. Also prepare relevant detailed connection drawings as per selected manufacturer details and airport standards, with necessary approval to be obtained from consultants and authority regulatory bodies having jurisdiction, along with material submission approval with airport authorities.
84 |  | General guideline for onsite electrical works 1. DB have per phase RCBO protection.2. Minimum wire size shall be 2.5 Sq. mm and power circuits wire size should be 4.0 sq.mm.3. All equipment’s above 1 KW shall be provided with ELCB shall run operated through industrial type switch socket only.4. Only GI conduit will be used.5. Equipment protection devices and appropriate earthing as per approved load to be provided.6. All DB and panel have dual earthing connection.7. All internal wires cables shall be FRLSH FRLSZH.8. Main distribution board will not be fixed on wooden material.9. IT , Data and low voltage wires shall be drawn In Separate10. Switch Sockets outlets will not be over loaded with multiple connection conduit and not with electrical11. All lights shall be LED.12. Provision of Emergency light should be there.13. No combustive material are to be store under closed the electrical switch board distribution board meter etc.14. The concessioner should install suitable type rated fire extinguisher near electrical panel.15. Shutter type switch socket outlet on suitable MS box shall be used with proper earthing.16. All electrical equipment shall be proper earthed and connected to main earthing with suitably sized earthing conductor.17. Final approved Single line diagram sealed in a plastic folder shall be provided inside each electrical panel.13. No combustive material are to be store under closed the electrical switch board distribution board meter etc.18. Load balancing to be done.19. Power connection for Existing BTU meter Water meter to be provided from concessionaire DB.20. All electrical source to be enclosure with IP65 Device with louvered openable cabinet and all fire protection.21. Panel GA drawing to be share with DIAL for approval.22. Before installation, material inspection to be done.23. Test certificate for installed electrical material to be submitted to DIAL . 24. If any changes due to site constraint, prior intimation to be provided to DIAL. Post approval only SLD to revised.25.all SP MCB as ‘C’ characteristic.In case, Incomer rating equal to or more than 200Amps Automatic Tube Detection and Suppression System to be doneCO2,FM200 HFC-227ea gas based automatic tube detection suppression system needs to be installed for Electrical Panel with Incomer rating equal to or more than 200Amps.Drawing needs to be submitted for prior approval.System sizing design calculations also need to be incorporated in drawing. | General guideline for onsite electrical works 1. DB have per phase RCBO protection.2. Minimum wire size shall be 2.5 Sq. mm and power circuits wire size should be 4.0 sq.mm.3. All equipment’s above 1 KW shall be provided with ELCB shall run operated through industrial type switch socket only.4. Only GI conduit will be used.5. Equipment protection devices and appropriate earthing as per approved load to be provided.6. All DB and panel have dual earthing connection.7. All internal wires cables shall be FRLSH FRLSZH.8. Main distribution board will not be fixed on wooden material.9. IT , Data and low voltage wires shall be drawn In Separate10. Switch Sockets outlets will not be over loaded with multiple connection conduit and not with electrical11. All lights shall be LED.12. Provision of Emergency light should be there.13. No combustive material are to be store under closed the electrical switch board distribution board meter etc.14. The concessioner should install suitable type rated fire extinguisher near electrical panel.15. Shutter type switch socket outlet on suitable MS box shall be used with proper earthing.16. All electrical equipment shall be proper earthed and connected to main earthing with suitably sized earthing conductor.17. Final approved Single line diagram sealed in a plastic folder shall be provided inside each electrical panel.13. No combustive material are to be store under closed the electrical switch board distribution board meter etc.18. Load balancing to be done.19. Power connection for Existing BTU meter Water meter to be provided from concessionaire DB.20. All electrical source to be enclosure with IP65 Device with louvered openable cabinet and all fire protection.21. Panel GA drawing to be share with DIAL for approval.22. Before installation, material inspection to be done.23. Test certificate for installed electrical material to be submitted to DIAL . 24. If any changes due to site constraint, prior intimation to be provided to DIAL. Post approval only SLD to revised.25.all SP MCB as ‘C’ characteristic.In case, Incomer rating equal to or more than 200Amps Automatic Tube Detection and Suppression System to be doneCO2,FM200 HFC-227ea gas based automatic tube detection suppression system needs to be installed for Electrical Panel with Incomer rating equal to or more than 200Amps.Drawing needs to be submitted for prior approval.System sizing design calculations also need to be incorporated in drawing.

## Technical Score Detail
|  | RFQ No: R2569 COST COMPARISON REPORT | RFQ No: R2569 COST COMPARISON REPORT | RFQ No: R2569 COST COMPARISON REPORT | Comp. Date : 06/01/2025 | Comp. Date : 06/01/2025 | Comp. Date : 06/01/2025 | Vendor Name : CHIRAG ELECTRICAL |  | Vendor Name : Arrow Electrical |  | Vendor Name : Electech Enterprises
|  | RFQ No: R2569 COST COMPARISON REPORT | RFQ No: R2569 COST COMPARISON REPORT | RFQ No: R2569 COST COMPARISON REPORT | RFQ #: R2569 | RFQ #: R2569 | RFQ #: R2569 | Contact Name : MOHD AKIL |  | Contact Name : SANTOSH KHAKE |  | Contact Name : Alam
|  | RFQ No: R2569 COST COMPARISON REPORT | RFQ No: R2569 COST COMPARISON REPORT | RFQ No: R2569 COST COMPARISON REPORT | RFQ Date : 06/01/2025 13:21:47 | RFQ Date : 06/01/2025 13:21:47 | RFQ Date : 06/01/2025 13:21:47 | Vendor City : |  | Vendor City : |  | Vendor City :
|  | RFQ No: R2569 COST COMPARISON REPORT | RFQ No: R2569 COST COMPARISON REPORT | RFQ No: R2569 COST COMPARISON REPORT | BCD Date : 06/01/2025 15:01:00 | BCD Date : 06/01/2025 15:01:00 | BCD Date : 06/01/2025 15:01:00 | Telephone # : |  | Telephone # : |  | Telephone # :
|  | RFQ No: R2569 COST COMPARISON REPORT | RFQ No: R2569 COST COMPARISON REPORT | RFQ No: R2569 COST COMPARISON REPORT |  |  |  | Mobile # : 9560263557 |  | Mobile # : |  | Mobile # :
PR Number : TFS GURGAON-2425-00039 | PR Number : TFS GURGAON-2425-00039 | PR Number : TFS GURGAON-2425-00039 | PR Number : TFS GURGAON-2425-00039 | PR Number : TFS GURGAON-2425-00039 | PR Number : TFS GURGAON-2425-00039 | PR Number : TFS GURGAON-2425-00039 | PR Number : TFS GURGAON-2425-00039 | Email : pushpak.shewale@k-corp.in |  | Email : project.arrowelectricals@gmail.com |  | Email : alam@electechenterprises.net
Package / RFQ Name : PR for Electrical for DEL GORDON RAMSAY T1. | Package / RFQ Name : PR for Electrical for DEL GORDON RAMSAY T1. | Package / RFQ Name : PR for Electrical for DEL GORDON RAMSAY T1. | Package / RFQ Name : PR for Electrical for DEL GORDON RAMSAY T1. | Package / RFQ Name : PR for Electrical for DEL GORDON RAMSAY T1. | Package / RFQ Name : PR for Electrical for DEL GORDON RAMSAY T1. | Package / RFQ Name : PR for Electrical for DEL GORDON RAMSAY T1. | Package / RFQ Name : PR for Electrical for DEL GORDON RAMSAY T1. | Round # : 4 (Auction) |  | Round # : 4 (Auction) |  | Round # : 4 (Auction)
Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Quotation Date : |  | Quotation Date : |  | Quotation Date :
Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Currency :INR | Currency :INR | Currency :INR | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date :
Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | BUDGET PRICE : | .00 |  | Quote Currency : |  | Quote Currency : |  | Quote Currency :
# | Item Code | Item Description | Last PO Details | Unit | Qty | Last PO Unit Rate | Last PO Total Value | Score | Justification | Score | Justification | Score | Justification
1 | Electrical | Interior Electrical |  | EA | 1.000 | 0.00 | 0.00
2 | A | CONNECTING INTEGRATING UNIT M E SERVICES TO AIRPORT M E SERVICES BUILDING |  |  | 0.000 | 0.00 | 0.00
3 | A.1 | If any termination connection of the unit services are required outside the site location (i.e. connection of the unit M E to the airport M E or service termination to the airport external façade roof etc.); then the contractor has to work in consultation with the airport to plan, design detail for such connections. The contractor to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor to make good after installation any penetrations including providing fire seals as requried as per airport requirement. |  |  | 0.000 | 0.00 | 0.00
4 | C.1 | Supply and Laying of approved make Fire Rated LSZH XLPE insulated PVC sheathed, Copper conductor, Steel Tape Wire Armoured, 1100V grade cable, Number of Cable Core as per SLD Load Calculation Sheet (Main Cable) Unarmoured Single Core Wire (ECC). The cable shall be laid Underground on Cable Tray through Cable Trunking in Pipe on Wall Trench using necessary supporting clamping arrangements.The cable shall be provided with cable identification tags made out of Aluminium strip, engraved with cable size and the routing. Make - Polycab, KEI, RR, Havells, Gemco |  |  | 0.000 | 0.00 | 0.00
5 | C.1.1 | 3.5C x120 SQ.MM XLPE AL. CABLE |  | Mtr | 20.000 | 0.00 | 0.00
6 | C.1.2 | 4C X 25 SQ.MM XLPE AL. CABLE |  | Mtr | 12.000 | 0.00 | 0.00
7 | C.1.3 | 4C X 6 SQ.MM XLPE CU. CABLE |  | Mtr | 200.000 | 0.00 | 0.00
8 | D | CABLE END TERMINATIONS |  |  | 0.000 | 0.00 | 0.00
9 | D.1 | Supply and Installation of approved make cable end Termination for the following cables using Single Compression Brass Glands, Solderless Tinned Copper Lugs, Gland earthing of adequate size, etc.complete. |  |  | 0.000 | 0.00 | 0.00
10 | D.1.1 | 3.5C x120 SQ.MM XLPE AL. CABLE |  | Nos | 4.000 | 0.00 | 0.00
11 | D.1.2 | 4C X 25 SQ.MM XLPE AL. CABLE |  | Nos | 2.000 | 0.00 | 0.00
12 | D.1.3 | 4C X 6 SQ.MM XLPE CU. CABLE |  | Nos | 16.000 | 0.00 | 0.00
13 | E | DISTRIBUTION BOARDS |  |  | 0.000 | 0.00 | 0.00
14 | E.1 | Supply, Installation, Testing Commissioning of approved make Surface Flush Floor mounting 10kA 25kA Distribution Boards, Devices, Relays and all accessories. The RYB sequence should be provided at the incomer entry, followed by on off and trip indicators. The DB shall be made out of 1.2 mm CRCA sheet steel enclosure and powder coated complete with cable gland plate knock out at the top and bottom. The DB shall have hinged lockable door. The busbar shall be tinned copper, for phases mounted on suitable type Insulator, Independent neutral busbar including inter connecting wiring earth bus on insulation mount, complete with Protective devices (MCCB, MCB, RCCB, RCBO, etc.) The Contractor shall be responsible to supply materials and equipment complying with the green building specification if required. All DB s must named as per the SLD Load Calculation Sheet. Laminated SLD Load Calculation Sheet shall be placed near to DB Locations. The RCCB RCBO shall be Hpi Si series MCB s shall be B C Curve (As per Airport requirement). LT Siwitchgear (MCCB, MCB, RCBO, RCCB) -Legrand, ABB, Schneider, Siemens MFM meter shall be of Digital kVAH Type of approved make or any other make with kVAH option with Approval from TS Department. 160 5A CT with Energy Meter as per the scheme. |  |  | 0.000 | 0.00 | 0.00
15 | E.1.1 | SMDBIncomer 160A 4P MCCB - 1 No.Outgoings63A 4P MCB - 1No.32A 4P RCBO - 10 Nos.20A 2P RCBO - 3 Nos. |  | Each | 1.000 | 0.00 | 0.00
16 | E.1.2 | LPDB16 Way PPI TPN DBIncomer 63A 4P MCB-1 No.40A 30mA 2P RCBO - 3 Nos.Outgoings10 16 20 25 32A SP MCB- 48 Nos.16 Way PPI TPN DBIncomer 63A 4P MCB-1 No.40A 30mA 2P RCBO - 3 Nos.Outgoings10 16 20 25 32A SP MCB- 48 Nos. |  | Each | 1.000 | 0.00 | 0.00
17 | E.1.3 | LDB16 Way SPN DBIncomer 32A 30mA DP RCCB-1 No.Outgoings10 16 20 25A SP MCB- 12 Nos. |  | Each | 1.000 | 0.00 | 0.00
18 | E.1.4 | UPS DB |  | Each | 1.000 | 0.00 | 0.00
19 | F | EARTHING |  |  | 0.000 | 0.00 | 0.00
20 | F.1 | Supply laying testing and commissioning of strip and round conductor (Copper Aluminium GI) as per IS3043 on surface or recess of through conduit of suitable size as required. All body part should be double earthed. |  |  | 0.000 | 0.00 | 0.00
21 | F.1.1 | 25x6 GI Strip |  | Nos | 50.000 | 0.00 | 0.00
22 | F.1.2 | 10 SWG Copper conductor |  | Nos | 24.000 | 0.00 | 0.00
23 | F.1.3 | 12 SWG Copper conductor |  | Nos | 80.000 | 0.00 | 0.00
24 | F.1.4 | 16 SWG Copper conductor |  | Nos | 10.000 | 0.00 | 0.00
25 | G | LIGHT POINT WIRING |  |  | 0.000 | 0.00 | 0.00
26 | G.1 | Supply, Installation, Testing Commissioning of Point wiring (Light Fixtures to be as approved by Architect Design BOQ) with approved makes Switches Lighting Control Switch Board with FRLSH PVC insulated Flexible Copper Wires 660 1100V grade using 2 X 1.5 Sq mm PVC insulated fine stranded single core FRLSH copper conductor wires phase and neutral and with 1.5 Sq mm PVC insulated, green coloured, fine stranded single core copper cable as earth continuity, earth wire crimped to copper socket, fastened using brass bolt and nut etc through suitable size GI Conduit Heavy Duty PVC Conduit GI Trunking (Containment size Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. carrying out Surface Concealed wiring as per site condition maintain aesthetic of the unit.Wiring shall be as per IS 732. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports brackets for conduit and Trunking suspension. Wire Make - Polycab, KEI, RR, Havells, Gemco Modular Switches, Sockets - Legrand, ABB, Schneider, Siemens GI PVC Conduit Make -AKG, BEC (ISI marked) |  |  | 0.000 | 0.00 | 0.00
27 | G.1.1 | 1 No. light point controlled by 1 No 10A, SP Switch. |  | Nos | 21.000 | 0.00 | 0.00
28 | G.1.2 | Secondary light points. (from the first light point without supply and installation of switches.) |  | Nos | 109.000 | 0.00 | 0.00
29 | H | CIRCUIT WIRING |  |  | 0.000 | 0.00 | 0.00
30 | H.1 | Supply, Installation, Testing Commissioning of approved makes FRLSH PVC insulated Flexible Copper Cable Wires 660 1100V grade through suitable size GI Conduit Heavy Duty PVC Conduit GI Trunking (Containment size Type selection as per site requirement) for the following types of wires. For dummy sockets wiring considered. Wire Make - Polycab, KEI, RR, Havells, Gemco GI PVC Conduit Make -AKG, BEC (ISI marked) |  |  | 0.000 | 0.00 | 0.00
31 | H.1.1 | Circuit wiring for light points using 2 Runs of 2.5 sq.mm PVC insulated copper wires along with 1 Run of 1.5 sqmm pvc copper wire (Green) for continuous earthing, through suitable GI Conduit Heavy Duty PVC Conduit GI Trunking from DB to Light control switch box Normal Sockets. |  | Mtr | 900.000 | 0.00 | 0.00
32 | H.1.2 | Power points using 2 Runs of 4 sq.mm PVC insulated copper wires along with 1 Run of 2.5 sqmm pvc copper wire (Green) for continuous earthing, through suitable GI Conduit Heavy Duty PVC Conduit GI Trunking from DB to Power points. |  | Mtr | 300.000 | 0.00 | 0.00
33 | H.1.3 | Power points using 2 Runs of 4 sq.mm PVC insulated copper wires along with 1 Run of 4 sqmm pvc copper wire (Green) for continuous earthing, through suitable GI Conduit Heavy Duty PVC Conduit GI Trunking from Main DB to UPS DB |  | Mtr | 30.000 | 0.00 | 0.00
34 | H.1.4 | Power points using 2 Runs of 6 sq.mm PVC insulated copper wires along with 1 Run of 4 sqmm pvc copper wire (Green) for continuous earthing, through suitable GI Conduit Heavy Duty PVC Conduit GI Trunking from Main DB to LDB |  | Mtr | 10.000 | 0.00 | 0.00
35 | J | POWER POINTS (SWITCHES SOCKETS) |  |  | 0.000 | 0.00 | 0.00
36 | J.1 | Supply, Installation, Testing Commissioning of approved makes Devices (Switches Sockets - Face Plate Finish as approved by Architect Matching to Architecture interior Finishes) complete with suitable GI Back boxes, Earthing, accessories, glands, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. on Surface Concealed as per site condition maintain aesthetic of the unit.Type annd IP rating should be as per Airport requirements. The rate shall include wall chasing, chipping of floors, rough plastering. The unit shall be suitable for 400 ± 15 volts 3 phase and 230 ± 10 volts 1 phase, 50 60 Hz, AC supply as per Airport Country power supply. Modular Switches, Sockets - Legrand, ABB, Schneider, Siemens |  |  | 0.000 | 0.00 | 0.00
37 | J.1.1 | 13A Single Switched Socket Outlet |  | Nos | 10.000 | 0.00 | 0.00
38 | J.1.2 | 13A Dual Switched Socket Outlet |  | Nos | 4.000 | 0.00 | 0.00
39 | J.1.3 | 13A Single Unswitched Socket Outlet |  | Nos | 2.000 | 0.00 | 0.00
40 | J.1.4 | 13A Dual Switched Socket Outlet + Dual USB Port |  | Nos | 10.000 | 0.00 | 0.00
41 | J.1.5 | 16A Single Switched Socket Outlet |  | Nos | 33.000 | 0.00 | 0.00
42 | J.1.6 | 16A Single Unswitched Socket Outlet |  | Nos | 1.000 | 0.00 | 0.00
43 | J.1.7 | 13A One Gang One Way Switch |  | Nos | 2.000 | 0.00 | 0.00
44 | J.1.8 | Double Pole Switch With Neon Indicator |  | Nos | 1.000 | 0.00 | 0.00
45 | J.1.9 | 16A Single Phase Industrial Switched Socket (3 pin) ((wall mounted metal clad socket) |  | Nos | 3.000 | 0.00 | 0.00
46 | J.1.10 | 20A Single Phase Industrial Switched Socket (3 pin) ((wall mounted metal clad socket) |  | Nos | 7.000 | 0.00 | 0.00
47 | J.1.11 | 32A Three Phase Industrial Switched Socket (5 pin) ((wall mounted metal clad socket) |  | Nos | 6.000 | 0.00 | 0.00
48 | J.1.12 | 20A Three Phase Isolator with Enclosure |  | Nos | 2.000 | 0.00 | 0.00
49 | K | CONTAINMENT |  |  | 0.000 | 0.00 | 0.00
50 | K.1 | Supply Installation of approved makes GI Conduit Heavy Duty PVC Conduit, through Wall Ceiling Floor as per drawings, complete with ISI standard accessories factory made fittings. GI PVC Conduit Make -AKG, BEC (ISI marked) Cable tray- MEM, Profab (ISI marked) |  |  | 0.000 | 0.00 | 0.00
51 | K.1.1 | 250x 50 mm Cable Tray |  | Mtr | 20.000 | 0.00 | 0.00
52 | K.1.2 | 200x 50 mm Cable Tray |  | Mtr | 5.000 | 0.00 | 0.00
53 | K.1.3 | 100x 50 mm Cable Tray |  | Mtr | 55.000 | 0.00 | 0.00
54 | L | UPS SYSTEM |  |  | 0.000 | 0.00 | 0.00
55 | L.1 | Supply, Installation, Testing Commissioning of approved makes UPS along with required Battery for specified back-up time, complete with Battery Stand (If required) standard accessories equipments required for complete functioning of the system, earthing, support system (if required), etc. The Contractor shall be responsible to supply materials and equipment complying with the green building specification if required. |  |  | 0.000 | 0.00 | 0.00
56 | L.1.1 | 2 KVA Single phase UPS with 30 Minute Back-up |  | Nos. | 1.000 | 0.00 | 0.00
57 | M | CCTV SYSTEM |  |  | 0.000 | 0.00 | 0.00
58 | M.1 | Supply, Installation, Testing Commissioning of approved makes CCTV System with suitable required cabling through suitable size GI Conduit GI Trunking (Containment size Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with CCTV console DVR with Power Box , Suitable POE with Port switch Surveillance hard disk,etc. carrying out Surface Concealed wiring as per site condition maintain aesthetic of the unit. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports brackets for conduit and Trunking suspension. |  |  | 0.000 | 0.00 | 0.00
59 | M.1.1 | CCTV Ceiling Mount Dome Camera, As approved or confirmed by client with all neccessary accessories, etc. |  | Nos | 0.000 | 0.00 | 0.00
60 | M.1.2 | Suitable size IDF RACK with Necessary Patch Panel Network switch as required. |  | Nos | 0.000 | 0.00 | 0.00
61 | M.1.3 | 16-Channel DVR |  | Nos | 0.000 | 0.00 | 0.00
62 | M.1.4 | 3+ 1 cable on surface concealed wall, including suitable conduits, fittings, accessories, etc. |  | Mtr. | 150.000 | 0.00 | 0.00
63 | N | DATA NETWORK SYSTEM |  |  | 0.000 | 0.00 | 0.00
64 | N.1 | Supply, Installation, Testing Commissioning of approved makes Data Telephone Network System with required cabling through suitable size GI Conduit Heavy Duty PVC Conduit GI Trunking (Containment size Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with IDF SERVER Rack using patch cordes, etc. carrying out Surface Concealed wiring as per site condition maintain aesthetic of the unit. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports brackets for conduit and Trunking suspension. |  |  | 0.000 | 0.00 | 0.00
65 | N.1.1 | Single Data outlet (RJ45) Jack |  | Nos | 4.000 | 0.00 | 0.00
66 | N.1.2 | Dual Data outlet (RJ45) Jack |  | Nos | 2.000 | 0.00 | 0.00
67 | N.1.3 | WIFI Router |  | Nos | 1.000 | 0.00 | 0.00
68 | N.1.4 | SITC of CAT6 cable on surface concealed wall, including suitable conduits, fittings, accessories, etc.(For dummy points cabling considered) |  | Mtr. | 220.000 | 0.00 | 0.00
69 | O | PA SYSTEM |  |  | 0.000 | 0.00 | 0.00
70 | O.1 | Supply, Installation, Testing Commissioning of approved makes PA System with required cabling through suitable size GI Conduit GI Trunking (Containment size Type selection as per site requirement), complete with suitable GI back boxes, Earthing, EOLR, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with IDF Rack, etc. carrying out Surface Concealed wiring as per site condition maintain aesthetic of the unit. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports brackets for conduit and Trunking suspension. |  |  | 0.000 | 0.00 | 0.00
71 | O.1.1 | 6 Watts ceiling mount Speaker with all the necessary accessories |  | Nos | 5.000 | 0.00 | 0.00
72 | O.1.2 | Volume Controller |  | Nos | 1.000 | 0.00 | 0.00
73 | O.1.3 | PA Controller with Amplifier |  | Nos | 1.000 | 0.00 | 0.00
74 | O.1.4 | SITC of 2C 1.5 Sq mm Cu multi-stranded PVC insulated shielded FRLS cable |  | Mtr. | 50.000 | 0.00 | 0.00
75 | P | ELECTRICAL SERVICE IDENTIFICATION LABELS, SIGNS TAGS |  |  | 0.000 | 0.00 | 0.00
76 | P.1 | All services like Panels, Cables, Pipes etc need to be clearly labelled or tagged at site with service identification, direction etc. And all equipment needs to tagged as per Airport requirements. |  |  | 0.000 | 0.00 | 0.00
77 | P.1.1 | Labelling Tagging for Services and Equipment s |  | Lot | 1.000 | 0.00 | 0.00
78 | Q | MISCELLANEOUS |  |  | 0.000 | 0.00 | 0.00
79 | Q.1 | The contractor needs to mention any additional items or missing items that are not mentioned in the above BOQ after a detailed site survey or inspection and to be validated by consultants. |  |  | 0.000 | 0.00 | 0.00
80 | Q.1.1 | Providing and Fixing of Electrical Standard Grade Rubber Mat suitable for LT Volts |  | Unit | 1.000 | 0.00 | 0.00
81 | Q.1.2 | Provide and Fixing Shock Treatment Chart |  | Unit | 1.000 | 0.00 | 0.00
82 | Q.1.3 | Provide and Fixing of L.T. danger sign boards in Panel side |  | Unit | 1.000 | 0.00 | 0.00
83 | R | SHOP DRAWINGS APPROVALS |  |  | 0.000 | 0.00 | 0.00
84 | R.1 | Preparation and submission of a detailed shop drawing for the electrical system after a thorough study of design drawings, site surveys, and relevant airport standards with correct routing, size, and elevations. The drawings also need to be coordinated with other MEP services like HVAC, plumbing, and fire services, along with updating SLD, load calculation sheets, and power layouts as per approved, selected, or supplied equipment power and phase requirements, this also needs to be coordinated with latest architectural, structural and interior design drawings, before construction. Necessary amendments to the drawings are to be made and resubmitted in case of any variations on site while at the construction stage of the project. Also prepare relevant detailed connection drawings as per selected manufacturer details and airport standards, with necessary approval to be obtained from consultants and authority regulatory bodies having jurisdiction, along with material submission approval with airport authorities. |  |  | 0.000 | 0.00 | 0.00
85 |  | General guideline for onsite electrical works 1. DB have per phase RCBO protection.2. Minimum wire size shall be 2.5 Sq. mm and power circuits wire size should be 4.0 sq.mm.3. All equipment’s above 1 KW shall be provided with ELCB shall run operated through industrial type switch socket only.4. Only GI conduit will be used.5. Equipment protection devices and appropriate earthing as per approved load to be provided.6. All DB and panel have dual earthing connection.7. All internal wires cables shall be FRLSH FRLSZH.8. Main distribution board will not be fixed on wooden material.9. IT , Data and low voltage wires shall be drawn In Separate10. Switch Sockets outlets will not be over loaded with multiple connection conduit and not with electrical11. All lights shall be LED.12. Provision of Emergency light should be there.13. No combustive material are to be store under closed the electrical switch board distribution board meter etc.14. The concessioner should install suitable type rated fire extinguisher near electrical panel.15. Shutter type switch socket outlet on suitable MS box shall be used with proper earthing.16. All electrical equipment shall be proper earthed and connected to main earthing with suitably sized earthing conductor.17. Final approved Single line diagram sealed in a plastic folder shall be provided inside each electrical panel.13. No combustive material are to be store under closed the electrical switch board distribution board meter etc.18. Load balancing to be done.19. Power connection for Existing BTU meter Water meter to be provided from concessionaire DB.20. All electrical source to be enclosure with IP65 Device with louvered openable cabinet and all fire protection.21. Panel GA drawing to be share with DIAL for approval.22. Before installation, material inspection to be done.23. Test certificate for installed electrical material to be submitted to DIAL . 24. If any changes due to site constraint, prior intimation to be provided to DIAL. Post approval only SLD to revised.25.all SP MCB as ‘C’ characteristic.In case, Incomer rating equal to or more than 200Amps Automatic Tube Detection and Suppression System to be doneCO2,FM200 HFC-227ea gas based automatic tube detection suppression system needs to be installed for Electrical Panel with Incomer rating equal to or more than 200Amps.Drawing needs to be submitted for prior approval.System sizing design calculations also need to be incorporated in drawing. |  |  | 0.000 | 0.00 | 0.00