## Summary
Outlet- Nando's HVAC, FAS & Fire Sprinklers
Budget- 21,31,272
RFQ No: R2174 COST COMPARISON REPORT | Comp. Date : 15/11/2024
| PIONEER PROJECT SOLUTION |  |  | ANJLE MEP PROJECT |  |  | CRYSTAL AIRCOOL |  | Mahamaya Engineering
Rounds | R0 | R1 | Auction | R0 | R1 | Auction | R0 | Auction | R0 | R1 | Auction
HVAC high side | 610000 | 573000 | 545000 | 975000 | 635000 | 745000 | 641500 | 535000 | 1243970 | 766970 | 600000
Hvac - low side | 1910150 | 1816000 | 1750000 | 2516250 | 2177180 | 2270250 | 2854440 | 2102075 | 4182525 | 2853500 | 1900000
Fire Sprinkler | 218750 | 181155 | 181155 | 226650 | 214500 | 210650 | 262445 | 191741 | 303700 | 217450 | 185000
FAS | 147650 | 124000 | 124000 | 170534 | 171134 | 171134 | 181850 | 114650 | 432000 | 178200 | 132000
Total | 2886550 | 2694155 | 2600155 | 3888434 | 3197814 | 3397034 | 3940235 | 2943466 | 6162195 | 4016120 | 2817000
Suppliers Invited
PIONEER PROJECT SOLUTION | FL Group
ANJLE MEP PROJECT | Inventech Solutions
CRYSTAL AIRCOOL | TAMIL CONSTRUCTION
Mahamaya Engineering | Yashvas Interiors
M & A Interiors
A K PROJECTS
NS Associate
FL Group

## BOQ Price Bid
|  | RFQ No: R2174 COST COMPARISON REPORT | Comp. Date : 13/11/2024 | Comp. Date : 13/11/2024 | Comp. Date : 13/11/2024 | Vendor Name : PIONEER PROJECT SOLUTION | Vendor Name : PIONEER PROJECT SOLUTION | Vendor Name : PIONEER PROJECT SOLUTION | Vendor Name : PIONEER PROJECT SOLUTION | Vendor Name : PIONEER PROJECT SOLUTION | Vendor Name : PIONEER PROJECT SOLUTION | Vendor Name : ANJLE MEP PROJECT PVT LTD | Vendor Name : ANJLE MEP PROJECT PVT LTD | Vendor Name : ANJLE MEP PROJECT PVT LTD | Vendor Name : ANJLE MEP PROJECT PVT LTD | Vendor Name : ANJLE MEP PROJECT PVT LTD | Vendor Name : ANJLE MEP PROJECT PVT LTD | Vendor Name : CRYSTAL AIRCOOL | Vendor Name : CRYSTAL AIRCOOL | Vendor Name : CRYSTAL AIRCOOL | Vendor Name : CRYSTAL AIRCOOL | Vendor Name : Mahamaya Engineering | Vendor Name : Mahamaya Engineering | Vendor Name : Mahamaya Engineering | Vendor Name : Mahamaya Engineering | Vendor Name : Mahamaya Engineering | Vendor Name : Mahamaya Engineering
|  | RFQ No: R2174 COST COMPARISON REPORT | RFQ #: R2174 | RFQ #: R2174 | RFQ #: R2174 | Contact Name : Mohd Ashraf | Contact Name : Mohd Ashraf | Contact Name : Mohd Ashraf | Contact Name : Mohd Ashraf | Contact Name : Mohd Ashraf | Contact Name : Mohd Ashraf | Contact Name : PREMKANT | Contact Name : PREMKANT | Contact Name : PREMKANT | Contact Name : PREMKANT | Contact Name : PREMKANT | Contact Name : PREMKANT | Contact Name : JOHN | Contact Name : JOHN | Contact Name : JOHN | Contact Name : JOHN | Contact Name : Yash Katoch | Contact Name : Yash Katoch | Contact Name : Yash Katoch | Contact Name : Yash Katoch | Contact Name : Yash Katoch | Contact Name : Yash Katoch
|  | RFQ No: R2174 COST COMPARISON REPORT | RFQ Date : 07/11/2024 17:00:07 | RFQ Date : 07/11/2024 17:00:07 | RFQ Date : 07/11/2024 17:00:07 | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City : delhi | Vendor City : delhi | Vendor City : delhi | Vendor City : delhi | Vendor City : delhi | Vendor City : delhi
|  | RFQ No: R2174 COST COMPARISON REPORT | BCD Date : 14/11/2024 23:55:00 | BCD Date : 14/11/2024 23:55:00 | BCD Date : 14/11/2024 23:55:00 | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # : 9810360460 | Telephone # : 9810360460 | Telephone # : 9810360460 | Telephone # : 9810360460 | Telephone # : 9810360460 | Telephone # : 9810360460
|  | RFQ No: R2174 COST COMPARISON REPORT |  |  |  | Mobile # : | Mobile # : | Mobile # : | Mobile # : | Mobile # : | Mobile # : | Mobile # : | Mobile # : | Mobile # : | Mobile # : | Mobile # : | Mobile # : | Mobile # : | Mobile # : | Mobile # : | Mobile # : | Mobile # : 9810360460 | Mobile # : 9810360460 | Mobile # : 9810360460 | Mobile # : 9810360460 | Mobile # : 9810360460 | Mobile # : 9810360460
PR Number : TFSPL-2425-00916,TFSPL-2425-00917,TFSPL-2425-00920 | PR Number : TFSPL-2425-00916,TFSPL-2425-00917,TFSPL-2425-00920 | PR Number : TFSPL-2425-00916,TFSPL-2425-00917,TFSPL-2425-00920 | PR Number : TFSPL-2425-00916,TFSPL-2425-00917,TFSPL-2425-00920 | PR Number : TFSPL-2425-00916,TFSPL-2425-00917,TFSPL-2425-00920 | PR Number : TFSPL-2425-00916,TFSPL-2425-00917,TFSPL-2425-00920 | Email : projectspioneer@gmail.com | Email : projectspioneer@gmail.com | Email : projectspioneer@gmail.com | Email : projectspioneer@gmail.com | Email : projectspioneer@gmail.com | Email : projectspioneer@gmail.com | Email : anjlemepprojects@gmail.com | Email : anjlemepprojects@gmail.com | Email : anjlemepprojects@gmail.com | Email : anjlemepprojects@gmail.com | Email : anjlemepprojects@gmail.com | Email : anjlemepprojects@gmail.com | Email : crystalhvac002@gmail.com | Email : crystalhvac002@gmail.com | Email : crystalhvac002@gmail.com | Email : crystalhvac002@gmail.com | Email : mahamaya.engineering1@gmail.com | Email : mahamaya.engineering1@gmail.com | Email : mahamaya.engineering1@gmail.com | Email : mahamaya.engineering1@gmail.com | Email : mahamaya.engineering1@gmail.com | Email : mahamaya.engineering1@gmail.com
Package / RFQ Name : PR for HVAC, Fire & FAS for DEL NANDOS T3 INT | Package / RFQ Name : PR for HVAC, Fire & FAS for DEL NANDOS T3 INT | Package / RFQ Name : PR for HVAC, Fire & FAS for DEL NANDOS T3 INT | Package / RFQ Name : PR for HVAC, Fire & FAS for DEL NANDOS T3 INT | Package / RFQ Name : PR for HVAC, Fire & FAS for DEL NANDOS T3 INT | Package / RFQ Name : PR for HVAC, Fire & FAS for DEL NANDOS T3 INT | Round # : 2 (RFQ) | Round # : 2 (RFQ) | Round # : 3 (RFQ) | Round # : 3 (RFQ) | Round # : 5 (RFQ) | Round # : 5 (RFQ) | Round # : 2 (RFQ) | Round # : 2 (RFQ) | Round # : 3 (RFQ) | Round # : 2 (RFQ) | Round # : 5 (RFQ) | Round # : 5 (RFQ) | Round # : 2 (RFQ) | Round # : 2 (RFQ) | Round # : 5 (RFQ) | Round # : 5 (RFQ) | Round # : 2 (RFQ) | Round # : 2 (RFQ) | Round # : 3 (RFQ) | Round # : 3 (RFQ) | Round # : 5 (RFQ) | Round # : 5 (RFQ)
Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score :
Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Currency :INR | Currency :INR | Currency :INR | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date :
Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | BUDGET PRICE :.00 | BUDGET PRICE :.00 | BUDGET PRICE :.00 | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date :
Sr No. | Item Code | Item Description | UOM | Qty | Minimum Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount
1 |  | HVAChigh side | NOS | 1 |  |  | 610000 |  | 573000 |  | 545000 |  | 975000 |  | 635000 |  | 745000 |  | 641500 |  | 535000 |  | 1243970 |  | 766970 |  | 600000
1 |  | Prices shall be based on supply, installation, testing commissioning (SITC) at site including all taxes, duties, transportation insurance etc.
2 | 1 | VRF SYSTEMS VRF OUTDOOR UNITS Supply of air cooled variable refrigerant flow modular type condensing units, each comprising of multiple scroll compressors all inverter driven, full charge of refrigerant gas (R-410a), lubricating oil and all accessories as per the specifications. The condensing units shall be suitable to work on heating cooling mode. The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B . The COP of the system shall be greater than 4 under ARI conditions for 100% load . The condensing units shall be suitable for operation on 415 ± 10% volts, 50Hz, 3 phase AC power supply. VRF unit shall be supplied with operating panel for operation control. ODU to have standard factory coated treatment for heat rust corrosion for Condenser coil, panels, motor, electricals heat exchanger, Power Cabling etc. The condensing units shall be of following capacities Refrigeration Capacities indicated below are actual capacity. Selection to be done considering referigerant piping length and derating at @ 40°C. Vendor has to submit highlight if capacity of the unit exceed diversity factor after derating for 40°C ambient conditions. Any alteration in capacity after bidding will not be entertain. Vendor has to provide unit to meet the refrigeration requirement. Make Daikin, Toshiba, Mitsubishi Refrigeration Capacity - 14 HP | Nos | 1 | 315000 | 315000 | 315000 | 295000 | 295000 | 285000 | 285000 | 415000 | 415000 | 315000 | 315000 | 415000 | 415000 | 375000 | 375000 | 295500 | 295500 | 532000 | 532000 | 383000 | 383000 | 383000 | 383000
3 | 2.1 | VRF INDOOR UNITS Supply,Installation,Testing and Commissioning of variable refrigerant flow modular type indoor units Corded Cordless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling as well as heating mode. The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 ±6% volts, 50Hz, 1 phase AC power supply. Ductable indoor units shall be suitable to handle extent of ductwork as shown in the design drawings and dehumidified air quantity as mentioned below. The indoor unit shall be complete with pre filter remote as per requirement. Unit shall be quoted with T-Tube flange connection kit for for higher fresh air intake. Except Hi-wall unit, all other units shall have port for fresh air intake and inbuilt drain pump. The indoor units shall be of following capacities . HIGH STATIC DUCTABLE TYPE INDOOR UNIT with CORDED REMOTE CONTROLLER Indoor Temperature NMT 22°C 2542 CFM 6.4 TR | Nos. | 2 | 190000 | 105000 | 210000 | 100000 | 200000 | 91000 | 182000 | 165000 | 330000 | 115000 | 230000 | 165000 | 330000 | 95000 | 190000 | 90000 | 180000 | 290000 | 580000 | 135000 | 270000 | 135000 | 270000
4 | 2.2 | CEILING MOUNTED TYPE COMPACT CASSETTE UNIT with CORDLESS REMOTE CONTROLLER Indoor Temperature NMT 22°C 318 CFM 0.6 TR | Nos. | 1 | 35000 | 40000 | 40000 | 37500 | 37500 | 37500 | 37500 | 65000 | 65000 | 45000 | 45000 | 65000 | 65000 | 35000 | 35000 | 34000 | 34000 | 86000 | 86000 | 68000 | 68000 | 68000 | 68000
5 | 3 | CENTRALISED REMOTE CONTROLLER Supply of the Graphic central remote Controller (Touch Screen Type) . It must act as an advanced air conditioning management system to facilitate complete control of VRF air conditioning equipment. It should be user friendly through its touch screen, icon display and color LCD display. Integratable upto 64 remote controller groups (including AHUs TFAs) and BMS compatible with ethernet Wi-Fi communication protocol for remote monitoring. In addition to basic controls such as settings for on stop, the operation mode temperature, the air quantity and auto louver can be set. If a problem occurs, an alarm code immediately shows the details of the problem. An external input terminal is provided as standard. External signals enable the following function central operation stop, demand control, emergency stop, central operation output, central alarm output. Controller shall however be suitable for future connectivity of indoor outdoor units also. Central Remote Controller | Nos. | 1 | 41500 | 45000 | 45000 | 40500 | 40500 | 40500 | 40500 | 165000 | 165000 | 45000 | 45000 | 165000 | 165000 | 41500 | 41500 | 39500 | 39500 | 45970 | 45970 | 45970 | 45970 | 45970 | 45970
6 |  | GENERAL NOTES The cost shall be included liftting shifting of each equipment material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material equipment.
2 |  | Hvac - low side | NOS | 1 |  |  | 1910150 |  | 1816000 |  | 1750000 |  | 2516250 |  | 2177180 |  | 2270250 |  | 2854440 |  | 2102075 |  | 4182525 |  | 2853500 |  | 1900000
7 | 2 | INDIGENOUS WORK
8 | 2.1 | INSTALLATION OF VRF OUT-DOOR UNITS
9 |  | Installation, Charging, Testing and commissioning of VRF system with Environment friendly refrigerant gas for the below mentioned system. This shall include lifting, shifting and positioning of outdoor units, nitrogen leak testing, oil charging, vaccumisation etc.,
10 | a | Refrigeration Capacity - 14 HP | Nos. | 1 | 20000 | 20000 | 20000 | 18000 | 18000 | 15000 | 15000 | 45000 | 45000 | 25000 | 25000 | 45000 | 45000 | 49000 | 49000 | 28000 | 28000 | 120000 | 120000 | 45000 | 45000 | 45000 | 45000
11 | 2.2 | INSTALLATION OF VRF INDOOR UNITS
12 |  | Installation, Charging, Testing and commissioning of units complete with centrifugal blower, cooling coil with suitable rows, electronic expansion valves, high efficiency pre filter sections, drain pump etc as per specifications.
13 | 0 | 2542 CFM 6.4 TR | Nos. | 2 | 15000 | 7500 | 15000 | 7000 | 14000 | 7000 | 14000 | 8500 | 17000 | 7500 | 15000 | 8500 | 17000 | 8500 | 17000 | 7500 | 15000 | 18000 | 36000 | 12750 | 25500 | 12750 | 25500
14 | 0 | 318 CFM 0.6 TR | Nos. | 1 | 2000 | 2500 | 2500 | 2200 | 2200 | 2200 | 2200 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2500 | 2500 | 1800 | 1800 | 15000 | 15000 | 6750 | 6750 | 6750 | 6750
15 | 2.3 | INSTALLATION OF CENTRALISED REMOTE CONTROLLER
16 |  | Installation, Charging, Testing and commissioning of of the Graphic central remote Controller (Touch Screen Type) . It must act as an advanced air conditioning management system to facilitate complete control of VRF air conditioning equipment. It should be user friendly through its touch screen, icon display and color LCD display. Integratable upto 64 remote controller groups (including AHUs TFAs) and BMS compatible with ethernet Wi-Fi communication protocol for remote monitoring. In addition to basic controls such as settings for on stop, the operation mode temperature, the air quantity and auto louver can be set. If a problem occurs, an alarm code immediately shows the details of the problem. An external input terminal is provided as standard. External signals enable the following function central operation stop, demand control, emergency stop, central operation output, central alarm output. Controller shall however be suitable for future connectivity of indoor outdoor units also.
17 | a | Central Remote Controller | Nos. | 1 | 4500 | 5000 | 5000 | 4500 | 4500 | 3000 | 3000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 4050 | 4050 | 4500 | 4500 | 4800 | 4800 | 4800 | 4800
18 | 2.4 | VRF REFRIGERANT PIPING FITTING WITH INSULATION
19 |  | Supply, Installation, Testing and Commissioning of the refrigerant piping with nitrile rubber insulation in sleeve form.It should be selected for maximum working pressure of 624 psi for R – 410a refrigerant circuit and for maximum working pressure of 500psi in case of R407C refrigerant. The Ref. Piping shall be pressure tested at 1.5 times the working pressure. Copper pipes shall be made of phosphorus deoxidized seamless copper. Minimum thickness to be used for refrigerant piping shall be as follows The insulation( Nitrile rubber, class-O, self extinguishing, CFC free, thermal conductivity of not more than .035w Wm°K shall be 19 mm thick for suction piping liquid line. All Exposed Piping on the floor shall be enclosed in openable GI trays insulation should be with UV protection with mil cloth.The Ref. Piping shall be properly supported at every 1.5 m distance with stands and support linked with rubber as per specifications. | Rmt | 75 | 153750 | 2050 | 153750 | 1950 | 146250 | 1950 | 146250 | 2450 | 183750 | 2250 | 168750 | 2450 | 183750 | 2350 | 176250 | 1845 | 138375 | 3200 | 240000 | 2800 | 210000 | 2800 | 210000
20 |  | Make Maxflow Mandev Heling
21 |  | Note Referiferant piping shall include liquid + gas pipe with all necessory fittings. Also, the size of the same shall be as per manufactured standard.
22 | 2.5 | GAS CHARGING
23 |  | Additional gas charging - Over and above standard Gas charging quantity | Kg | 15 | 15000 | 1000 | 15000 | 950 | 14250 | 900 | 13500 | 2050 | 30750 | 2050 | 30750 | 2050 | 30750 | 1550 | 23250 | 1550 | 23250 | 1500 | 22500 | 1250 | 18750 | 1250 | 18750
24 | 2.6 | REFNET JOINTS
25 |  | SITC of Special Refrigerant T Y-joints for VRF units | Nos | 2 | 3600 | 3500 | 7000 | 3000 | 6000 | 2850 | 5700 | 6500 | 13000 | 6500 | 13000 | 6500 | 13000 | 5500 | 11000 | 5500 | 11000 | 1800 | 3600 | 2300 | 4600 | 2300 | 4600
26 | 2.7 | POWER CABLING
27 |  | Supply, handling, laying effecting proper connections testing and commissioning of following sizes of 1.1 KV grade XLPE insulated FRLS Aluminium Copper conductor cables laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with Copper earthing as specified for continuous earthing along with cable. (Earthing will be measured separately and need not be quoted under this item). All complete as required and as per final instruction as given by Owners Consultants. (MCCB,s provided 5m from Outdoor unit).
28 |  | Make Polycab, KEI Finolex
29 | b | Suitable copper Armoured cable - from MCB Isolator to VRF ODU. | Rmt | 5 | 1750 | 350 | 1750 | 325 | 1625 | 300 | 1500 | 1050 | 5250 | 1050 | 5250 | 1050 | 5250 | 370 | 1850 | 365 | 1825 | 415 | 2075 | 415 | 2075 | 415 | 2075
30 | d | 8 SWG Copper Wire | Rmt | 10 | 1500 | 150 | 1500 | 140 | 1400 | 100 | 1000 | 150 | 1500 | 150 | 1500 | 150 | 1500 | 320 | 3200 | 250 | 2500 | 755 | 7550 | 275 | 2750 | 275 | 2750
31 | 2.8 | COMMUNICATION CABLE
32 |  | SITC of the control cabling from Indoor to outdoor unit Outdoor unit to CRC BACnet for all the units with the necessary fittings. The cabling shall be of weather proof type as most of the cabling will have open exposure to atmosphere. The cabling shall be bundled properly and shall be neatly aligned with the Refrigerant piping. The cabling shall be well supported with G.I cable tray throughout the piping length.
33 |  | Make Polycab, KEI Finolex
34 | a | 1.5 sqmm 2 core | Rmt | 135 | 20250 | 150 | 20250 | 140 | 18900 | 120 | 16200 | 250 | 33750 | 250 | 33750 | 250 | 33750 | 290 | 39150 | 200 | 27000 | 450 | 60750 | 220 | 29700 | 220 | 29700
35 | 2.9 | PERFORATED GI CABLE TRAYS
36 |  | Supplying Fixing of following sizes of Perforated GI cable tray duly painted of height 50mm along with necessary bends, reducers etc. anchored along the wall suspended from the ceiling with necessary MS supports. External Internal refrigerant piping shall be provided and laid on GI covered cable trays with cover.
37 | a | 150mm wide | Rmt | 25 | 13750 | 550 | 13750 | 525 | 13125 | 525 | 13125 | 650 | 16250 | 550 | 13750 | 650 | 16250 | 650 | 16250 | 495 | 12375 | 1450 | 36250 | 875 | 21875 | 875 | 21875
38 | b | 300mm wide | Rmt | 50 | 37500 | 750 | 37500 | 675 | 33750 | 675 | 33750 | 950 | 47500 | 850 | 42500 | 950 | 47500 | 850 | 42500 | 675 | 33750 | 2350 | 117500 | 1150 | 57500 | 1150 | 57500
39 | 2.1 | FRAMEWORK FOR VRF ODU
40 |  | Supply, Fabrication and Installation of MS frame using channels angle iron sections as required for mounting of air cooled remote condenser in service areas or terrace level. The frame work shall be applied with red oxide primer and thereafter, two coats of enamel paint of approved colour. The general arrangement drawing for frame work shall be got approved from the Architects Structural Engineers prior to commencement of fabrication. | Nos. | 1 | 8500 | 8500 | 8500 | 8000 | 8000 | 8000 | 8000 | 25000 | 25000 | 15000 | 15000 | 25000 | 25000 | 10500 | 10500 | 9500 | 9500 | 15000 | 15000 | 11000 | 11000 | 11000 | 11000
41 | 2.11 | INSULATED CONDENSATE DRAIN PIPE
42 |  | SITC of UPVC pipes of following sizes for drain with necessary supports and fittings such as elbows, tees reducers etc. The insulation line to be insulated with nitrile rubber insulation of thickness 9mm and wrapped by weather proof protection tape. The Pipe wherever concealed should also have a parallel line as a standby arrangement in case of block of primary pipe .
43 |  | Make Supreme, Prince, Astral
44 | a | 25 mm Dia | Rmt | 30 | 4800 | 160 | 4800 | 150 | 4500 | 150 | 4500 | 350 | 10500 | 250 | 7500 | 350 | 10500 | 175 | 5250 | 170 | 5100 | 389 | 11670 | 220 | 6600 | 220 | 6600
45 | b | 32 mm Dia | Rmt | 20 | 3600 | 180 | 3600 | 165 | 3300 | 165 | 3300 | 450 | 9000 | 350 | 7000 | 450 | 9000 | 185 | 3700 | 180 | 3600 | 489 | 9780 | 280 | 5600 | 280 | 5600
46 | 2.12 | Supply, installation of Cowl piece connection with bird screen for VRF Outdoor units | Nos | 1 | 7500 | 7500 | 7500 | 7000 | 7000 | 6000 | 6000 | 8000 | 8000 | 5000 | 5000 | 8000 | 8000 | 10000 | 10000 | 9000 | 9000 | 12000 | 12000 | 12000 | 12000 | 12000 | 12000
47 | Note : | Quantities of refrigerant piping and cabling are based on the drawings with Indoor Outdoor units Locations shown and for the specified configuration. Vendor to confirm refrigerant piping and cabling quantities based on the system configuration being offered by them.
48 | 3 | VENTILATION SYSTEM
49 | 3.1 | KITCHEN EXHAUST FAN
50 |  | SITC of Cabinet type SISW Centrifugal Blower, Belt Direct Drive, Statically Dynamically Balanced, Backward Curved Impeller fan, Dunlop Anti- Vibration Pads etc. Motor should be outside stream with TEFC squirrel cage, weather protection shield, IP 55 rating with Class H Insulation, suitable for 3phase, 415volts, 50hz power supply. Sound level should be 65dB @ 3mtr distance. The quote shall include with MS frame, starter panel along with its required cable. Supplied with Dunlop Anti- Vibration Pads Canvass Connection. Fan shall be BMS compatible. Power will be provided 5 ft away from fan and necessary control wiring with plug will be provided by AC contractor.(Vendor to crosscheck static pressure calculation).
51 |  | Make Kruger Nicotra Avantec
52 | a | 6600 CFM, 65mm ESP (Class H) | Nos. | 1 | 145000 | 165000 | 165000 | 160000 | 160000 | 160000 | 160000 | 235000 | 235000 | 195000 | 195000 | 235000 | 235000 | 145000 | 145000 | 142000 | 142000 | 415000 | 415000 | 170000 | 170000 | 170000 | 170000
53 | 3.2 | KITCHEN DRY SCRUBBER
54 |  | SITC of Dry scrubber – Electrostatic Air cleaner with starter panel as per specifications, suitable for following capacities, including electrical starter panel . The Air filtration efficiency should be between 90 to 95% units shall be staked one above other or side by side as per site requirement, if vendor will propose multiple units.
55 |  | Finishing - Power coated, Dark Blue
56 |  | Operating voltage - 220 Vac+ -10%, 50 Hz (Single phase)
57 |  | Features - Short circuit, arc protection and auto restore power supply, BMS (Building Management System) terminals provided, Auto power cut-off when door is opened, Indicator LEDs for normal or wash indicator, Set of Terminals for remote LED normal or wash indicator
58 |  | Efficiency - Upto 95%, meets NIOSH 5026 Oil Mist Test
59 |  | Particle Size - Collects particles as small as 0.01 microns
60 |  | Motor - Sealead ball bearings UL, single phase.
61 |  | Cell - Ionizing voltage - 12 KVdc
62 |  | Collector voltage - 6 KVdc
63 |  | One cell comprising of 9 ionizing wires and 25 collection plates
64 |  | Controls - Auto cut-off when door is opened. Indicator lights for fault, normal or wash function.
65 |  | Pre-filter - Aluminium mesh, washable Dry contact for BMS.
66 |  | Make Rydair Espair
67 |  | CFM - 6600 | Nos. | 1 | 235000 | 235000 | 235000 | 230000 | 230000 | 226925 | 226925 | 450000 | 450000 | 315000 | 315000 | 450000 | 450000 | 255000 | 255000 | 245000 | 245000 | 430000 | 430000 | 275000 | 275000 | 275000 | 275000
68 | 3.2 | KITCHEN FRESH AIR FAN WITH AIRWASHER TYPE
69 |  | SITC of CELDEK FILL package type air cooling unit with minimum 90% saturation efficiency. Air cooling unit shall be factory assembled and complete with double skin casing 0.8mm Inner outer pre-coated GI sheets, DIDW forward curved fans with TEFC, sq. cage, induction motors 1440 RPM (IE-3) with IP-55 Protection. Suitable for operation on 415 ± 10% voltage, 50 Hz 3 phase AC supply, drive package including multi sheave pulleys and belts for fans and motors, 1.2mm thick tank pad section in SS Construction, vibration isolators, wire mesh pre-filters, 200 mm thick CELDEK FILL, 1HP Water Circulation Pump (1W+1S), internal PVC piping, valves and fittings, 4-bend PVC eliminator. MERV 8 G4 pleated pre-filters should be made of 100% synthetic media to capture common airborne contaminants as per ASHRAE Standard 52.2. (Vendor to crosscheck static pressure calculation)
70 |  | Make Kruger Nicotra Avantec
71 | a | 5600 CFM, 50mm ESP (Class F) | Nos. | 1 | 135000 | 155000 | 155000 | 145000 | 145000 | 145000 | 145000 | 265000 | 265000 | 215000 | 215000 | 265000 | 265000 | 135000 | 135000 | 130000 | 130000 | 425000 | 425000 | 185000 | 185000 | 185000 | 185000
72 | 3.3 | FRAMEWORK FOR FANS
73 |  | Supply, Fabrication and Installation of MS frame using channels angle iron sections as required for mounting of ventilation fans scrubber in areas shown in the layout. The frame work shall be applied with red oxide primer and thereafter, two coats of enamel paint of approved colour. The general arrangement drawing for frame work shall be got approved from the Architects Structural Engineers prior to commencement of fabrication. | Kg | 200 | 50000 | 250 | 50000 | 225 | 45000 | 225 | 45000 | 250 | 50000 | 250 | 50000 | 250 | 50000 | 550 | 110000 | 550 | 110000 | 350 | 70000 | 350 | 70000 | 350 | 70000
74 |  | Note
75 | a. | Fan outlet velocity - 1600 FPM
76 | b. | All cabinet fans should have plenum section.
77 | c. | Fresh air fan if any,should to have 6mm thick synthetic media washable filter with framework.
78 | d. | Contractor shall submit static pressure calculation for all above units to Client Consultant.
79 | e. | Any change in motor HP or coil selection shall be made at no extra cost to client.
80 | f. | Fan efficiency shall be minimum 75%
81 | g. | The cost shall be included liftting shifting of each equipment material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material equipment.
82 | 4 | SHEET METAL WORKS
83 | 4.1 | FACTORY FABRICATED G.I RECTANGULAR DUCT
84 |  | Supply, Fabrication, Testing, and Commissioning of Factory Fabricated GI Sheet Metal 120GSM Rectangular boxed ducting, Plenums, Cowls, Elbows with turning vanes, Splitters, Reducers, Flanges, Collars etc as per IS and Installaton as per SMACNA standards, The complete ducting shall be provided with MS Supports, Rods, Angles, Flanges, Bracing, Rubber Gaskets, Wooden frames, Canvas Connections, etc. as per drawings and specifications.
85 |  | GI Sheet Makes Tata, Jindal, SAIL, Ispat
86 |  | Make Rola Star, Zeco Ductofab
87 | a | 18 Gauge GI Sheet Metal Duct (Above 2251mm Plenum) | Sq.mtr | 10 | 18500 | 1850 | 18500 | 1750 | 17500 | 1650 | 16500 | 1850 | 18500 | 1800 | 18000 | 1850 | 18500 | 3099 | 30990 | 2220 | 22200 | 2150 | 21500 | 2150 | 21500 | 2150 | 21500
88 | b | 20 Gauge GI Sheet Metal Duct (1501-2250mm) For Kitchen Exhaust Works | Sq.mtr | 150 | 247500 | 1650 | 247500 | 1600 | 240000 | 1500 | 225000 | 1650 | 247500 | 1600 | 240000 | 1650 | 247500 | 2750 | 412500 | 1850 | 277500 | 4800 | 720000 | 2800 | 420000 | 2800 | 420000
89 | c | 22 Gauge GI Sheet Metal Duct (751-1500mm) | Sq.mtr | 100 | 145000 | 1450 | 145000 | 1400 | 140000 | 1350 | 135000 | 1450 | 145000 | 1400 | 140000 | 1450 | 145000 | 1780 | 178000 | 1650 | 165000 | 1850 | 185000 | 1850 | 185000 | 1850 | 185000
90 | d | 24 Gauge GI Sheet Metal Duct (0-750mm) | Sq.mtr | 120 | 150000 | 1250 | 150000 | 1200 | 144000 | 1150 | 138000 | 1250 | 150000 | 1250 | 150000 | 1250 | 150000 | 1540 | 184800 | 1750 | 210000 | 1650 | 198000 | 1550 | 186000 | 1550 | 186000
91 | 4.2 | EXTRUDED ALUMINIUM CEILING GRILLES
92 |  | Supply, Installation, Testing and Balancing of Powder coated aluminium supply air grilles complete with removable inner core as per approved shop drawing and specifications. The area of grille can be of any geometrical shape (Square rectangular Linear). The grilles shall be with 15 30 45° deflections as per requirement. The Colour shall be decided and approved by client and architect.
93 |  | Make Cosmos, Air Master System Air
94 |  | Linear Square Rectangular Grille | Sq.mtr | 6 | 46800 | 8500 | 51000 | 8000 | 48000 | 8000 | 48000 | 8750 | 52500 | 8750 | 52500 | 8750 | 52500 | 18500 | 111000 | 17500 | 105000 | 7800 | 46800 | 7800 | 46800 | 7800 | 46800
95 | 4.3 | SS EXHAUST AND FRESH AIR GRILLES
96 |  | SITC of 18G S.S 304 Grills adjustable Double Deflector With S.S Volume Control Dampers. Grills to be of Double Deflection Type for ease of deflection on all sides and to have necessary built in Dampers for adjustable nature.
97 |  | Make Carryaire System Air Dynacraft Air Master
98 | a | Linear Square Rectangular Grille | Sq.mtr | 0.5 | 4250 | 10500 | 5250 | 9500 | 4750 | 9500 | 4750 | 8750 | 4375 | 8750 | 4375 | 8750 | 4375 | 20500 | 10250 | 17500 | 8750 | 8500 | 4250 | 6500 | 3250 | 6500 | 3250
99 | 4.4 | DOOR TRANSFER GRILLE
100 |  | SITC of Aluminium extruded powder coated Door transfer grills.
101 |  | Door transfer grille (Back to Back) | Sq.mtr | 1 | 7500 | 8500 | 8500 | 8000 | 8000 | 8000 | 8000 | 9500 | 9500 | 9500 | 9500 | 9500 | 9500 | 19500 | 19500 | 17500 | 17500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500
102 |  | Make Cosmos, Air Master System Air
103 | 4.5 | MULTI LEAF VOLUME CONTROL DAMPER
104 |  | SITC of opposed blade aerofoil type 1.2 mm thick Anodized Aluminium volume control dampers for ducts shall be provided with concealed gears, plastic operator and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawings and specifications. | Sq.mtr | 2.5 | 23125 | 10500 | 26250 | 9500 | 23750 | 9500 | 23750 | 9250 | 23125 | 9250 | 23125 | 9250 | 23125 | 20500 | 51250 | 17500 | 43750 | 14500 | 36250 | 12000 | 30000 | 12000 | 30000
105 |  | Make Cosmos, Air Master System Air
106 | 4.6 | OPPOSED BLADE DAMPER
107 |  | SITC of Aluminium Opposed blade dampers black powder coated vertical blades type for supply air collar. The damper should be gear operated type. | Sq.mtr | 2 | 9000 | 4500 | 9000 | 4200 | 8400 | 4200 | 8400 | 4650 | 9300 | 4040 | 8080 | 4650 | 9300 | 20500 | 41000 | 16500 | 33000 | 14500 | 29000 | 9500 | 19000 | 9500 | 19000
108 | 4.7 | CANVAS CONNECTION
109 |  | SITC of Flexible connections between mouth piece of Fan and initial piece of ducting with inspection zip. Flexible connections shall be double thickness non-flammable material (Fire retardant type).
110 | a | For VRF Ductable Unit | Nos. | 3 | 9000 | 3000 | 9000 | 2700 | 8100 | 2700 | 8100 | 3450 | 10350 | 3000 | 9000 | 3450 | 10350 | 15500 | 46500 | 11500 | 34500 | 4000 | 12000 | 4000 | 12000 | 4000 | 12000
111 | c | For Kitchen EX FA Fan | Nos. | 4 | 12000 | 3000 | 12000 | 2700 | 10800 | 2700 | 10800 | 3650 | 14600 | 3650 | 14600 | 3650 | 14600 | 15500 | 62000 | 11500 | 46000 | 4500 | 18000 | 4500 | 18000 | 4500 | 18000
112 | 4.8 | CURTAIN TYPE FIRE DAMPER
113 |  | SITC of fire dampers consist of 16G GI frame, 20G GI interlocking blades secured with SS springs, blades outside airstream clamped with fusible link UL-555 listed with melting point 165 225°F, etc; as per the approved shop drawings and specifications.
114 |  | Make Carryaire System Air Dynacraft Air Master
115 | a | Bare fire dampers | Sq.mtr | 1 | 12500 | 12500 | 12500 | 11500 | 11500 | 11500 | 11500 | 16500 | 16500 | 16500 | 16500 | 16500 | 16500 | 35500 | 35500 | 28500 | 28500 | 33500 | 33500 | 19500 | 19500 | 19500 | 19500
116 | b | Fusible link as per specification UL 555 | No | 1 | 1500 | 4500 | 4500 | 2000 | 2000 | 2000 | 2000 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 35500 | 35500 | 28500 | 28500 | 8800 | 8800 | 2850 | 2850 | 2850 | 2850
117 |  | NOTES
118 |  | The ducting support should be as per tender specification and additional supports are to be provided by Contractor as decided by Consultant.
119 |  | Muslin cloth cover for all air outlets during construction.
120 |  | Pressure testing of complete duct work as per DW SMACNA standard.
121 |  | Silicon sealant for longitudinal transverse joints as per specification.
122 |  | Diffusers grilles shall be powder coated as per color approved by Architect.
123 | 5 | THERMAL ACOUSTIC INSULATION
124 | 5.1 | THERMAL INSULATION
125 |  | Supply fixing of Thermal insulation for supply air duct using 19mm thick class O Closed cell nitrile rubber with anti-microbial coating on it. Insulation shall have Thermal conductivity of 0.033 W (m.K) and water vapor permeance of 0.10. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape. The duct shall be stick with recommended adhesive. | Sq.mtr | 100 | 75000 | 750 | 75000 | 700 | 70000 | 650 | 65000 | 950 | 95000 | 910 | 91000 | 950 | 95000 | 1550 | 155000 | 1350 | 135000 | 1450 | 145000 | 1050 | 105000 | 1050 | 105000
126 |  | Make Armaflex K-flex Aerofoam ALP Aeroflex
127 | 5.2 | ACOUSTIC INSULATION
128 |  | Supply fixing acoustic insulation for ducting using Class 1 closed cell elastomeric insulation of 10mm thick Nitrile rubber insulation adhesive, longitudinal transverse joints sealed with adhesive in neat clean manner. Material shall be processed Nitrile Rubber foam with anti-microbial protection. Insulation shall have thermal conductivity of 0.047 W (m.K) and density of 140 - 180 kg m³. | Sq.mtr | 25 | 26250 | 1050 | 26250 | 1000 | 25000 | 850 | 21250 | 1450 | 36250 | 1450 | 36250 | 1450 | 36250 | 1350 | 33750 | 1250 | 31250 | 2550 | 63750 | 1800 | 45000 | 1800 | 45000
129 |  | Make Armaflex K-flex Aerofoam ALP Aeroflex
130 | 5.3 | THERMAL INSULATION FOR KITCHEN EXHAUST DUCTS
131 |  | SITC of 80mm thick Glass Fibre Blanket Insulation material bonded with Thrmosetting Resin, with factory applied laminated aluminium foil of 22 micrns with fibre glass backing. Further, wire mesh along with 7 mil cloth shall be applied on above the insulation with proper adhersive. Nominal density 32 Kg CuM. Thermal conductivity, < 0.033 W m.K at 24 degreeC. All Insuation material and adhesives shall be as per Class I for surface spread and in accordance with BS 476, Class O for non-combustible grade. | Sq.mtr | 150 | 157500 | 1050 | 157500 | 1000 | 150000 | 900 | 135000 | 1250 | 187500 | 1050 | 157500 | 1250 | 187500 | 1650 | 247500 | 1550 | 232500 | 3700 | 555000 | 1800 | 270000 | 1800 | 270000
132 |  | Make Rockwool UP Twiga
133 |  | Note
134 | a. | Insulation work to be coordinated with other agencies and repair to be included by contractor as per site requirement.
135 | b. | Vendors to take care of the installation, if any damages takes place the vendor to repair or replace and hand over to clients in good and acceptable condition.
136 | c. | Thermal insulation shall be internal for Elliptical Expossed ducting.
137 | 6 | ELECTRICAL WORKS
138 | 6.2 | POWER CABLING
139 |  | Supply, handling, laying effecting proper connections testing and commissioning of following sizes of 1.1 KV grade XLPE insulated FRLS Aluminium Copper conductor cables laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with Copper earthing as specified for continuous earthing along with cable. All complete as required and as per final instruction as given by Owners Consultants and as per Technical specifications. Earthing shall be measured separately and shall be connected in two runs. Power to ELCB to be provided near each ODU by electrical contractor.
140 | a | Suitable Power Cable
141 |  | Suitable for 6600 CFM Kitchen Exhaust Fan, Star Delta Panel with VFD | Rmt | 10 | 0 | 550 | 5500 | 450 | 4500 | 450 | 4500 | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 7500 | 750 | 7500 | 0 | 0 | 800 | 8000 | 800 | 8000
142 |  | Suitable for 5600 CFM Kitchen Air-washer, Star Delta Panel with VFD | Rmt | 10 | 0 | 550 | 5500 | 450 | 4500 | 450 | 4500 | 450 | 4500 | 450 | 4500 | 450 | 4500 | 750 | 7500 | 750 | 7500 | 0 | 0 | 800 | 8000 | 800 | 8000
143 | b | Earthing
144 |  | 8 SWG | Rmt | 40 | 0 | 150 | 6000 | 140 | 5600 | 140 | 5600 | 450 | 18000 | 450 | 18000 | 450 | 18000 | 850 | 34000 | 750 | 30000 | 0 | 0 | 225 | 9000 | 225 | 9000
145 | 6.3 | CABLE TERMINATION
146 |  | Supply Making of Cable termination of armoured unarmoured cables 1.1 KV grade including installation of cable glands, cable lugs (Aluminium for A2XFY copper for 2XFY YY Double compression type), heat shrinkable sleeves on long ends, crimping paste etc. The work includes testing commissioning of cables, meggaring values submitting reports of tests. (One set includes termination of all cores of one end only). All crimping tools dies shall be arranged by contractor.
147 | a | Suitable for 6600 CFM Kitchen Exhaust Fan, Star Delta Panel with VFD | Nos. | 2 | 0 | 500 | 1000 | 450 | 900 | 350 | 700 | 2500 | 5000 | 2000 | 4000 | 2500 | 5000 | 15500 | 31000 | 38500 | 77000 | 0 | 0 | 650 | 1300 | 650 | 1300
148 | b | Suitable for 5600 CFM Kitchen Air-washer, Star Delta Panel with VFD | Nos. | 2 | 0 | 500 | 1000 | 450 | 900 | 350 | 700 | 2500 | 5000 | 2000 | 4000 | 2500 | 5000 | 16500 | 33000 | 38500 | 77000 | 0 | 0 | 650 | 1300 | 650 | 1300
149 | 6.4 | CABLE TRAYS
150 |  | Supplying Fixing of following sizes of GI cable tray duly painted perforated type of height 50mm along with necessary bends, reducers etc. anchored along the wall suspended from the ceiling with necessary MS supports.
151 | a | 50mm wide x 50mm ht x 1.6mm thick | Rmt | 20 | 9000 | 550 | 11000 | 550 | 11000 | 450 | 9000 | 450 | 9000 | 450 | 9000 | 450 | 9000 | 1250 | 25000 | 1550 | 31000 | 2200 | 44000 | 13500 | 270000 | 13500 | 270000
3 |  | Fire Sprinkler | NOS | 1 |  |  | 218750 |  | 181155 |  | 181155 |  | 226650 |  | 214500 |  | 210650 |  | 262445 |  | 191741 |  | 303700 |  | 217450 |  | 185000
152 | 1 | Providing, laying, jointing, testing and commissioning of G.I. `C Class pipes (IS 1239 (Part-I)-1979) including cutting,threading welding etc providing all malleable galvanized iron fittings conforming to IS 1879, viz. Flanges, bends, tees, elbows,reducers, unions, supporting with G. I. clamps, hangers, M.S. brackets etc. including cutting holes and chases in brick or RCC wall slabs and making good the same to the Approval of Architect consultant,complete including painting with one coat of primer and two or more coats of synthetic enamel paint of approved make and shade.
153 | i) | 25 mm dia. | RMT | 25 | 18750 | 750 | 18750 | 700 | 17500 | 700 | 17500 | 850 | 21250 | 750 | 18750 | 850 | 21250 | 1300 | 32500 | 980 | 24500 | 1850 | 46250 | 980 | 24500 | 980 | 24500
154 | ii) | 32 mm dia. | RMT | 5 | 4750 | 950 | 4750 | 900 | 4500 | 900 | 4500 | 1050 | 5250 | 950 | 4750 | 1050 | 5250 | 1425 | 7125 | 1080 | 5400 | 2000 | 10000 | 1150 | 5750 | 1150 | 5750
155 | iii) | 40 mm dia. | RMT | 15 | 15750 | 1050 | 15750 | 1000 | 15000 | 1000 | 15000 | 1250 | 18750 | 1050 | 15750 | 1250 | 18750 | 1575 | 23625 | 1400 | 21000 | 2170 | 32550 | 1250 | 18750 | 1250 | 18750
156 | iv) | 50 mm dia. | RMT | 20 | 25000 | 1250 | 25000 | 1200 | 24000 | 1200 | 24000 | 1450 | 29000 | 1250 | 25000 | 1450 | 29000 | 1690 | 33800 | 1550 | 31000 | 2250 | 45000 | 1450 | 29000 | 1450 | 29000
157 | v) | 65 mm dia. | RMT | 5 | 7250 | 1450 | 7250 | 1350 | 6750 | 1350 | 6750 | 1650 | 8250 | 1450 | 7250 | 1650 | 8250 | 1950 | 9750 | 1750 | 8750 | 2450 | 12250 | 1550 | 7750 | 1550 | 7750
158 | vi) | 80 mm dia. | RMT | 5 | 8250 | 1650 | 8250 | 1500 | 7500 | 1500 | 7500 | 1850 | 9250 | 1850 | 9250 | 1850 | 9250 | 2125 | 10625 | 1900 | 9500 | 2650 | 13250 | 1850 | 9250 | 1850 | 9250
159 | vii) | 100 mm dia. | RMT | 5 | 9250 | 1850 | 9250 | 1750 | 8750 | 1750 | 8750 | 2050 | 10250 | 2050 | 10250 | 2050 | 10250 | 2950 | 14750 | 2500 | 12500 | 2980 | 14900 | 2110 | 10550 | 2110 | 10550
160 | 2 | Providing , fixing testing and commissioning of pendant type sprinkler heads 68 deg. Temp (Quick response type) | No. | 5 | 5250 | 1650 | 8250 | 1250 | 6250 | 1250 | 6250 | 1050 | 5250 | 1050 | 5250 | 1050 | 5250 | 1950 | 9750 | 1750 | 8750 | 1050 | 5250 | 1050 | 5250 | 1050 | 5250
161 | 3 | Providing , fixing testing and commissioning of concealed type sprinkler heads 68 deg. Temp.(Quick response type) | No. | 10 | 13000 | 2250 | 22500 | 1850 | 18500 | 1850 | 18500 | 2250 | 22500 | 2250 | 22500 | 2250 | 22500 | 1950 | 19500 | 1750 | 17500 | 1300 | 13000 | 1300 | 13000 | 1300 | 13000
162 | 4 | Providing , fixing testing and commissioning of upright type sprinkler heads 68 deg. (Quick response type) | No. | 23 | 25300 | 1450 | 33350 | 1000 | 23000 | 1000 | 23000 | 1150 | 26450 | 1100 | 25300 | 1150 | 26450 | 1890 | 43470 | 1770 | 40710 | 1100 | 25300 | 1100 | 25300 | 1100 | 25300
163 | 5 | Providing , fixing testing and commissioning of pendent type sprinkler heads 79 deg. Temp including (Quick response type) | No. | 9 | 9450 | 1650 | 14850 | 1250 | 11250 | 1250 | 11250 | 1050 | 9450 | 1050 | 9450 | 1050 | 9450 | 2250 | 20250 | 1859 | 16731 | 1450 | 13050 | 1450 | 13050 | 1450 | 13050
164 | 6 | Providing fixing testing and commissioning of UL Rated SS braided Flexible pipe (Prior to order please check condition of existing droppers)
165 | i) | 1Mt Ht | No. | 2 | 3700 | 2250 | 4500 | 1850 | 3700 | 1850 | 3700 | 1850 | 3700 | 1850 | 3700 | 1850 | 3700 | 1900 | 3800 | 1800 | 3600 | 2350 | 4700 | 2100 | 4200 | 2100 | 4200
166 | ii) | 1.6Mt Ht | No. | 7 | 14700 | 3050 | 21350 | 2250 | 15750 | 2250 | 15750 | 2450 | 17150 | 2450 | 17150 | 2450 | 17150 | 2100 | 14700 | 1900 | 13300 | 3100 | 21700 | 2800 | 19600 | 2800 | 19600
167 | 7 | Gun metal chrome finished Ball valves (PN 16) with fittings of screwedend type.
168 | I) | 32 mm dia. (Sprinkler drain-OPTIONAL) | Nos. | 1 | 2450 | 2450 | 2450 | 2205 | 2205 | 2205 | 2205 | 3650 | 3650 | 3650 | 3650 | 3650 | 3650 | 3800 | 3800 | 3500 | 3500 | 13000 | 13000 | 13000 | 13000 | 13000 | 13000
169 | 8 | Wheel operated Butterfly Valves (PN 16) with inbuilt supervisory switch (UL listed and FM approved) with CI Body, Black Nitrile Body Liner and Nylon Coated SG Iron Disc with material and labour including hydraulic testing etc. complete as per drawing, specification to the level of satisfaction of Site- Incharge.
170 | I) | 80 mm dia. | No. | 1 | 15000 | 22500 | 22500 | 16500 | 16500 | 16500 | 16500 | 36500 | 36500 | 36500 | 36500 | 36500 | 36500 | 15000 | 15000 | 15000 | 15000 | 33500 | 33500 | 18500 | 18500 | 18500 | 18500
4 |  | FAS | NOS | 1 |  |  | 147650 |  | 124000 |  | 124000 |  | 170534 |  | 171134 |  | 171134 |  | 181850 |  | 114650 |  | 432000 |  | 178200 |  | 132000
171 | 13.1.1 | Fire alarm Addressable control panel (1 Loop)
172 | 13.3.3 | Supply,Installation,Testing Commissioning of Horn Strobe rated at 82 dBA @ 3m for Audible annunciation and 75cd flashing at 1 Hz for visual indication with Control modules and necessary accessories including back box. | Nos | 2 | 12400 | 6200 | 12400 | 5650 | 11300 | 5650 | 11300 | 7656 | 15312 | 7656 | 15312 | 7656 | 15312 | 9000 | 18000 | 8000 | 16000 | 8000 | 16000 | 8000 | 16000 | 8000 | 16000
173 | 13.3.4 | Supply, Installation,Testing Commissioning of Analogue Addressable Flash scan Type Photoelectric smoke detectors( Below False Ceiling) having Rotary, decimal addressing system with standard base, built in isolation function and junction box. The detector shall be capable to address in the range of 1-159. The detector shall be with Visible bi-color LEDs for 360 deg viewing and shall blink green every time the detector is addressed, and illuminate steady red on alarm. | Nos | 5 | 26250 | 6200 | 31000 | 5200 | 26000 | 5200 | 26000 | 5250 | 26250 | 5250 | 26250 | 5250 | 26250 | 6000 | 30000 | 5500 | 27500 | 7500 | 37500 | 7500 | 37500 | 7500 | 37500
174 | 13.3.7 | Supply,Installation,Testing Commissioning of Analogue Addressable Flash scan Type Heat Detector having Rotary, decimal addressing system with standard base, built in isolation function and junction box. The detector shall be capable to address in the range of 1-159. The detector shall be with Visible bi-color LEDs for 360 deg viewing and shall blink green every time the detector is addressed, and illuminate steady red on alarm. (Make- Edward-EST-SIGA-HFS) | Nos | 4 | 20200 | 6400 | 25600 | 5200 | 20800 | 5200 | 20800 | 5050 | 20200 | 5050 | 20200 | 5050 | 20200 | 6750 | 27000 | 5500 | 22000 | 8000 | 32000 | 6800 | 27200 | 6800 | 27200
175 | 13.3.9 | Supply,Installation,Testing Commissioning of Addressable Break Glass Manual Call Point having Rotary, decimal addressing system and having an integrally mounted addressable module that monitors and reports contact status. | Nos | 2 | 12000 | 6000 | 12000 | 5400 | 10800 | 5400 | 10800 | 7850 | 15700 | 7850 | 15700 | 7850 | 15700 | 6850 | 13700 | 5600 | 11200 | 7000 | 14000 | 7000 | 14000 | 7000 | 14000
176 | 13.4 | SITC of Fault Isolator. | Nos | 1 | 5500 | 6200 | 6200 | 5000 | 5000 | 5000 | 5000 | 7522 | 7522 | 7522 | 7522 | 7522 | 7522 | 8500 | 8500 | 7500 | 7500 | 5500 | 5500 | 7000 | 7000 | 7000 | 7000
177 | 13.5 | SITC of 2Cx1.5sq.mm multistranded FRLS Cu. Armoured for RED Colour,Mylan Shielded Screened cable For SLC. | Mtrs | 120 | 17400 | 160 | 19200 | 135 | 16200 | 135 | 16200 | 140 | 16800 | 145 | 17400 | 145 | 17400 | 270 | 32400 | 260 | 31200 | 350 | 42000 | 200 | 24000 | 200 | 24000
178 | 13.6 | Response indicator. | Nos | 5 | 1250 | 550 | 2750 | 350 | 1750 | 350 | 1750 | 250 | 1250 | 250 | 1250 | 250 | 1250 | 850 | 4250 | 750 | 3750 | 2500 | 12500 | 550 | 2750 | 550 | 2750
179 | 13.7 | Supply Installation of CAT-6 Cable(DIAL FAS PANEL TO RFPA PANEL) | Mtr. | 150 | 13500 | 90 | 13500 | 81 | 12150 | 81 | 12150 | 150 | 22500 | 150 | 22500 | 150 | 22500 | 180 | 27000 | 170 | 25500 | 1650 | 247500 | 165 | 24750 | 165 | 24750
180 | 13.8 | Programing Charges to Paid Airport Vendor | No | 1 | 21000 | 25000 | 25000 | 20000 | 20000 | 20000 | 20000 | 45000 | 45000 | 45000 | 45000 | 45000 | 45000 | 21000 | 21000 | 20000 | 20000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000

## Technical Score Detail
|  | RFQ No: R2174 COST COMPARISON REPORT | RFQ No: R2174 COST COMPARISON REPORT | RFQ No: R2174 COST COMPARISON REPORT | Comp. Date : 13/11/2024 | Comp. Date : 13/11/2024 | Comp. Date : 13/11/2024 | Vendor Name : PIONEER PROJECT SOLUTION |  | Vendor Name : ANJLE MEP PROJECT PVT LTD |  | Vendor Name : CRYSTAL AIRCOOL |  | Vendor Name : Mahamaya Engineering
|  | RFQ No: R2174 COST COMPARISON REPORT | RFQ No: R2174 COST COMPARISON REPORT | RFQ No: R2174 COST COMPARISON REPORT | RFQ #: R2174 | RFQ #: R2174 | RFQ #: R2174 | Contact Name : Mohd Ashraf |  | Contact Name : PREMKANT |  | Contact Name : JOHN |  | Contact Name : Yash Katoch
|  | RFQ No: R2174 COST COMPARISON REPORT | RFQ No: R2174 COST COMPARISON REPORT | RFQ No: R2174 COST COMPARISON REPORT | RFQ Date : 07/11/2024 17:00:07 | RFQ Date : 07/11/2024 17:00:07 | RFQ Date : 07/11/2024 17:00:07 | Vendor City : |  | Vendor City : |  | Vendor City : |  | Vendor City : delhi
|  | RFQ No: R2174 COST COMPARISON REPORT | RFQ No: R2174 COST COMPARISON REPORT | RFQ No: R2174 COST COMPARISON REPORT | BCD Date : 14/11/2024 23:55:00 | BCD Date : 14/11/2024 23:55:00 | BCD Date : 14/11/2024 23:55:00 | Telephone # : |  | Telephone # : |  | Telephone # : |  | Telephone # : 9810360460
|  | RFQ No: R2174 COST COMPARISON REPORT | RFQ No: R2174 COST COMPARISON REPORT | RFQ No: R2174 COST COMPARISON REPORT |  |  |  | Mobile # : |  | Mobile # : |  | Mobile # : |  | Mobile # : 9810360460
PR Number : TFSPL-2425-00916,TFSPL-2425-00917,TFSPL-2425-00920 | PR Number : TFSPL-2425-00916,TFSPL-2425-00917,TFSPL-2425-00920 | PR Number : TFSPL-2425-00916,TFSPL-2425-00917,TFSPL-2425-00920 | PR Number : TFSPL-2425-00916,TFSPL-2425-00917,TFSPL-2425-00920 | PR Number : TFSPL-2425-00916,TFSPL-2425-00917,TFSPL-2425-00920 | PR Number : TFSPL-2425-00916,TFSPL-2425-00917,TFSPL-2425-00920 | PR Number : TFSPL-2425-00916,TFSPL-2425-00917,TFSPL-2425-00920 | PR Number : TFSPL-2425-00916,TFSPL-2425-00917,TFSPL-2425-00920 | Email : projectspioneer@gmail.com |  | Email : anjlemepprojects@gmail.com |  | Email : crystalhvac002@gmail.com |  | Email : mahamaya.engineering1@gmail.com
Package / RFQ Name : PR for HVAC, Fire & FAS for DEL NANDOS T3 INT | Package / RFQ Name : PR for HVAC, Fire & FAS for DEL NANDOS T3 INT | Package / RFQ Name : PR for HVAC, Fire & FAS for DEL NANDOS T3 INT | Package / RFQ Name : PR for HVAC, Fire & FAS for DEL NANDOS T3 INT | Package / RFQ Name : PR for HVAC, Fire & FAS for DEL NANDOS T3 INT | Package / RFQ Name : PR for HVAC, Fire & FAS for DEL NANDOS T3 INT | Package / RFQ Name : PR for HVAC, Fire & FAS for DEL NANDOS T3 INT | Package / RFQ Name : PR for HVAC, Fire & FAS for DEL NANDOS T3 INT | Round # : 2 (RFQ) |  | Round # : 2 (RFQ) |  | Round # : 2 (RFQ) |  | Round # : 2 (RFQ)
Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Buyer : Pushpak Mahesh Shewale | Quotation Date : |  | Quotation Date : |  | Quotation Date : |  | Quotation Date :
Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Currency :INR | Currency :INR | Currency :INR | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date :
Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | Comp. # : 2 | BUDGET PRICE : | .00 |  | Quote Currency : |  | Quote Currency : |  | Quote Currency : |  | Quote Currency :
# | Item Code | Item Description | Last PO Details | Unit | Qty | Last PO Unit Rate | Last PO Total Value | Score | Justification | Score | Justification | Score | Justification | Score | Justification
1 |  | HVAC- high side |  | NOS | 1.000 | 0.00 | 0.00
2 |  | Prices shall be based on supply, installation, testing commissioning (SITC) at site including all taxes, duties, transportation insurance etc. |  |  | 0.000 | 0.00 | 0.00
3 | 1 | VRF SYSTEMS VRF OUTDOOR UNITS Supply of air cooled variable refrigerant flow modular type condensing units, each comprising of multiple scroll compressors all inverter driven, full charge of refrigerant gas (R-410a), lubricating oil and all accessories as per the specifications. The condensing units shall be suitable to work on heating cooling mode. The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B . The COP of the system shall be greater than 4 under ARI conditions for 100% load . The condensing units shall be suitable for operation on 415 ± 10% volts, 50Hz, 3 phase AC power supply. VRF unit shall be supplied with operating panel for operation control. ODU to have standard factory coated treatment for heat rust corrosion for Condenser coil, panels, motor, electricals heat exchanger, Power Cabling etc. The condensing units shall be of following capacities Refrigeration Capacities indicated below are actual capacity. Selection to be done considering referigerant piping length and derating at @ 40°C. Vendor has to submit highlight if capacity of the unit exceed diversity factor after derating for 40°C ambient conditions. Any alteration in capacity after bidding will not be entertain. Vendor has to provide unit to meet the refrigeration requirement. Make Daikin, Toshiba, Mitsubishi Refrigeration Capacity - 14 HP |  | Nos | 1.000 | 0.00 | 0.00
4 | 2.1 | VRF INDOOR UNITS Supply,Installation,Testing and Commissioning of variable refrigerant flow modular type indoor units Corded Cordless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling as well as heating mode. The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 ±6% volts, 50Hz, 1 phase AC power supply. Ductable indoor units shall be suitable to handle extent of ductwork as shown in the design drawings and dehumidified air quantity as mentioned below. The indoor unit shall be complete with pre filter remote as per requirement. Unit shall be quoted with T-Tube flange connection kit for for higher fresh air intake. Except Hi-wall unit, all other units shall have port for fresh air intake and inbuilt drain pump. The indoor units shall be of following capacities . HIGH STATIC DUCTABLE TYPE INDOOR UNIT with CORDED REMOTE CONTROLLER Indoor Temperature NMT 22°C 2542 CFM 6.4 TR |  | Nos. | 2.000 | 0.00 | 0.00
5 | 2.2 | CEILING MOUNTED TYPE COMPACT CASSETTE UNIT with CORDLESS REMOTE CONTROLLER Indoor Temperature NMT 22°C 318 CFM 0.6 TR |  | Nos. | 1.000 | 0.00 | 0.00
6 | 3 | CENTRALISED REMOTE CONTROLLER Supply of the Graphic central remote Controller (Touch Screen Type) . It must act as an advanced air conditioning management system to facilitate complete control of VRF air conditioning equipment. It should be user friendly through its touch screen, icon display and color LCD display. Integratable upto 64 remote controller groups (including AHUs TFAs) and BMS compatible with ethernet Wi-Fi communication protocol for remote monitoring. In addition to basic controls such as settings for on stop, the operation mode temperature, the air quantity and auto louver can be set. If a problem occurs, an alarm code immediately shows the details of the problem. An external input terminal is provided as standard. External signals enable the following function central operation stop, demand control, emergency stop, central operation output, central alarm output. Controller shall however be suitable for future connectivity of indoor outdoor units also. Central Remote Controller |  | Nos. | 1.000 | 0.00 | 0.00
7 |  | GENERAL NOTES The cost shall be included liftting shifting of each equipment material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material equipment. |  |  | 0.000 | 0.00 | 0.00
8 |  | Hvac - low side |  | NOS | 1.000 | 0.00 | 0.00
9 | 2 | INDIGENOUS WORK |  |  | 0.000 | 0.00 | 0.00
10 | 2.1 | INSTALLATION OF VRF OUT-DOOR UNITS |  |  | 0.000 | 0.00 | 0.00
11 |  | Installation, Charging, Testing and commissioning of VRF system with Environment friendly refrigerant gas for the below mentioned system. This shall include lifting, shifting and positioning of outdoor units, nitrogen leak testing, oil charging, vaccumisation etc., |  |  | 0.000 | 0.00 | 0.00
12 | a | Refrigeration Capacity - 14 HP |  | Nos. | 1.000 | 0.00 | 0.00
13 | 2.2 | INSTALLATION OF VRF INDOOR UNITS |  |  | 0.000 | 0.00 | 0.00
14 |  | Installation, Charging, Testing and commissioning of units complete with centrifugal blower, cooling coil with suitable rows, electronic expansion valves, high efficiency pre filter sections, drain pump etc as per specifications. |  |  | 0.000 | 0.00 | 0.00
15 | 0 | 2542 CFM 6.4 TR |  | Nos. | 2.000 | 0.00 | 0.00
16 | 0 | 318 CFM 0.6 TR |  | Nos. | 1.000 | 0.00 | 0.00
17 | 2.3 | INSTALLATION OF CENTRALISED REMOTE CONTROLLER |  |  | 0.000 | 0.00 | 0.00
18 |  | Installation, Charging, Testing and commissioning of of the Graphic central remote Controller (Touch Screen Type) . It must act as an advanced air conditioning management system to facilitate complete control of VRF air conditioning equipment. It should be user friendly through its touch screen, icon display and color LCD display. Integratable upto 64 remote controller groups (including AHUs TFAs) and BMS compatible with ethernet Wi-Fi communication protocol for remote monitoring. In addition to basic controls such as settings for on stop, the operation mode temperature, the air quantity and auto louver can be set. If a problem occurs, an alarm code immediately shows the details of the problem. An external input terminal is provided as standard. External signals enable the following function central operation stop, demand control, emergency stop, central operation output, central alarm output. Controller shall however be suitable for future connectivity of indoor outdoor units also. |  |  | 0.000 | 0.00 | 0.00
19 | a | Central Remote Controller |  | Nos. | 1.000 | 0.00 | 0.00
20 | 2.4 | VRF REFRIGERANT PIPING FITTING WITH INSULATION |  |  | 0.000 | 0.00 | 0.00
21 |  | Supply, Installation, Testing and Commissioning of the refrigerant piping with nitrile rubber insulation in sleeve form.It should be selected for maximum working pressure of 624 psi for R – 410a refrigerant circuit and for maximum working pressure of 500psi in case of R407C refrigerant. The Ref. Piping shall be pressure tested at 1.5 times the working pressure. Copper pipes shall be made of phosphorus deoxidized seamless copper. Minimum thickness to be used for refrigerant piping shall be as follows The insulation( Nitrile rubber, class-O, self extinguishing, CFC free, thermal conductivity of not more than .035w Wm°K shall be 19 mm thick for suction piping liquid line. All Exposed Piping on the floor shall be enclosed in openable GI trays insulation should be with UV protection with mil cloth.The Ref. Piping shall be properly supported at every 1.5 m distance with stands and support linked with rubber as per specifications. |  | Rmt | 75.000 | 0.00 | 0.00
22 |  | Make Maxflow Mandev Heling |  |  | 0.000 | 0.00 | 0.00
23 |  | Note Referiferant piping shall include liquid + gas pipe with all necessory fittings. Also, the size of the same shall be as per manufactured standard. |  |  | 0.000 | 0.00 | 0.00
24 | 2.5 | GAS CHARGING |  |  | 0.000 | 0.00 | 0.00
25 |  | Additional gas charging - Over and above standard Gas charging quantity |  | Kg | 15.000 | 0.00 | 0.00
26 | 2.6 | REFNET JOINTS |  |  | 0.000 | 0.00 | 0.00
27 |  | SITC of Special Refrigerant T Y-joints for VRF units |  | Nos | 2.000 | 0.00 | 0.00
28 | 2.7 | POWER CABLING |  |  | 0.000 | 0.00 | 0.00
29 |  | Supply, handling, laying effecting proper connections testing and commissioning of following sizes of 1.1 KV grade XLPE insulated FRLS Aluminium Copper conductor cables laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with Copper earthing as specified for continuous earthing along with cable. (Earthing will be measured separately and need not be quoted under this item). All complete as required and as per final instruction as given by Owners Consultants. (MCCB,s provided 5m from Outdoor unit). |  |  | 0.000 | 0.00 | 0.00
30 |  | Make Polycab, KEI Finolex |  |  | 0.000 | 0.00 | 0.00
31 | b | Suitable copper Armoured cable - from MCB Isolator to VRF ODU. |  | Rmt | 5.000 | 0.00 | 0.00
32 | d | 8 SWG Copper Wire |  | Rmt | 10.000 | 0.00 | 0.00
33 | 2.8 | COMMUNICATION CABLE |  |  | 0.000 | 0.00 | 0.00
34 |  | SITC of the control cabling from Indoor to outdoor unit Outdoor unit to CRC BACnet for all the units with the necessary fittings. The cabling shall be of weather proof type as most of the cabling will have open exposure to atmosphere. The cabling shall be bundled properly and shall be neatly aligned with the Refrigerant piping. The cabling shall be well supported with G.I cable tray throughout the piping length. |  |  | 0.000 | 0.00 | 0.00
35 |  | Make Polycab, KEI Finolex |  |  | 0.000 | 0.00 | 0.00
36 | a | 1.5 sqmm 2 core |  | Rmt | 135.000 | 0.00 | 0.00
37 | 2.9 | PERFORATED GI CABLE TRAYS |  |  | 0.000 | 0.00 | 0.00
38 |  | Supplying Fixing of following sizes of Perforated GI cable tray duly painted of height 50mm along with necessary bends, reducers etc. anchored along the wall suspended from the ceiling with necessary MS supports. External Internal refrigerant piping shall be provided and laid on GI covered cable trays with cover. |  |  | 0.000 | 0.00 | 0.00
39 | a | 150mm wide |  | Rmt | 25.000 | 0.00 | 0.00
40 | b | 300mm wide |  | Rmt | 50.000 | 0.00 | 0.00
41 | 2.10 | FRAMEWORK FOR VRF ODU |  |  | 0.000 | 0.00 | 0.00
42 |  | Supply, Fabrication and Installation of MS frame using channels angle iron sections as required for mounting of air cooled remote condenser in service areas or terrace level. The frame work shall be applied with red oxide primer and thereafter, two coats of enamel paint of approved colour. The general arrangement drawing for frame work shall be got approved from the Architects Structural Engineers prior to commencement of fabrication. |  | Nos. | 1.000 | 0.00 | 0.00
43 | 2.11 | INSULATED CONDENSATE DRAIN PIPE |  |  | 0.000 | 0.00 | 0.00
44 |  | SITC of UPVC pipes of following sizes for drain with necessary supports and fittings such as elbows, tees reducers etc. The insulation line to be insulated with nitrile rubber insulation of thickness 9mm and wrapped by weather proof protection tape. The Pipe wherever concealed should also have a parallel line as a standby arrangement in case of block of primary pipe . |  |  | 0.000 | 0.00 | 0.00
45 |  | Make Supreme, Prince, Astral |  |  | 0.000 | 0.00 | 0.00
46 | a | 25 mm Dia |  | Rmt | 30.000 | 0.00 | 0.00
47 | b | 32 mm Dia |  | Rmt | 20.000 | 0.00 | 0.00
48 | 2.12 | Supply, installation of Cowl piece connection with bird screen for VRF Outdoor units |  | Nos | 1.000 | 0.00 | 0.00
49 | Note : | Quantities of refrigerant piping and cabling are based on the drawings with Indoor Outdoor units Locations shown and for the specified configuration. Vendor to confirm refrigerant piping and cabling quantities based on the system configuration being offered by them. |  |  | 0.000 | 0.00 | 0.00
50 | 3 | VENTILATION SYSTEM |  |  | 0.000 | 0.00 | 0.00
51 | 3.1 | KITCHEN EXHAUST FAN |  |  | 0.000 | 0.00 | 0.00
52 |  | SITC of Cabinet type SISW Centrifugal Blower, Belt Direct Drive, Statically Dynamically Balanced, Backward Curved Impeller fan, Dunlop Anti- Vibration Pads etc. Motor should be outside stream with TEFC squirrel cage, weather protection shield, IP 55 rating with Class H Insulation, suitable for 3phase, 415volts, 50hz power supply. Sound level should be 65dB @ 3mtr distance. The quote shall include with MS frame, starter panel along with its required cable. Supplied with Dunlop Anti- Vibration Pads Canvass Connection. Fan shall be BMS compatible. Power will be provided 5 ft away from fan and necessary control wiring with plug will be provided by AC contractor.(Vendor to crosscheck static pressure calculation). |  |  | 0.000 | 0.00 | 0.00
53 |  | Make Kruger Nicotra Avantec |  |  | 0.000 | 0.00 | 0.00
54 | a | 6600 CFM, 65mm ESP (Class H) |  | Nos. | 1.000 | 0.00 | 0.00
55 | 3.2 | KITCHEN DRY SCRUBBER |  |  | 0.000 | 0.00 | 0.00
56 |  | SITC of Dry scrubber – Electrostatic Air cleaner with starter panel as per specifications, suitable for following capacities, including electrical starter panel . The Air filtration efficiency should be between 90 to 95% units shall be staked one above other or side by side as per site requirement, if vendor will propose multiple units. |  |  | 0.000 | 0.00 | 0.00
57 |  | Finishing - Power coated, Dark Blue |  |  | 0.000 | 0.00 | 0.00
58 |  | Operating voltage - 220 Vac+ -10%, 50 Hz (Single phase) |  |  | 0.000 | 0.00 | 0.00
59 |  | Features - Short circuit, arc protection and auto restore power supply, BMS (Building Management System) terminals provided, Auto power cut-off when door is opened, Indicator LEDs for normal or wash indicator, Set of Terminals for remote LED normal or wash indicator |  |  | 0.000 | 0.00 | 0.00
60 |  | Efficiency - Upto 95%, meets NIOSH 5026 Oil Mist Test |  |  | 0.000 | 0.00 | 0.00
61 |  | Particle Size - Collects particles as small as 0.01 microns |  |  | 0.000 | 0.00 | 0.00
62 |  | Motor - Sealead ball bearings UL, single phase. |  |  | 0.000 | 0.00 | 0.00
63 |  | Cell - Ionizing voltage - 12 KVdc |  |  | 0.000 | 0.00 | 0.00
64 |  | Collector voltage - 6 KVdc |  |  | 0.000 | 0.00 | 0.00
65 |  | One cell comprising of 9 ionizing wires and 25 collection plates |  |  | 0.000 | 0.00 | 0.00
66 |  | Controls - Auto cut-off when door is opened. Indicator lights for fault, normal or wash function. |  |  | 0.000 | 0.00 | 0.00
67 |  | Pre-filter - Aluminium mesh, washable Dry contact for BMS. |  |  | 0.000 | 0.00 | 0.00
68 |  | Make Rydair Espair |  |  | 0.000 | 0.00 | 0.00
69 |  | CFM - 6600 |  | Nos. | 1.000 | 0.00 | 0.00
70 | 3.2 | KITCHEN FRESH AIR FAN WITH AIRWASHER TYPE |  |  | 0.000 | 0.00 | 0.00
71 |  | SITC of CELDEK FILL package type air cooling unit with minimum 90% saturation efficiency. Air cooling unit shall be factory assembled and complete with double skin casing 0.8mm Inner outer pre-coated GI sheets, DIDW forward curved fans with TEFC, sq. cage, induction motors 1440 RPM (IE-3) with IP-55 Protection. Suitable for operation on 415 ± 10% voltage, 50 Hz 3 phase AC supply, drive package including multi sheave pulleys and belts for fans and motors, 1.2mm thick tank pad section in SS Construction, vibration isolators, wire mesh pre-filters, 200 mm thick CELDEK FILL, 1HP Water Circulation Pump (1W+1S), internal PVC piping, valves and fittings, 4-bend PVC eliminator. MERV 8 G4 pleated pre-filters should be made of 100% synthetic media to capture common airborne contaminants as per ASHRAE Standard 52.2. (Vendor to crosscheck static pressure calculation) |  |  | 0.000 | 0.00 | 0.00
72 |  | Make Kruger Nicotra Avantec |  |  | 0.000 | 0.00 | 0.00
73 | a | 5600 CFM, 50mm ESP (Class F) |  | Nos. | 1.000 | 0.00 | 0.00
74 | 3.3 | FRAMEWORK FOR FANS |  |  | 0.000 | 0.00 | 0.00
75 |  | Supply, Fabrication and Installation of MS frame using channels angle iron sections as required for mounting of ventilation fans scrubber in areas shown in the layout. The frame work shall be applied with red oxide primer and thereafter, two coats of enamel paint of approved colour. The general arrangement drawing for frame work shall be got approved from the Architects Structural Engineers prior to commencement of fabrication. |  | Kg | 200.000 | 0.00 | 0.00
76 |  | Note |  |  | 0.000 | 0.00 | 0.00
77 | a. | Fan outlet velocity - 1600 FPM |  |  | 0.000 | 0.00 | 0.00
78 | b. | All cabinet fans should have plenum section. |  |  | 0.000 | 0.00 | 0.00
79 | c. | Fresh air fan if any,should to have 6mm thick synthetic media washable filter with framework. |  |  | 0.000 | 0.00 | 0.00
80 | d. | Contractor shall submit static pressure calculation for all above units to Client Consultant. |  |  | 0.000 | 0.00 | 0.00
81 | e. | Any change in motor HP or coil selection shall be made at no extra cost to client. |  |  | 0.000 | 0.00 | 0.00
82 | f. | Fan efficiency shall be minimum 75% |  |  | 0.000 | 0.00 | 0.00
83 | g. | The cost shall be included liftting shifting of each equipment material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material equipment. |  |  | 0.000 | 0.00 | 0.00
84 | 4 | SHEET METAL WORKS |  |  | 0.000 | 0.00 | 0.00
85 | 4.1 | FACTORY FABRICATED G.I RECTANGULAR DUCT |  |  | 0.000 | 0.00 | 0.00
86 |  | Supply, Fabrication, Testing, and Commissioning of Factory Fabricated GI Sheet Metal 120GSM Rectangular boxed ducting, Plenums, Cowls, Elbows with turning vanes, Splitters, Reducers, Flanges, Collars etc as per IS and Installaton as per SMACNA standards, The complete ducting shall be provided with MS Supports, Rods, Angles, Flanges, Bracing, Rubber Gaskets, Wooden frames, Canvas Connections, etc. as per drawings and specifications. |  |  | 0.000 | 0.00 | 0.00
87 |  | GI Sheet Makes Tata, Jindal, SAIL, Ispat |  |  | 0.000 | 0.00 | 0.00
88 |  | Make Rola Star, Zeco Ductofab |  |  | 0.000 | 0.00 | 0.00
89 | a | 18 Gauge GI Sheet Metal Duct (Above 2251mm Plenum) |  | Sq.mtr | 10.000 | 0.00 | 0.00
90 | b | 20 Gauge GI Sheet Metal Duct (1501-2250mm) For Kitchen Exhaust Works |  | Sq.mtr | 150.000 | 0.00 | 0.00
91 | c | 22 Gauge GI Sheet Metal Duct (751-1500mm) |  | Sq.mtr | 100.000 | 0.00 | 0.00
92 | d | 24 Gauge GI Sheet Metal Duct (0-750mm) |  | Sq.mtr | 120.000 | 0.00 | 0.00
93 | 4.2 | EXTRUDED ALUMINIUM CEILING GRILLES |  |  | 0.000 | 0.00 | 0.00
94 |  | Supply, Installation, Testing and Balancing of Powder coated aluminium supply air grilles complete with removable inner core as per approved shop drawing and specifications. The area of grille can be of any geometrical shape (Square rectangular Linear). The grilles shall be with 15 30 45° deflections as per requirement. The Colour shall be decided and approved by client and architect. |  |  | 0.000 | 0.00 | 0.00
95 |  | Make Cosmos, Air Master System Air |  |  | 0.000 | 0.00 | 0.00
96 |  | Linear Square Rectangular Grille |  | Sq.mtr | 6.000 | 0.00 | 0.00
97 | 4.3 | SS EXHAUST AND FRESH AIR GRILLES |  |  | 0.000 | 0.00 | 0.00
98 |  | SITC of 18G S.S 304 Grills adjustable Double Deflector With S.S Volume Control Dampers. Grills to be of Double Deflection Type for ease of deflection on all sides and to have necessary built in Dampers for adjustable nature. |  |  | 0.000 | 0.00 | 0.00
99 |  | Make Carryaire System Air Dynacraft Air Master |  |  | 0.000 | 0.00 | 0.00
100 | a | Linear Square Rectangular Grille |  | Sq.mtr | 0.500 | 0.00 | 0.00
101 | 4.4 | DOOR TRANSFER GRILLE |  |  | 0.000 | 0.00 | 0.00
102 |  | SITC of Aluminium extruded powder coated Door transfer grills. |  |  | 0.000 | 0.00 | 0.00
103 |  | Door transfer grille (Back to Back) |  | Sq.mtr | 1.000 | 0.00 | 0.00
104 |  | Make Cosmos, Air Master System Air |  |  | 0.000 | 0.00 | 0.00
105 | 4.5 | MULTI LEAF VOLUME CONTROL DAMPER |  |  | 0.000 | 0.00 | 0.00
106 |  | SITC of opposed blade aerofoil type 1.2 mm thick Anodized Aluminium volume control dampers for ducts shall be provided with concealed gears, plastic operator and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawings and specifications. |  | Sq.mtr | 2.500 | 0.00 | 0.00
107 |  | Make Cosmos, Air Master System Air |  |  | 0.000 | 0.00 | 0.00
108 | 4.6 | OPPOSED BLADE DAMPER |  |  | 0.000 | 0.00 | 0.00
109 |  | SITC of Aluminium Opposed blade dampers black powder coated vertical blades type for supply air collar. The damper should be gear operated type. |  | Sq.mtr | 2.000 | 0.00 | 0.00
110 | 4.7 | CANVAS CONNECTION |  |  | 0.000 | 0.00 | 0.00
111 |  | SITC of Flexible connections between mouth piece of Fan and initial piece of ducting with inspection zip. Flexible connections shall be double thickness non-flammable material (Fire retardant type). |  |  | 0.000 | 0.00 | 0.00
112 | a | For VRF Ductable Unit |  | Nos. | 3.000 | 0.00 | 0.00
113 | c | For Kitchen EX FA Fan |  | Nos. | 4.000 | 0.00 | 0.00
114 | 4.8 | CURTAIN TYPE FIRE DAMPER |  |  | 0.000 | 0.00 | 0.00
115 |  | SITC of fire dampers consist of 16G GI frame, 20G GI interlocking blades secured with SS springs, blades outside airstream clamped with fusible link UL-555 listed with melting point 165 225°F, etc; as per the approved shop drawings and specifications. |  |  | 0.000 | 0.00 | 0.00
116 |  | Make Carryaire System Air Dynacraft Air Master |  |  | 0.000 | 0.00 | 0.00
117 | a | Bare fire dampers |  | Sq.mtr | 1.000 | 0.00 | 0.00
118 | b | Fusible link as per specification UL 555 |  | No | 1.000 | 0.00 | 0.00
119 |  | NOTES |  |  | 0.000 | 0.00 | 0.00
120 |  | The ducting support should be as per tender specification and additional supports are to be provided by Contractor as decided by Consultant. |  |  | 0.000 | 0.00 | 0.00
121 |  | Muslin cloth cover for all air outlets during construction. |  |  | 0.000 | 0.00 | 0.00
122 |  | Pressure testing of complete duct work as per DW SMACNA standard. |  |  | 0.000 | 0.00 | 0.00
123 |  | Silicon sealant for longitudinal transverse joints as per specification. |  |  | 0.000 | 0.00 | 0.00
124 |  | Diffusers grilles shall be powder coated as per color approved by Architect. |  |  | 0.000 | 0.00 | 0.00
125 | 5 | THERMAL ACOUSTIC INSULATION |  |  | 0.000 | 0.00 | 0.00
126 | 5.1 | THERMAL INSULATION |  |  | 0.000 | 0.00 | 0.00
127 |  | Supply fixing of Thermal insulation for supply air duct using 19mm thick class O Closed cell nitrile rubber with anti-microbial coating on it. Insulation shall have Thermal conductivity of 0.033 W (m.K) and water vapor permeance of 0.10. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape. The duct shall be stick with recommended adhesive. |  | Sq.mtr | 100.000 | 0.00 | 0.00
128 |  | Make Armaflex K-flex Aerofoam ALP Aeroflex |  |  | 0.000 | 0.00 | 0.00
129 | 5.2 | ACOUSTIC INSULATION |  |  | 0.000 | 0.00 | 0.00
130 |  | Supply fixing acoustic insulation for ducting using Class 1 closed cell elastomeric insulation of 10mm thick Nitrile rubber insulation adhesive, longitudinal transverse joints sealed with adhesive in neat clean manner. Material shall be processed Nitrile Rubber foam with anti-microbial protection. Insulation shall have thermal conductivity of 0.047 W (m.K) and density of 140 - 180 kg m³. |  | Sq.mtr | 25.000 | 0.00 | 0.00
131 |  | Make Armaflex K-flex Aerofoam ALP Aeroflex |  |  | 0.000 | 0.00 | 0.00
132 | 5.3 | THERMAL INSULATION FOR KITCHEN EXHAUST DUCTS |  |  | 0.000 | 0.00 | 0.00
133 |  | SITC of 80mm thick Glass Fibre Blanket Insulation material bonded with Thrmosetting Resin, with factory applied laminated aluminium foil of 22 micrns with fibre glass backing. Further, wire mesh along with 7 mil cloth shall be applied on above the insulation with proper adhersive. Nominal density 32 Kg CuM. Thermal conductivity, < 0.033 W m.K at 24 degreeC. All Insuation material and adhesives shall be as per Class I for surface spread and in accordance with BS 476, Class O for non-combustible grade. |  | Sq.mtr | 150.000 | 0.00 | 0.00
134 |  | Make Rockwool UP Twiga |  |  | 0.000 | 0.00 | 0.00
135 |  | Note |  |  | 0.000 | 0.00 | 0.00
136 | a. | Insulation work to be coordinated with other agencies and repair to be included by contractor as per site requirement. |  |  | 0.000 | 0.00 | 0.00
137 | b. | Vendors to take care of the installation, if any damages takes place the vendor to repair or replace and hand over to clients in good and acceptable condition. |  |  | 0.000 | 0.00 | 0.00
138 | c. | Thermal insulation shall be internal for Elliptical Expossed ducting. |  |  | 0.000 | 0.00 | 0.00
139 | 6 | ELECTRICAL WORKS |  |  | 0.000 | 0.00 | 0.00
140 | 6.2 | POWER CABLING |  |  | 0.000 | 0.00 | 0.00
141 |  | Supply, handling, laying effecting proper connections testing and commissioning of following sizes of 1.1 KV grade XLPE insulated FRLS Aluminium Copper conductor cables laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with Copper earthing as specified for continuous earthing along with cable. All complete as required and as per final instruction as given by Owners Consultants and as per Technical specifications. Earthing shall be measured separately and shall be connected in two runs. Power to ELCB to be provided near each ODU by electrical contractor. |  |  | 0.000 | 0.00 | 0.00
142 | a | Suitable Power Cable |  |  | 0.000 | 0.00 | 0.00
143 |  | Suitable for 6600 CFM Kitchen Exhaust Fan, Star Delta Panel with VFD |  | Rmt | 10.000 | 0.00 | 0.00
144 |  | Suitable for 5600 CFM Kitchen Air-washer, Star Delta Panel with VFD |  | Rmt | 10.000 | 0.00 | 0.00
145 | b | Earthing |  |  | 0.000 | 0.00 | 0.00
146 |  | 8 SWG |  | Rmt | 40.000 | 0.00 | 0.00
147 | 6.3 | CABLE TERMINATION |  |  | 0.000 | 0.00 | 0.00
148 |  | Supply Making of Cable termination of armoured unarmoured cables 1.1 KV grade including installation of cable glands, cable lugs (Aluminium for A2XFY copper for 2XFY YY Double compression type), heat shrinkable sleeves on long ends, crimping paste etc. The work includes testing commissioning of cables, meggaring values submitting reports of tests. (One set includes termination of all cores of one end only). All crimping tools dies shall be arranged by contractor. |  |  | 0.000 | 0.00 | 0.00
149 | a | Suitable for 6600 CFM Kitchen Exhaust Fan, Star Delta Panel with VFD |  | Nos. | 2.000 | 0.00 | 0.00
150 | b | Suitable for 5600 CFM Kitchen Air-washer, Star Delta Panel with VFD |  | Nos. | 2.000 | 0.00 | 0.00
151 | 6.4 | CABLE TRAYS |  |  | 0.000 | 0.00 | 0.00
152 |  | Supplying Fixing of following sizes of GI cable tray duly painted perforated type of height 50mm along with necessary bends, reducers etc. anchored along the wall suspended from the ceiling with necessary MS supports. |  |  | 0.000 | 0.00 | 0.00
153 | a | 50mm wide x 50mm ht x 1.6mm thick |  | Rmt | 20.000 | 0.00 | 0.00
154 |  | Fire Sprinkler |  | NOS | 1.000 | 0.00 | 0.00
155 | 1 | Providing, laying, jointing, testing and commissioning of G.I. `C Class pipes (IS 1239 (Part-I)-1979) including cutting,threading welding etc providing all malleable galvanized iron fittings conforming to IS 1879, viz. Flanges, bends, tees, elbows,reducers, unions, supporting with G. I. clamps, hangers, M.S. brackets etc. including cutting holes and chases in brick or RCC wall slabs and making good the same to the Approval of Architect consultant,complete including painting with one coat of primer and two or more coats of synthetic enamel paint of approved make and shade. |  |  | 0.000 | 0.00 | 0.00
156 | i) | 25 mm dia. |  | RMT | 25.000 | 0.00 | 0.00
157 | ii) | 32 mm dia. |  | RMT | 5.000 | 0.00 | 0.00
158 | iii) | 40 mm dia. |  | RMT | 15.000 | 0.00 | 0.00
159 | iv) | 50 mm dia. |  | RMT | 20.000 | 0.00 | 0.00
160 | v) | 65 mm dia. |  | RMT | 5.000 | 0.00 | 0.00
161 | vi) | 80 mm dia. |  | RMT | 5.000 | 0.00 | 0.00
162 | vii) | 100 mm dia. |  | RMT | 5.000 | 0.00 | 0.00
163 | 2 | Providing , fixing testing and commissioning of pendant type sprinkler heads 68 deg. Temp (Quick response type) |  | No. | 5.000 | 0.00 | 0.00
164 | 3 | Providing , fixing testing and commissioning of concealed type sprinkler heads 68 deg. Temp.(Quick response type) |  | No. | 10.000 | 0.00 | 0.00
165 | 4 | Providing , fixing testing and commissioning of upright type sprinkler heads 68 deg. (Quick response type) |  | No. | 23.000 | 0.00 | 0.00
166 | 5 | Providing , fixing testing and commissioning of pendent type sprinkler heads 79 deg. Temp including (Quick response type) |  | No. | 9.000 | 0.00 | 0.00
167 | 6 | Providing fixing testing and commissioning of UL Rated SS braided Flexible pipe (Prior to order please check condition of existing droppers) |  |  | 0.000 | 0.00 | 0.00
168 | i) | 1Mt Ht |  | No. | 2.000 | 0.00 | 0.00
169 | ii) | 1.6Mt Ht |  | No. | 7.000 | 0.00 | 0.00
170 | 7 | Gun metal chrome finished Ball valves (PN 16) with fittings of screwedend type. |  |  | 0.000 | 0.00 | 0.00
171 | I) | 32 mm dia. (Sprinkler drain-OPTIONAL) |  | Nos. | 1.000 | 0.00 | 0.00
172 | 8 | Wheel operated Butterfly Valves (PN 16) with inbuilt supervisory switch (UL listed and FM approved) with CI Body, Black Nitrile Body Liner and Nylon Coated SG Iron Disc with material and labour including hydraulic testing etc. complete as per drawing, specification to the level of satisfaction of Site- Incharge. |  |  | 0.000 | 0.00 | 0.00
173 | I) | 80 mm dia. |  | No. | 1.000 | 0.00 | 0.00
174 |  | FAS |  | NOS | 1.000 | 0.00 | 0.00
175 | 13.1.1 | Fire alarm Addressable control panel (1 Loop) |  |  | 0.000 | 0.00 | 0.00
176 | 13.3.3 | Supply,Installation,Testing Commissioning of Horn Strobe rated at 82 dBA @ 3m for Audible annunciation and 75cd flashing at 1 Hz for visual indication with Control modules and necessary accessories including back box. |  | Nos | 2.000 | 0.00 | 0.00
177 | 13.3.4 | Supply, Installation,Testing Commissioning of Analogue Addressable Flash scan Type Photoelectric smoke detectors( Below False Ceiling) having Rotary, decimal addressing system with standard base, built in isolation function and junction box. The detector shall be capable to address in the range of 1-159. The detector shall be with Visible bi-color LEDs for 360 deg viewing and shall blink green every time the detector is addressed, and illuminate steady red on alarm. |  | Nos | 5.000 | 0.00 | 0.00
178 | 13.3.7 | Supply,Installation,Testing Commissioning of Analogue Addressable Flash scan Type Heat Detector having Rotary, decimal addressing system with standard base, built in isolation function and junction box. The detector shall be capable to address in the range of 1-159. The detector shall be with Visible bi-color LEDs for 360 deg viewing and shall blink green every time the detector is addressed, and illuminate steady red on alarm. (Make- Edward-EST-SIGA-HFS) |  | Nos | 4.000 | 0.00 | 0.00
179 | 13.3.9 | Supply,Installation,Testing Commissioning of Addressable Break Glass Manual Call Point having Rotary, decimal addressing system and having an integrally mounted addressable module that monitors and reports contact status. |  | Nos | 2.000 | 0.00 | 0.00
180 | 13.4 | SITC of Fault Isolator. |  | Nos | 1.000 | 0.00 | 0.00
181 | 13.5 | SITC of 2Cx1.5sq.mm multistranded FRLS Cu. Armoured for RED Colour,Mylan Shielded Screened cable For SLC. |  | Mtrs | 120.000 | 0.00 | 0.00
182 | 13.6 | Response indicator. |  | Nos | 5.000 | 0.00 | 0.00
183 | 13.7 | Supply Installation of CAT-6 Cable(DIAL FAS PANEL TO RFPA PANEL) |  | Mtr. | 150.000 | 0.00 | 0.00
184 | 13.8 | Programing Charges to Paid Airport Vendor |  | No | 1.000 | 0.00 | 0.00