## BOQ Price Bid
|  | RFQ No: R0087 COST COMPARISON REPORT | RFQ No: R0087 COST COMPARISON REPORT | Comp. Date : 12/02/2024 | Comp. Date : 12/02/2024 | Comp. Date : 12/02/2024 | FALLOW DEZIENCE TREE LLP | Vendor Name : FALLOW DEZIENCE TREE LLP | Mahamaya Engineering | Vendor Name : Mahamaya Engineering | ANJLE MEP PROJECTS PRIVATE LIMITED | Vendor Name : ANJLE MEP PROJECTS PRIVATE LIMITED | Pioneer Infra And Turnkey Solutions | Vendor Name : Pioneer Infra And Turnkey Solutions
|  | RFQ No: R0087 COST COMPARISON REPORT | RFQ No: R0087 COST COMPARISON REPORT | RFQ #: R0087 | RFQ #: R0087 | RFQ #: R0087 | Contact Name : Khursheed Ahmad/Jasmine Grover | Contact Name : Khursheed Ahmad/Jasmine Grover | Contact Name : Yash Katoch | Contact Name : Yash Katoch | Contact Name : Priyanka/Premkant Rajpoot | Contact Name : Priyanka/Premkant Rajpoot | Contact Name : Pankaj Upadhyay/Bipin Upadhyay | Contact Name : Pankaj Upadhyay/Bipin Upadhyay
|  | RFQ No: R0087 COST COMPARISON REPORT | RFQ No: R0087 COST COMPARISON REPORT | RFQ Date : 09/02/2024 20:55:33 | RFQ Date : 09/02/2024 20:55:33 | RFQ Date : 09/02/2024 20:55:33 | Vendor City : | Vendor City : | Vendor City : delhi | Vendor City : delhi | Vendor City : | Vendor City : | Vendor City : | Vendor City :
|  | RFQ No: R0087 COST COMPARISON REPORT | RFQ No: R0087 COST COMPARISON REPORT | BCD Date : 10/02/2024 20:55:00 | BCD Date : 10/02/2024 20:55:00 | BCD Date : 10/02/2024 20:55:00 | Telephone # : | Telephone # : | Telephone # : 9810360460 | Telephone # : 9810360460 | Telephone # : | Telephone # : | Telephone # : | Telephone # :
|  | RFQ No: R0087 COST COMPARISON REPORT | RFQ No: R0087 COST COMPARISON REPORT |  |  |  | Mobile # : | Mobile # : | Mobile # : 9810360460 | Mobile # : 9810360460 | Mobile # : | Mobile # : | Mobile # : | Mobile # :
PR Number : Semolina-2324-00122 | PR Number : Semolina-2324-00122 | PR Number : Semolina-2324-00122 | PR Number : Semolina-2324-00122 | PR Number : Semolina-2324-00122 | PR Number : Semolina-2324-00122 | PR Number : Semolina-2324-00122 | Email : accounts@fallowdezience.com | Email : accounts@fallowdezience.com | Email : mahamaya.engineering1@gmail.com | Email : mahamaya.engineering1@gmail.com | Email : anjlemepprojects@gmail.com | Email : anjlemepprojects@gmail.com | Email : bipinu@pioneerindinfra.com | Email : bipinu@pioneerindinfra.com
Package / RFQ Name : HVAC work, AJ Kitchen- Ahmedbad | Package / RFQ Name : HVAC work, AJ Kitchen- Ahmedbad | Package / RFQ Name : HVAC work, AJ Kitchen- Ahmedbad | Package / RFQ Name : HVAC work, AJ Kitchen- Ahmedbad | Package / RFQ Name : HVAC work, AJ Kitchen- Ahmedbad | Package / RFQ Name : HVAC work, AJ Kitchen- Ahmedbad | Package / RFQ Name : HVAC work, AJ Kitchen- Ahmedbad | Round # : 4 (RFQ) | Round # : 4 (RFQ) | Round # : 4 (RFQ) | Round # : 4 (RFQ) | Round # : 4 (RFQ) | Round # : 4 (RFQ) | Round # : 4 (RFQ) | Round # : 4 (RFQ)
Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Buyer : Jogeswar Sahu | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score :
Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Currency :INR | Currency :INR | Currency :INR | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date :
Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | BUDGET PRICE :.00 | BUDGET PRICE :.00 | BUDGET PRICE :.00 | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date :
Sr No. | Item Code | Item Name | Item Description | UOM | Qty | Minimum Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount
1 |  | HVAC High Side work and Low side Work for AJ Kitchen Ahmedabad | BOQ for HVAC High Side work and HVAC Low side work for AJ Kitchen Ahmedabad | NOS | 1 |  |  | 805029 |  | 761270 |  | 839700 |  | 1048901
1 | Note: | Prices shall be based on supply, installation, testing commissioning (SITC) at site including all taxes, duties, transportation insurance etc. | Prices shall be based on supply, installation, testing commissioning (SITC) at site including all taxes, duties, transportation insurance etc.
2 | 1 | CHILLED WATER TYPE CEILING SUSPENDED AHU (AIR HANDLING UNIT) | CHILLED WATER TYPE CEILING SUSPENDED AHU (AIR HANDLING UNIT)
3 | 1.1 | CEILING SUSPENDED AHU | CEILING SUSPENDED AHU
4 |  | Supply and assembly of Ceiling Suspended Double skin cabinet type AHU Integrated (Air handling units) of following specifications | Supply and assembly of Ceiling Suspended Double skin cabinet type AHU Integrated (Air handling units) of following specifications
5 |  | Frame Structure It shall consist of 48mm Extruded Aluminium with thermal break profile. | Frame Structure It shall consist of 48mm Extruded Aluminium with thermal break profile.
6 |  | Panel 45mm + - 2mm thick double skin sandwich panels with rockwool insulation of density 64 kg m3 or PUF insulation of 48 kg m3 , The sheet thickness shall be minimum 0.6 mm for the outer skin precoated and 0.8 mm thickness for the inner skin of plain GI. | Panel 45mm + - 2mm thick double skin sandwich panels with rockwool insulation of density 64 kg m3 or PUF insulation of 48 kg m3 , The sheet thickness shall be minimum 0.6 mm for the outer skin precoated and 0.8 mm thickness for the inner skin of plain GI.
7 |  | Filtration Section It shall be provided with single stage washable type of prefilter MERV 8 first stage which shall be placed before coil section. | Filtration Section It shall be provided with single stage washable type of prefilter MERV 8 first stage which shall be placed before coil section.
8 |  | Coil Section Chilled water coil Multi row deep constructed with Aluminium fins of min 0.11mm thick 12 Fins per inch, and copper tubes of min 27 Guage thickness HYRDOPHYLLIC coated fins. Copper tube shall be min 12.5mm diameter. AHRI certified coil.The coil face area velocity shall not exceed 2.5m sec (500 fpm). | Coil Section Chilled water coil Multi row deep constructed with Aluminium fins of min 0.11mm thick 12 Fins per inch, and copper tubes of min 27 Guage thickness HYRDOPHYLLIC coated fins. Copper tube shall be min 12.5mm diameter. AHRI certified coil.The coil face area velocity shall not exceed 2.5m sec (500 fpm).
9 |  | Drain Pan Condensate drain pan shall be fabricated from 18G SS 304 powder coated, insulated with 13 mm thick closed cell elastomeric(nitrile rubber) insulation. | Drain Pan Condensate drain pan shall be fabricated from 18G SS 304 powder coated, insulated with 13 mm thick closed cell elastomeric(nitrile rubber) insulation.
10 |  | Fan Section SISW DIDW Direct drive backward curved fan. The fan section shall be provided with limt switch for safety to shut off fan during Opening of access door. Fan outlet velocity not to exceed 1600 FPM. The sound level shall not be exceed more than 60dB @ 1m from the source. Vibration isolators, Door Limit switch, UV Lamp as per Technical Specifications, AHU Summary Sheet and drawings. Total static pressue has to calculated by Contractor as per the configuration. | Fan Section SISW DIDW Direct drive backward curved fan. The fan section shall be provided with limt switch for safety to shut off fan during Opening of access door. Fan outlet velocity not to exceed 1600 FPM. The sound level shall not be exceed more than 60dB @ 1m from the source. Vibration isolators, Door Limit switch, UV Lamp as per Technical Specifications, AHU Summary Sheet and drawings. Total static pressue has to calculated by Contractor as per the configuration.
11 |  | Other Details AHU to house control box terminal box with Auto-Manual switch and incomer power terminal, with SPP, Over Undervoltage protection, shortcircuit protection and with no-nc contacts (potential free contact) to be provided for tripping on signal from Fire Dampers Fire Alarm Panel. Power cable from Terminal box to motor control cabling of required size upto the thermostat sensor etc. to be provided. Internal electrical and control wiring of AHU to be provided as factory fitted from AHU supplier. The cost shall include all necessary supports accessories required for installation. | Other Details AHU to house control box terminal box with Auto-Manual switch and incomer power terminal, with SPP, Over Undervoltage protection, shortcircuit protection and with no-nc contacts (potential free contact) to be provided for tripping on signal from Fire Dampers Fire Alarm Panel. Power cable from Terminal box to motor control cabling of required size upto the thermostat sensor etc. to be provided. Internal electrical and control wiring of AHU to be provided as factory fitted from AHU supplier. The cost shall include all necessary supports accessories required for installation.
12 |  | Contractor shall design the chilled water coil according to the following conditions | Contractor shall design the chilled water coil according to the following conditions
13 |  | a. Coil air entering temperature - 75.4°F DB | a. Coil air entering temperature - 75.4°F DB
14 |  | b. Coil air leaving temperature - 54 deg. F DB 52.99 deg. F WB | b. Coil air leaving temperature - 54 deg. F DB 52.99 deg. F WB
15 |  | c. Chilled water temperature entering - 6.0 deg. C 42.8 deg. F | c. Chilled water temperature entering - 6.0 deg. C 42.8 deg. F
16 |  | d. Chilled water temperature leaving - 13.3 deg. C 55.9 deg. F | d. Chilled water temperature leaving - 13.3 deg. C 55.9 deg. F
17 |  | Make VTS Zeco Citizen | Make VTS Zeco Citizen
18 |  | Type Capacity Tonnage ESP No. of | Type Capacity Tonnage ESP No. of
19 |  | (Cfm) TR (mm WG) Rows | (Cfm) TR (mm WG) Rows
20 | a | CS AHU 1500 4.32 25 4 6 | CS AHU 1500 4.32 25 4 6 | No. | 1 | 95000 | 129340 | 129340 | 100000 | 100000 | 95000 | 95000 | 250000 | 250000
|  | Total |  |  |  | 95000 |  | 129340 |  | 100000 |  | 95000 |  | 250000
21 |  | GENERAL NOTES | GENERAL NOTES
22 | a. | LHS RHS VALVE station location to be confirmed. | LHS RHS VALVE station location to be confirmed.
23 | b. | Fan outlet velocity - 1600 FPM | Fan outlet velocity - 1600 FPM
24 | c. | Contractor shall submit static pressure calculation for all above units to Client Consultant. | Contractor shall submit static pressure calculation for all above units to Client Consultant.
25 | d. | Any change in motor HP shall be made at no extra cost to client. | Any change in motor HP shall be made at no extra cost to client.
26 | e. | Fan efficiency shall be minimum 75% | Fan efficiency shall be minimum 75%
27 | f. | The cost shall be included liftting shifting of each equipment material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material equipment. | The cost shall be included liftting shifting of each equipment material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material equipment.
28 |  | SUB-TOTAL | SUB-TOTAL
29 | 2 | CHILLED WATER PIPING WITH INSULATION | CHILLED WATER PIPING WITH INSULATION
30 | 2.1 | CHW PIPE | CHW PIPE
31 |  | SITC of MS Heavy duty class C ERW Chilled Water pipe conforming to IS 1239 - 2004 primer painted including bends, tees, MS supports, PUFF saddles, anchor fasteners, steel angles and any other material required to complete the work. The piping flange connection bolts, washers and nuts should be hot dipped galvanised. Flourscent Plastic Sticker paint shall be applied to indicate Water flow directions. Only End flanges to be used for capping of pipes. Table E of BS code for flange thickness to be adhered. | SITC of MS Heavy duty class C ERW Chilled Water pipe conforming to IS 1239 - 2004 primer painted including bends, tees, MS supports, PUFF saddles, anchor fasteners, steel angles and any other material required to complete the work. The piping flange connection bolts, washers and nuts should be hot dipped galvanised. Flourscent Plastic Sticker paint shall be applied to indicate Water flow directions. Only End flanges to be used for capping of pipes. Table E of BS code for flange thickness to be adhered.
32 |  | Make Jindal Hissar TATA | Make Jindal Hissar TATA
33 | a | F 32 mm | F 32 mm | Rmt | 20 | 19000 | 1500 | 30000 | 1050 | 21000 | 950 | 19000 | 1550 | 31000
34 | 2.2 | CHILLED WATER PIPING INSULATION - INTERNAL USE | CHILLED WATER PIPING INSULATION - INTERNAL USE
35 |  | SITC of insulation for chilled water. piping. For internal pipe - Stick 25mm thick Nitrile rubber class O Closed cell nitrile rubber with anti-microbial coating on it. Insulation shall have Thermal conductivity of 0.033 W (m.K) and water vapor permeance of 0.10. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape and putting PVC bands at all supports. | SITC of insulation for chilled water. piping. For internal pipe - Stick 25mm thick Nitrile rubber class O Closed cell nitrile rubber with anti-microbial coating on it. Insulation shall have Thermal conductivity of 0.033 W (m.K) and water vapor permeance of 0.10. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape and putting PVC bands at all supports.
36 |  | Make Armaflex K-flex | Make Armaflex K-flex
37 | a | F 32 mm | F 32 mm | Rmt | 20 | 10200 | 700 | 14000 | 575 | 11500 | 650 | 13000 | 510 | 10200
38 | 2.3 | BALL VALVE | BALL VALVE
39 |  | SITC of following sizes of Ball Valve consist of Cap, Brass Body, Rated for 150 psi SWP, 600 psi WOG Pressure Two-piece construction; with brass body, regular port, B-16 chrome-plated ball and stem, replaceable “Teflon” or “TFE” seats and seals, blowout-proof stem, vinyl covered steel handle, threaded or soldered ends and extended stem for insulated piping. Same valve shall be used as a Drain valve. | SITC of following sizes of Ball Valve consist of Cap, Brass Body, Rated for 150 psi SWP, 600 psi WOG Pressure Two-piece construction; with brass body, regular port, B-16 chrome-plated ball and stem, replaceable “Teflon” or “TFE” seats and seals, blowout-proof stem, vinyl covered steel handle, threaded or soldered ends and extended stem for insulated piping. Same valve shall be used as a Drain valve.
40 |  | Make Zoloto Audco Kitz | Make Zoloto Audco Kitz
41 | a | F 32 mm | F 32 mm | Nos. | 3 | 7500 | 2500 | 7500 | 3000 | 9000 | 3850 | 11550 | 5000 | 15000
42 | 2.4 | BALL VALVE WITH Y-STRAINER | BALL VALVE WITH Y-STRAINER
43 |  | SITC of following sizes of Brass Ball Valve with Y-Strainer consist of Cap, Brass Body, Rated for 150 psi SWP, 600 psi WOG Pressure Two-piece construction; with brass body, regular port, B-16 chrome-plated ball and stem, replaceable “Teflon” or “TFE” seats and seals, blowout-proof stem, vinyl covered steel handle, threaded or soldered ends and extended stem for insulated piping. Filter element shall be of non magnetic SS sheet with perforation. | SITC of following sizes of Brass Ball Valve with Y-Strainer consist of Cap, Brass Body, Rated for 150 psi SWP, 600 psi WOG Pressure Two-piece construction; with brass body, regular port, B-16 chrome-plated ball and stem, replaceable “Teflon” or “TFE” seats and seals, blowout-proof stem, vinyl covered steel handle, threaded or soldered ends and extended stem for insulated piping. Filter element shall be of non magnetic SS sheet with perforation.
44 |  | Make Zoloto Audco Kitz | Make Zoloto Audco Kitz
45 | a | F 32 mm | F 32 mm | No. | 1 | 3850 | 4800 | 4800 | 5850 | 5850 | 3850 | 3850 | 13500 | 13500
46 | 2.5 | PIBCV VALVES | PIBCV VALVES
47 |  | SITC of Pressure Independent Balancing cum Control Valves (PIBCV) including integrated motorised control valve and balancing device for combined flow and water balancing requirement. Valve body to be rated for PN 16. The valve design flow rate should be factory calibrated with + - 5% flow accuracy. Valve shall have necessary measuring ports, drain port, flanges etc., Valve shall also provide temperature sensor with necessary cabling (min 2mtr length to be considered with each valve). The balancing to be done through microprocessor based hand held terminal POT and the same results shall be furnished in the water balancing report as part of commissioning report and handing over manual. | SITC of Pressure Independent Balancing cum Control Valves (PIBCV) including integrated motorised control valve and balancing device for combined flow and water balancing requirement. Valve body to be rated for PN 16. The valve design flow rate should be factory calibrated with + - 5% flow accuracy. Valve shall have necessary measuring ports, drain port, flanges etc., Valve shall also provide temperature sensor with necessary cabling (min 2mtr length to be considered with each valve). The balancing to be done through microprocessor based hand held terminal POT and the same results shall be furnished in the water balancing report as part of commissioning report and handing over manual.
48 |  | Make Oventrop Siemens Danfoss | Make Oventrop Siemens Danfoss
49 | a | F 32 mm | F 32 mm | No. | 1 | 18000 | 45000 | 45000 | 35000 | 35000 | 46500 | 46500 | 18000 | 18000
50 | 2.6 | Auto Air Vent Valves | Auto Air Vent Valves
51 |  | Make Anergy Flamco | Make Anergy Flamco
52 |  | Providing and fitting Auto Vent Valves. | Providing and fitting Auto Vent Valves.
53 | a | SITC of Auto air vent in each risers common headers AHU. 3 4 auto vent valves at each coil riser header. | SITC of Auto air vent in each risers common headers AHU. 3 4 auto vent valves at each coil riser header. | Nos. | 2 | 3000 | 1500 | 3000 | 2550 | 5100 | 2450 | 4900 | 3700 | 7400
54 | 2.7 | SITC of Pressure gauges Thermometers | SITC of Pressure gauges Thermometers
55 |  | Make H Guru Waree | Make H Guru Waree
56 |  | Necessary pressure gauges and thermometers 4 Dial type. | Necessary pressure gauges and thermometers 4 Dial type.
57 | a | Water Pressure gauges 150mm dial complete with gauge valves, mounting, fittings and copper tubing extension wherever required. Pressure gauges Range 0-10 Kg CM2 | Water Pressure gauges 150mm dial complete with gauge valves, mounting, fittings and copper tubing extension wherever required. Pressure gauges Range 0-10 Kg CM2 | Nos. | 2 | 3300 | 3500 | 7000 | 2000 | 4000 | 1650 | 3300 | 8300 | 16600
58 | b | Thermometers of the mercury in glass stem type and copper separable well complete with guard etc., of industrial grade mounting on water lines. Length 9 12 inches, Thermometer, Range 0-50 deg C | Thermometers of the mercury in glass stem type and copper separable well complete with guard etc., of industrial grade mounting on water lines. Length 9 12 inches, Thermometer, Range 0-50 deg C | Nos. | 2 | 3100 | 6000 | 12000 | 1550 | 3100 | 2450 | 4900 | 2700 | 5400
59 | c | Thermowells | Thermowells | Nos. | 4 | 3600 | 4500 | 18000 | 900 | 3600 | 1250 | 5000 | 1700 | 6800
60 | d | SITC of Brass Test Plug of industrial grade mounting on water | SITC of Brass Test Plug of industrial grade mounting on water | Nos. | 0 | 0 | 0 | 0 | 0 | 0 | 2350 | 0 | 0 | 0
61 | 2.8 | INSULATED CONDENSATE DRAIN PIPE | INSULATED CONDENSATE DRAIN PIPE
62 |  | SITC of UPVC pipes of following sizes for drain with necessary supports and fittings such as elbows, tees reducers etc. The insulation line to be insulated with nitrile rubber insulation of thickness 9mm and wrapped by weather proof protection tape. The Pipe wherever concealed should also have a parallel line as a standby arrangement in case of block of primary pipe . | SITC of UPVC pipes of following sizes for drain with necessary supports and fittings such as elbows, tees reducers etc. The insulation line to be insulated with nitrile rubber insulation of thickness 9mm and wrapped by weather proof protection tape. The Pipe wherever concealed should also have a parallel line as a standby arrangement in case of block of primary pipe .
63 |  | Make Supreme, Prince, Astral | Make Supreme, Prince, Astral
64 | a | F 25 mm | F 25 mm | Rmt | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 0 | 0
65 | b | F 32 mm | F 32 mm | Rmt | 10 | 4100 | 475 | 4750 | 410 | 4100 | 510 | 5100 | 1100 | 11000
66 |  | NOTES FOR PIPING | NOTES FOR PIPING
67 | a | Cover all open pipe ends with muslin cloth during construction | Cover all open pipe ends with muslin cloth during construction
68 | b | Pipe cleaning chemical treatment as per specs shall be included in the piping cost. | Pipe cleaning chemical treatment as per specs shall be included in the piping cost.
69 | c | Unit rates for all indicated sizes of pipes valves shall be furnished. | Unit rates for all indicated sizes of pipes valves shall be furnished.
70 | d | Cleaning Painting of pipe before insulation shall be included in piping cost. | Cleaning Painting of pipe before insulation shall be included in piping cost.
71 | e | The piping support should be as per tender specification and additional supports are to be provided Contractor as decided by Consultant. | The piping support should be as per tender specification and additional supports are to be provided Contractor as decided by Consultant.
72 | f | All the valves shall be insulated with the same material as that of Chilled water pipng and cost of insulation for valves shall be considered. | All the valves shall be insulated with the same material as that of Chilled water pipng and cost of insulation for valves shall be considered.
73 |  | SUB-TOTAL | SUB-TOTAL
74 | 3 | VENTILATION SYSTEM | VENTILATION SYSTEM
75 | 3.1 | KITCHEN DRY SCRUBBER | KITCHEN DRY SCRUBBER
76 |  | SITC of Dry scrubber – Electrostatic Air cleaner with starter panel as per specifications, suitable for following capacities, including electrical starter panel . The Air filtration efficiency should be between 90 to 95% units shall be staked one above other or side by side as per site requirement, if vendor will propose multiple units. | SITC of Dry scrubber – Electrostatic Air cleaner with starter panel as per specifications, suitable for following capacities, including electrical starter panel . The Air filtration efficiency should be between 90 to 95% units shall be staked one above other or side by side as per site requirement, if vendor will propose multiple units.
77 |  | Finishing - Power coated, Dark Blue | Finishing - Power coated, Dark Blue
78 |  | Operating voltage - 220 Vac+ -10%, 50 Hz (Single phase) | Operating voltage - 220 Vac+ -10%, 50 Hz (Single phase)
79 |  | Features - Short circuit, arc protection and auto restore power supply, BMS (Building Management System) terminals provided, Auto power cut-off when door is opened, Indicator LEDs for normal or wash indicator, Set of Terminals for remote LED normal or wash indicator | Features - Short circuit, arc protection and auto restore power supply, BMS (Building Management System) terminals provided, Auto power cut-off when door is opened, Indicator LEDs for normal or wash indicator, Set of Terminals for remote LED normal or wash indicator
80 |  | Efficiency - Upto 95%, meets NIOSH 5026 Oil Mist Test | Efficiency - Upto 95%, meets NIOSH 5026 Oil Mist Test
81 |  | Particle Size - Collects particles as small as 0.01 microns | Particle Size - Collects particles as small as 0.01 microns
82 |  | Motor - Sealead ball bearings UL, single phase. | Motor - Sealead ball bearings UL, single phase.
83 |  | Cell - Ionizing voltage - 12 KVdc | Cell - Ionizing voltage - 12 KVdc
84 |  | Collector voltage - 6 KVdc | Collector voltage - 6 KVdc
85 |  | One cell comprising of 9 ionizing wires and 25 collection plates | One cell comprising of 9 ionizing wires and 25 collection plates
86 |  | Controls - Auto cut-off when door is opened. Indicator lights for fault, normal or wash function. | Controls - Auto cut-off when door is opened. Indicator lights for fault, normal or wash function.
87 |  | Pre-filter - Aluminium mesh, washable Dry contact for BMS. | Pre-filter - Aluminium mesh, washable Dry contact for BMS.
88 |  | Make Rydair Espair | Make Rydair Espair
89 |  | CFM - 3100 | CFM - 3100 | No. | 1 | 155000 | 210000 | 210000 | 155000 | 155000 | 265000 | 265000 | 200000 | 200000
90 |  | SUB-TOTAL | SUB-TOTAL
91 | 4 | SHEET METAL WORKS | SHEET METAL WORKS
92 | 4.1 | FACTORY FABRICATED G.I RECTANGULAR DUCT | FACTORY FABRICATED G.I RECTANGULAR DUCT
93 |  | Supply, Fabrication, Testing, and Commissioning of Factory Fabricated GI Sheet Metal 120GSM Rectangular boxed ducting, Plenums, Cowls, Elbows with turning vanes, Splitters, Reducers, Flanges, Collars etc as per IS and Installaton as per SMACNA standards, The complete ducting shall be provided with MS Supports, Rods, Angles, Flanges, Bracing, Rubber Gaskets, Wooden frames, Canvas Connections, etc. as per drawings and specifications. | Supply, Fabrication, Testing, and Commissioning of Factory Fabricated GI Sheet Metal 120GSM Rectangular boxed ducting, Plenums, Cowls, Elbows with turning vanes, Splitters, Reducers, Flanges, Collars etc as per IS and Installaton as per SMACNA standards, The complete ducting shall be provided with MS Supports, Rods, Angles, Flanges, Bracing, Rubber Gaskets, Wooden frames, Canvas Connections, etc. as per drawings and specifications.
94 |  | GI Sheet Makes Tata, Jindal, SAIL, Ispat | GI Sheet Makes Tata, Jindal, SAIL, Ispat
95 |  | Make Rola Star, Zeco Ductofab | Make Rola Star, Zeco Ductofab
96 | a | 18 Gauge GI Sheet Metal Duct (Above 2251mm Plenum) | 18 Gauge GI Sheet Metal Duct (Above 2251mm Plenum) | Sq.mtr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97 | b | 20 Gauge GI Sheet Metal Duct (1501-2250mm) For Kitchen Works | 20 Gauge GI Sheet Metal Duct (1501-2250mm) For Kitchen Works | Sq.mtr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98 | c | 22 Gauge GI Sheet Metal Duct (751-1500mm) | 22 Gauge GI Sheet Metal Duct (751-1500mm) | Sq.mtr | 15 | 21750 | 2100 | 31500 | 1650 | 24750 | 1450 | 21750 | 1900 | 28500
99 | d | 24 Gauge GI Sheet Metal Duct (0-750mm) | 24 Gauge GI Sheet Metal Duct (0-750mm) | Sq.mtr | 75 | 93750 | 1404 | 105300 | 1450 | 108750 | 1250 | 93750 | 1800 | 135000
100 | 4.2 | EXTRUDED ALUMINIUM CEILING GRILLES | EXTRUDED ALUMINIUM CEILING GRILLES
101 |  | Supply, Installation, Testing and Balancing of Powder coated aluminium supply air grilles complete with removable inner core as per approved shop drawing and specifications. The area of grille can be of any geometrical shape (Square rectangular Linear). The grilles shall be with 15 30 45° deflections as per requirement. The Colour shall be decided and approved by client and architect. | Supply, Installation, Testing and Balancing of Powder coated aluminium supply air grilles complete with removable inner core as per approved shop drawing and specifications. The area of grille can be of any geometrical shape (Square rectangular Linear). The grilles shall be with 15 30 45° deflections as per requirement. The Colour shall be decided and approved by client and architect. | Sq.mtr | 3 | 24750 | 11700 | 35100 | 11000 | 33000 | 8250 | 24750 | 14917 | 44751
102 |  | Make Cosmos, Air Master System Air | Make Cosmos, Air Master System Air
103 | 4.3 | DOOR TRANSFER GRILLE | DOOR TRANSFER GRILLE
104 |  | SITC of Aluminium extruded powder coated Door transfer grills. | SITC of Aluminium extruded powder coated Door transfer grills.
105 |  | Door transfer grille (Back to Back) | Door transfer grille (Back to Back) | Sq.mtr | 1 | 4500 | 13500 | 13500 | 21500 | 21500 | 12500 | 12500 | 4500 | 4500
106 |  | Make Cosmos, Air Master System Air | Make Cosmos, Air Master System Air
107 | 4.4 | EXTRUDED ALUMINIUM SQUARE AIR DIFFUSER | EXTRUDED ALUMINIUM SQUARE AIR DIFFUSER
108 |  | Supply, Installation, Testing and Balancing of Powder coated aluminium supply air square diffuser complete with removable inner core as per approved shop drawing and specifications. The diffuser shall also be provided with Black painted GI opposed blade damper (OBD) of required sizes. The diffuser shall be suitable for gypsum grid ceiling. The Colour shall be decided and approved by client and architect. | Supply, Installation, Testing and Balancing of Powder coated aluminium supply air square diffuser complete with removable inner core as per approved shop drawing and specifications. The diffuser shall also be provided with Black painted GI opposed blade damper (OBD) of required sizes. The diffuser shall be suitable for gypsum grid ceiling. The Colour shall be decided and approved by client and architect.
109 |  | Make Cosmos Ruskin Titus Air Master | Make Cosmos Ruskin Titus Air Master
110 | a | SQUARE DIFFUSER FOR GRID CEILING 600X600mm | SQUARE DIFFUSER FOR GRID CEILING 600X600mm
111 |  | Supply Air Diffuser with OBD - Neck Size 225x225mm | Supply Air Diffuser with OBD - Neck Size 225x225mm | Nos. | 1 | 1850 | 2340 | 2340 | 5500 | 5500 | 1850 | 1850 | 7000 | 7000
112 | 4.5 | MULTI LEAF VOLUME CONTROL DAMPER | MULTI LEAF VOLUME CONTROL DAMPER
113 |  | SITC of opposed blade aerofoil type 1.2 mm thick Anodized Aluminium volume control dampers for ducts shall be provided with concealed gears, plastic operator and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawings and specifications. | SITC of opposed blade aerofoil type 1.2 mm thick Anodized Aluminium volume control dampers for ducts shall be provided with concealed gears, plastic operator and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawings and specifications. | Sq.mtr | 1 | 5304 | 5304 | 5304 | 7500 | 7500 | 12500 | 12500 | 17000 | 17000
114 |  | Make Cosmos, Air Master System Air | Make Cosmos, Air Master System Air
115 | 4.6 | OPPOSED BLADE DAMPER | OPPOSED BLADE DAMPER
116 |  | SITC of Aluminium Opposed blade dampers black powder coated vertical blades type for supply air collar. The damper should be gear operated type. | SITC of Aluminium Opposed blade dampers black powder coated vertical blades type for supply air collar. The damper should be gear operated type. | Sq.mtr | 1 | 3850 | 4290 | 4290 | 6500 | 6500 | 3850 | 3850 | 7500 | 7500
117 | 4.7 | CANVAS CONNECTION | CANVAS CONNECTION
118 |  | SITC of Flexible connections between mouth piece of Fan and initial piece of ducting with inspection zip. Flexible connections shall be double thickness non-flammable material (Fire retardant type). | SITC of Flexible connections between mouth piece of Fan and initial piece of ducting with inspection zip. Flexible connections shall be double thickness non-flammable material (Fire retardant type).
119 | a | For AHU | For AHU | No | 1 | 2496 | 2496 | 2496 | 3500 | 3500 | 2650 | 2650 | 14000 | 14000
120 | b | For Kitchen Ventilation Fan | For Kitchen Ventilation Fan | Nos. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121 | 4.8 | CURTAIN TYPE FIRE DAMPER | CURTAIN TYPE FIRE DAMPER
122 |  | SITC of fire dampers consist of 16G GI frame, 20G GI interlocking blades secured with SS springs, blades outside airstream clamped with fusible link UL-555 listed with melting point 165 225°F, etc; as per the approved shop drawings and specifications. | SITC of fire dampers consist of 16G GI frame, 20G GI interlocking blades secured with SS springs, blades outside airstream clamped with fusible link UL-555 listed with melting point 165 225°F, etc; as per the approved shop drawings and specifications.
123 |  | Make Carryaire System Air Dynacraft Air Master | Make Carryaire System Air Dynacraft Air Master
124 | a | Bare fire dampers | Bare fire dampers | Sq.mtr | 0 | 0 | 0 | 0 | 11500 | 0 | 0 | 0 | 3500 | 0
125 | b | Fusible link as per specification UL 555 | Fusible link as per specification UL 555 | No | 1 | 1170 | 1170 | 1170 | 3520 | 3520 | 16500 | 16500 | 9500 | 9500
126 |  | NOTES | NOTES
127 |  | The ducting support should be as per tender specification and additional supports are to be provided by Contractor as decided by Consultant. | The ducting support should be as per tender specification and additional supports are to be provided by Contractor as decided by Consultant.
128 |  | Muslin cloth cover for all air outlets during construction. | Muslin cloth cover for all air outlets during construction.
129 |  | Pressure testing of complete duct work as per DW SMACNA standard. | Pressure testing of complete duct work as per DW SMACNA standard.
130 |  | Silicon sealant for longitudinal transverse joints as per specification. | Silicon sealant for longitudinal transverse joints as per specification.
131 |  | Diffusers grilles shall be powder coated as per color approved by Architect. | Diffusers grilles shall be powder coated as per color approved by Architect.
132 |  | SUB-TOTAL | SUB-TOTAL
133 | 5 | THERMAL ACOUSTIC INSULATION | THERMAL ACOUSTIC INSULATION
134 | 5.1 | THERMAL INSULATION | THERMAL INSULATION
135 |  | Supply fixing of Thermal insulation for supply air duct using 13mm thick class O Closed cell nitrile rubber with anti-microbial coating on it. Insulation shall have Thermal conductivity of 0.033 W (m.K) and water vapor permeance of 0.10. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape. The duct shall be stick with recommended adhesive. | Supply fixing of Thermal insulation for supply air duct using 13mm thick class O Closed cell nitrile rubber with anti-microbial coating on it. Insulation shall have Thermal conductivity of 0.033 W (m.K) and water vapor permeance of 0.10. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape. The duct shall be stick with recommended adhesive. | Sq.mtr | 30 | 25500 | 975 | 29250 | 850 | 25500 | 950 | 28500 | 1000 | 30000
136 |  | Make Armaflex K-flex | Make Armaflex K-flex
137 | 5.2 | ACOUSTIC INSULATION | ACOUSTIC INSULATION
138 |  | Supply fixing acoustic insulation for ducting using Class 1 closed cell elastomeric insulation of 10mm thick Nitrile rubber insulation adhesive, longitudinal transverse joints sealed with adhesive in neat clean manner. Material shall be processed Nitrile Rubber foam with anti-microbial protection. Insulation shall have thermal conductivity of 0.047 W (m.K) and density of 140 - 180 kg m³. | Supply fixing acoustic insulation for ducting using Class 1 closed cell elastomeric insulation of 10mm thick Nitrile rubber insulation adhesive, longitudinal transverse joints sealed with adhesive in neat clean manner. Material shall be processed Nitrile Rubber foam with anti-microbial protection. Insulation shall have thermal conductivity of 0.047 W (m.K) and density of 140 - 180 kg m³. | Sq.mtr | 5 | 5850 | 1170 | 5850 | 1600 | 8000 | 1250 | 6250 | 1550 | 7750
139 |  | Make Armaflex K-flex | Make Armaflex K-flex
140 | 5.3 | THERMAL INSULATION FOR KITCHEN VENTILATION DUCTS | THERMAL INSULATION FOR KITCHEN VENTILATION DUCTS
141 |  | SITC of Glass Fibre Blanket Insulation material bonded with Thrmosetting Resin, with factory applied laminated aluminium foil of 22 micrns with fibre glass backing. Further, wire mesh along with 7 mil cloth shall be applied on above the insulation with proper adhersive. Nominal density 32 Kg CuM. Thermal conductivity, < 0.033 W m.K at 24 degreeC. All Insuation material and adhesives shall be as per Class I for surface spread and in accordance with BS 476, Class O for non-combustible grade. | SITC of Glass Fibre Blanket Insulation material bonded with Thrmosetting Resin, with factory applied laminated aluminium foil of 22 micrns with fibre glass backing. Further, wire mesh along with 7 mil cloth shall be applied on above the insulation with proper adhersive. Nominal density 32 Kg CuM. Thermal conductivity, < 0.033 W m.K at 24 degreeC. All Insuation material and adhesives shall be as per Class I for surface spread and in accordance with BS 476, Class O for non-combustible grade. | Sq.mtr | 55 | 36465 | 663 | 36465 | 1460 | 80300 | 750 | 41250 | 1500 | 82500
142 |  | Make Armaflex K-flex | Make Armaflex K-flex
143 |  | Note | Note
144 | a. | Insulation work to be coordinated with other agencies and repair to be included by contractor as per site requirement. | Insulation work to be coordinated with other agencies and repair to be included by contractor as per site requirement.
145 | b. | Vendors to take care of the installation, if any damages takes place the vendor to repair or replace and hand over to clients in good and acceptable condition. | Vendors to take care of the installation, if any damages takes place the vendor to repair or replace and hand over to clients in good and acceptable condition.
146 | c. | Thermal insulation shall be internal for Elliptical Expossed ducting. | Thermal insulation shall be internal for Elliptical Expossed ducting.
147 |  | SUB-TOTAL | SUB-TOTAL
148 | 6 | ELECTRICAL WORKS | ELECTRICAL WORKS
149 | 6.1 | STARTER PANEL | STARTER PANEL
150 |  | SITC of indoor outdoor, wall mounting type 3PH, 415VAC MOTOR STARTERS IN CRCA SHEET STEEL ENCLOSURE with necssary supporting brackets and required accessories, etc., The Enclosure shall be provided with knockouts suitable for cable termination at TOP BOTTOM for incoming and outgoing power cables of A2XFY type and size specified. The starters shall be complete with suitable MPCB MCCB, Contactor, Bi-metal O L relay with SPP, ON OFF Push buttons, on off trip indication Lamp, on off push button, phase indication Lamp. Selection of relay, contractor, MPCB MCCB etc. as per Type-2 Coordination. Panel shall have provision to connect with BMS. | SITC of indoor outdoor, wall mounting type 3PH, 415VAC MOTOR STARTERS IN CRCA SHEET STEEL ENCLOSURE with necssary supporting brackets and required accessories, etc., The Enclosure shall be provided with knockouts suitable for cable termination at TOP BOTTOM for incoming and outgoing power cables of A2XFY type and size specified. The starters shall be complete with suitable MPCB MCCB, Contactor, Bi-metal O L relay with SPP, ON OFF Push buttons, on off trip indication Lamp, on off push button, phase indication Lamp. Selection of relay, contractor, MPCB MCCB etc. as per Type-2 Coordination. Panel shall have provision to connect with BMS.
151 | a | Suitable for 1500 CFM AHU, DOL Starter Panel | Suitable for 1500 CFM AHU, DOL Starter Panel | No. | 1 | 15000 | 27300 | 27300 | 15000 | 15000 | 18600 | 18600 | 24000 | 24000
152 | 6.2 | POWER CABLING | POWER CABLING
153 |  | Supply, handling, laying effecting proper connections testing and commissioning of following sizes of 1.1 KV grade XLPE insulated FRLS Aluminium Copper conductor cables laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with Copper earthing as specified for continuous earthing along with cable. All complete as required and as per final instruction as given by Owners Consultants and as per Technical specifications. Earthing shall be measured separately and shall be connected in two runs. Power to ELCB to be provided near each ODU by electrical contractor. | Supply, handling, laying effecting proper connections testing and commissioning of following sizes of 1.1 KV grade XLPE insulated FRLS Aluminium Copper conductor cables laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with Copper earthing as specified for continuous earthing along with cable. All complete as required and as per final instruction as given by Owners Consultants and as per Technical specifications. Earthing shall be measured separately and shall be connected in two runs. Power to ELCB to be provided near each ODU by electrical contractor.
154 | a | Suitable Power Cable | Suitable Power Cable
155 |  | Suitable for 1500 CFM AHU, DOL Starter Panel | Suitable for 1500 CFM AHU, DOL Starter Panel | Rmt | 10 | 1950 | 195 | 1950 | 350 | 3500 | 350 | 3500 | 900 | 9000
156 | b | Earthing | Earthing
157 |  | 8 SWG | 8 SWG | Rmt | 20 | 2340 | 117 | 2340 | 220 | 4400 | 150 | 3000 | 120 | 2400
158 | 6.3 | BTU METER | BTU METER
159 |  | Supply,fixing and testing of inline Btu meter for the flow rate temperature measurement consisting mainly of following 3 parts | Supply,fixing and testing of inline Btu meter for the flow rate temperature measurement consisting mainly of following 3 parts
160 |  | a) Ultrasonic Flow Meter | a) Ultrasonic Flow Meter
161 |  | b) Matched pair of temp sensor | b) Matched pair of temp sensor
162 |  | c) Flowcell Sensor | c) Flowcell Sensor
163 |  | c) BTU Meter - 4 - 20mA DC from flowmeter | c) BTU Meter - 4 - 20mA DC from flowmeter
164 |  | Insertion type flowmeter shall be suitable for chilled water application for temp. Ranging from 0 to 50 deg C. Power supply shall be 240V AC (+ -) 15 %. Display shall have 16 characters LCD display with Back light, flow rate, Velocity, totaliser etc. Output shall be BMS Modbus compatible shall have keypad lockout security option. It also should be able to show various units such as gallons, ft^3, lbs, liters, m^3, kg etc | Insertion type flowmeter shall be suitable for chilled water application for temp. Ranging from 0 to 50 deg C. Power supply shall be 240V AC (+ -) 15 %. Display shall have 16 characters LCD display with Back light, flow rate, Velocity, totaliser etc. Output shall be BMS Modbus compatible shall have keypad lockout security option. It also should be able to show various units such as gallons, ft^3, lbs, liters, m^3, kg etc
165 |  | Make Honeywell Danfoss Siemens | Make Honeywell Danfoss Siemens
166 | a | Dia 32 mm | Dia 32 mm | No. | 1 | 9750 | 9750 | 9750 | 45000 | 45000 | 65400 | 65400 | 21000 | 21000
167 | 6.4 | CABLE TERMINATION | CABLE TERMINATION
168 |  | Supply Making of Cable termination of armoured unarmoured cables 1.1 KV grade including installation of cable glands, cable lugs (Aluminium for A2XFY copper for 2XFY YY Double compression type), heat shrinkable sleeves on long ends, crimping paste etc. The work includes testing commissioning of cables, meggaring values submitting reports of tests. (One set includes termination of all cores of one end only). All crimping tools dies shall be arranged by contractor. | Supply Making of Cable termination of armoured unarmoured cables 1.1 KV grade including installation of cable glands, cable lugs (Aluminium for A2XFY copper for 2XFY YY Double compression type), heat shrinkable sleeves on long ends, crimping paste etc. The work includes testing commissioning of cables, meggaring values submitting reports of tests. (One set includes termination of all cores of one end only). All crimping tools dies shall be arranged by contractor.
169 | a | Suitable for 1500 CFM AHU | Suitable for 1500 CFM AHU | No. | 1 | 1600 | 2184 | 2184 | 3000 | 3000 | 2500 | 2500 | 1600 | 1600
170 | 6.5 | CABLE TRAYS | CABLE TRAYS
171 |  | Supplying Fixing of following sizes of GI cable tray duly painted perforated type of height 50mm along with necessary bends, reducers etc. anchored along the wall suspended from the ceiling with necessary MS supports. | Supplying Fixing of following sizes of GI cable tray duly painted perforated type of height 50mm along with necessary bends, reducers etc. anchored along the wall suspended from the ceiling with necessary MS supports.
172 | a | 50mm wide x 50mm x 1.6mm Thick | 50mm wide x 50mm x 1.6mm Thick | Rmt | 10 | 3500 | 355 | 3550 | 480 | 4800 | 350 | 3500 | 1800 | 18000
173 |  | SUB-TOTAL | SUB-TOTAL |  |  |  |  | 675689 |  | 661270 |  | 744700 |  | 798901
174 |  | GRAND TOTAL | GRAND TOTAL |  |  |  |  | 805029 |  | 761270 |  | 839700 |  | 1048901

## Summary
Summary of HVAC work- KFC - AHM
SL NO. | Descricption | FallowDesign | Mahamaya Engineering | Anjle MEP | Pioneer Infra
1 | HVAC Hi Side | 129340 | 100000 | 95000 | 250000
2 | HVAC Low Side | 675689 | 661270 | 744700 | 798901
Total |  | 805029 | 761270 | 839700 | 1048901
GST of HI side |  | 36215.2 | 28000 | 26600 | 70000
GST of Low side |  | 121624.02 | 119028.6 | 134046 | 143802.18
total with GST |  | 962868.22 | 908298.6 | 1000346 | 1262703.18