## Price Comparison
|  | RFQ No: R0541 COST COMPARISON REPORT | RFQ No: R0541 COST COMPARISON REPORT | RFQ No: R0541 COST COMPARISON REPORT | Comp. Date : 29/03/2024 | Comp. Date : 29/03/2024 | Comp. Date : 29/03/2024 | Vendor Name : ANJLE MEP PROJECTS PVT LTD (RV232413533) | [5 empty] | Vendor Name : Arrow Electricals (RV232411833) | [5 empty] | Vendor Name : PIONEER PROJECT SOLUTION (RV232414136)
|  | RFQ No: R0541 COST COMPARISON REPORT | RFQ No: R0541 COST COMPARISON REPORT | RFQ No: R0541 COST COMPARISON REPORT | RFQ #: R0541 | RFQ #: R0541 | RFQ #: R0541 | Contact Name : Priyanka/Premkant Rajpoot | [5 empty] | Contact Name : | [5 empty] | Contact Name : Mohd Ashraf
|  | RFQ No: R0541 COST COMPARISON REPORT | RFQ No: R0541 COST COMPARISON REPORT | RFQ No: R0541 COST COMPARISON REPORT | RFQ Date : 26/03/2024 10:57:56 | RFQ Date : 26/03/2024 10:57:56 | RFQ Date : 26/03/2024 10:57:56 | Vendor City : | [5 empty] | Vendor City : | [5 empty] | Vendor City :
|  | RFQ No: R0541 COST COMPARISON REPORT | RFQ No: R0541 COST COMPARISON REPORT | RFQ No: R0541 COST COMPARISON REPORT | BCD Date : 28/03/2024 18:18:00 | BCD Date : 28/03/2024 18:18:00 | BCD Date : 28/03/2024 18:18:00 | Telephone # : | [5 empty] | Telephone # : | [5 empty] | Telephone # :
|  | RFQ No: R0541 COST COMPARISON REPORT | RFQ No: R0541 COST COMPARISON REPORT | RFQ No: R0541 COST COMPARISON REPORT |  |  |  | Mobile # : | [5 empty] | Mobile # : | [5 empty] | Mobile # :
PR Number : TFSPL-2324-00358 | PR Number : TFSPL-2324-00358 | PR Number : TFSPL-2324-00358 | PR Number : TFSPL-2324-00358 | PR Number : TFSPL-2324-00358 | PR Number : TFSPL-2324-00358 | PR Number : TFSPL-2324-00358 | PR Number : TFSPL-2324-00358 | Email : anjlemepprojects@gmail.com | [5 empty] | Email : khakesantosh10@gmail.com | [5 empty] | Email : projectspioneer@gmail.com
Package / RFQ Name : FAS work - International Food Hall - Delhi | Package / RFQ Name : FAS work - International Food Hall - Delhi | Package / RFQ Name : FAS work - International Food Hall - Delhi | Package / RFQ Name : FAS work - International Food Hall - Delhi | Package / RFQ Name : FAS work - International Food Hall - Delhi | Package / RFQ Name : FAS work - International Food Hall - Delhi | Package / RFQ Name : FAS work - International Food Hall - Delhi | Package / RFQ Name : FAS work - International Food Hall - Delhi | Round # : 4 (RFQ) | [5 empty] | Round # : 4 (RFQ) | [5 empty] | Round # : 4 (RFQ)
Buyer : Binu Balachandran / Technical : / Approver : | Buyer : Binu Balachandran / Technical : / Approver : | Buyer : Binu Balachandran / Technical : / Approver : | Buyer : Binu Balachandran / Technical : / Approver : | Buyer : Binu Balachandran / Technical : / Approver : | Buyer : Binu Balachandran / Technical : / Approver : | Buyer : Binu Balachandran / Technical : / Approver : | Buyer : Binu Balachandran / Technical : / Approver : | Quotation Date : |  |  | Quotation Validity Date : |  |  | Quotation Date : |  |  | Quotation Validity Date : |  |  | Quotation Date : |  |  | Quotation Validity Date :
Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Currency :INR | Currency :INR | Currency :INR | Buyer Remark : . | [5 empty] | Buyer Remark : | [5 empty] | Buyer Remark :
Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | BUDGET PRICE : | .00 |  | Quote Currency : INR | [5 empty] | Quote Currency : INR | [5 empty] | Quote Currency : INR
# | Item Code | Item Description | Unit | Qty | Last PO Details | Lowest Unit Rate | Lowest Vendor | First Bid | Disc % | GST % | Technical | Unit Price | Total | First Bid | Disc % | GST % | Technical | Unit Price | Total | First Bid | Disc % | GST % | Technical | Unit Price | Total
1 |  | FAS | NOS | 1.00 |  | 233125.00 | ANJLE MEP PROJECTS PVT LTD | 233125.00 | 0.00 | 18.00 |  | 233,125.00 | 233,125.00 | 236318.00 | 0.00 | 18.00 |  | 236,318.00 | 236,318.00 | 283350.00 | 0.00 | 18.00 |  | 283,350.00 | 283,350.00
Item Total | [8 empty] | .00 | 41,962.50 |  |  | 233,125.00 |  | .00 | 42,537.24 |  |  | 236,318.00 |  | .00 | 51,003.00 |  |  | 283,350.00
Discount Total Value | [7 empty] | Grand Dis. Amt | .00 |  |  |  | .00 | Grand Dis. Amt | .00 |  |  |  | .00 | Grand Dis. Amt | .00 |  |  |  | .00
GST Total Amount | [12 empty] | 41,962.50 | [5 empty] | 42,537.24 | [5 empty] | 51,003.00
Net Landed Cost | [11 empty] | INR | 275,087.50 |  |  |  |  | INR | 278,855.24 |  |  |  |  | INR | 334,353.00
Vendor Status | [7 empty] | Round # : 4 (RFQ) | Round # : 4 (RFQ)
Sr No. | Vendor Code | Vendor Name | [5 empty] | Status | Remarks
1 | RV232414692 | Dear Infra | [5 empty] | Participate
2 | RV232414136 | PIONEER PROJECT SOLUTION | [5 empty] | Participate
3 | RV232413533 | ANJLE MEP PROJECTS PVT LTD | [5 empty] | Participate
4 | RV232412099 | Electech Enterprises | [5 empty] | Not Participate
5 | RV232411833 | Arrow Electricals | [5 empty] | Participate
6 | RV232421261 | Rudra Ineriors | [5 empty] | Not Participate

## BOQ Price Bid
|  | RFQ No: R0541 COST COMPARISON REPORT | RFQ No: R0541 COST COMPARISON REPORT | Comp. Date : 29/03/2024 | Comp. Date : 29/03/2024 | Comp. Date : 29/03/2024 | Vendor Name : ANJLE MEP PROJECTS PVT LTD | Vendor Name : ANJLE MEP PROJECTS PVT LTD | Vendor Name : Arrow Electricals | Vendor Name : Arrow Electricals | Vendor Name : PIONEER PROJECT SOLUTION | Vendor Name : PIONEER PROJECT SOLUTION
|  | RFQ No: R0541 COST COMPARISON REPORT | RFQ No: R0541 COST COMPARISON REPORT | RFQ #: R0541 | RFQ #: R0541 | RFQ #: R0541 | Contact Name : Priyanka/Premkant Rajpoot | Contact Name : Priyanka/Premkant Rajpoot | Contact Name : | Contact Name : | Contact Name : Mohd Ashraf | Contact Name : Mohd Ashraf
|  | RFQ No: R0541 COST COMPARISON REPORT | RFQ No: R0541 COST COMPARISON REPORT | RFQ Date : 26/03/2024 10:57:56 | RFQ Date : 26/03/2024 10:57:56 | RFQ Date : 26/03/2024 10:57:56 | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City :
|  | RFQ No: R0541 COST COMPARISON REPORT | RFQ No: R0541 COST COMPARISON REPORT | BCD Date : 28/03/2024 18:18:00 | BCD Date : 28/03/2024 18:18:00 | BCD Date : 28/03/2024 18:18:00 | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # :
|  | RFQ No: R0541 COST COMPARISON REPORT | RFQ No: R0541 COST COMPARISON REPORT |  |  |  | Mobile # : | Mobile # : | Mobile # : | Mobile # : | Mobile # : | Mobile # :
PR Number : TFSPL-2324-00358 | PR Number : TFSPL-2324-00358 | PR Number : TFSPL-2324-00358 | PR Number : TFSPL-2324-00358 | PR Number : TFSPL-2324-00358 | PR Number : TFSPL-2324-00358 | PR Number : TFSPL-2324-00358 | Email : anjlemepprojects@gmail.com | Email : anjlemepprojects@gmail.com | Email : khakesantosh10@gmail.com | Email : khakesantosh10@gmail.com | Email : projectspioneer@gmail.com | Email : projectspioneer@gmail.com
Package / RFQ Name : FAS work - International Food Hall - Delhi | Package / RFQ Name : FAS work - International Food Hall - Delhi | Package / RFQ Name : FAS work - International Food Hall - Delhi | Package / RFQ Name : FAS work - International Food Hall - Delhi | Package / RFQ Name : FAS work - International Food Hall - Delhi | Package / RFQ Name : FAS work - International Food Hall - Delhi | Package / RFQ Name : FAS work - International Food Hall - Delhi | Round # : 4 (RFQ) | Round # : 4 (RFQ) | Round # : 4 (RFQ) | Round # : 4 (RFQ) | Round # : 4 (RFQ) | Round # : 4 (RFQ)
Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score :
Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Currency :INR | Currency :INR | Currency :INR | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date :
Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | BUDGET PRICE :.00 | BUDGET PRICE :.00 | BUDGET PRICE :.00 | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date :
Sr No. | Item Code | Item Name | Item Description | UOM | Qty | Minimum Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount
1 |  | FAS | FAS | NOS | 1.000 |  |  | 233,125.00 |  | 236,318.00 |  | 283,350.00
1 | 13 | FIRE ALARM SYSTEM (MAKE EST-3) | FIRE ALARM SYSTEM (MAKE EST-3)
2 | 13.1 | Single Loop Analog Addressable Fire Alarm Control panel (Expandable upto 1 Loop) with battery back up for 4 hours normal operation and 15 minutes alarm operation. The control panel per Loop Capacity 250 Detectrs and Devices, battery charger etc., 8.5 Touch Screen LCD Display, TCP IP Connectivity, 10000 Event Log, Keyless Log on Using RFID Cards. The panel shall be UL listed and preferably FM approved with response time less than 10sec. Installation of fire alarm system shall be done as per IS 2189 or relevant NFPA standard.The panel shall have the web enabled facility which can able to send or receive e-mails with memory of 1000 events recording.Note The vendor shall provide panel UL 9th edition listing certificate. (Make Edwards Honeywell) | Single Loop Analog Addressable Fire Alarm Control panel (Expandable upto 1 Loop) with battery back up for 4 hours normal operation and 15 minutes alarm operation. The control panel per Loop Capacity 250 Detectrs and Devices, battery charger etc., 8.5 Touch Screen LCD Display, TCP IP Connectivity, 10000 Event Log, Keyless Log on Using RFID Cards. The panel shall be UL listed and preferably FM approved with response time less than 10sec. Installation of fire alarm system shall be done as per IS 2189 or relevant NFPA standard.The panel shall have the web enabled facility which can able to send or receive e-mails with memory of 1000 events recording.Note The vendor shall provide panel UL 9th edition listing certificate. (Make Edwards Honeywell) | Nos | 0.000 | .00 | 0.00 | .00 | 145000.00 | .00 | 0.00 | .00
3 |  | i) Each loop with Min. 99 Devices + 99 Detectors modules connection capability of Addressable FACP) 2 Loop Pannel. | i) Each loop with Min. 99 Devices + 99 Detectors modules connection capability of Addressable FACP) 2 Loop Pannel.
4 |  | ii) FACP with all in-built modules displays. | ii) FACP with all in-built modules displays.
5 |  | iii) 240 volts AC power supply, automatic battery charger, 24 volts sealed lead acid batteries sufficient for 4 hours normal working. | iii) 240 volts AC power supply, automatic battery charger, 24 volts sealed lead acid batteries sufficient for 4 hours normal working.
6 |  | iv) Programming setting up | iv) Programming setting up
7 |  | v) system to be capable of operating the system for 2 hours during an emergency condition including all necessary software for remote programming of fire alarm system through central control station. | v) system to be capable of operating the system for 2 hours during an emergency condition including all necessary software for remote programming of fire alarm system through central control station.
8 |  | vi) As the number of hooters are 43, additional power supplies to be provided as required. | vi) As the number of hooters are 43, additional power supplies to be provided as required.
9 |  | Necessary Integration Facility with BMS for following functions - | Necessary Integration Facility with BMS for following functions -
10 |  | Alarm, Trouble condition,Supervisory alerts to BMS | Alarm, Trouble condition,Supervisory alerts to BMS
11 |  | Share Graphics of Security, Fire and HVAC | Share Graphics of Security, Fire and HVAC
12 |  | Fire alarm Addressable control panel (1 Loop) | Fire alarm Addressable control panel (1 Loop)
13 | 13.2 | Active Repeater Panel with 8.5 Touch Screen TFT display with TCP IP Eable Repeater Panel shall monitor and control (Scroll, Acknowledge, Reset Mute) all the events of the FACP to which it is connected and it shall have Port Vectoring Event Filtering capability of showing only ALARMS, TROUBLES or SUPERVISORY or customized combinations of user selected events. | Active Repeater Panel with 8.5 Touch Screen TFT display with TCP IP Eable Repeater Panel shall monitor and control (Scroll, Acknowledge, Reset Mute) all the events of the FACP to which it is connected and it shall have Port Vectoring Event Filtering capability of showing only ALARMS, TROUBLES or SUPERVISORY or customized combinations of user selected events. | Nos | 0.000 | .00 | 0.00 | .00 | 95500.00 | .00 | 0.00 | .00
14 |  | Supply installation and testing of signal loop components in a suitable galvanised steel junction box. | Supply installation and testing of signal loop components in a suitable galvanised steel junction box.
15 | 13.3 | Detectors and Devices | Detectors and Devices
16 |  | Supply,Installation,Testing Commissioning of Analogue Addressable Monitor module having Rotary, decimal addressing system for monitoring the field devices shall be capable of providing DPDTcontact rated at 24V DC, 2A. | Supply,Installation,Testing Commissioning of Analogue Addressable Monitor module having Rotary, decimal addressing system for monitoring the field devices shall be capable of providing DPDTcontact rated at 24V DC, 2A. | Nos | 0.000 | .00 | 0.00 | .00 | 4550.00 | .00 | 0.00 | .00
17 |  | Supply,Installation,Testing Commissioning of Analogue Addressable Relay module having Rotary, decimal addressing system for AHU tripping and shall be capable of providing DPDTcontact rated at 24v DC, 2A. | Supply,Installation,Testing Commissioning of Analogue Addressable Relay module having Rotary, decimal addressing system for AHU tripping and shall be capable of providing DPDTcontact rated at 24v DC, 2A. | Nos | 0.000 | .00 | 7250.00 | .00 | 4450.00 | .00 | 6500.00 | .00
18 |  | (For all AHU s, Fans Acess Control) | (For all AHU s, Fans Acess Control)
19 |  | Supply,Installation,Testing Commissioning of Horn Strobe rated at 82 dBA @ 3m for Audible annunciation and 75cd flashing at 1 Hz for visual indication with Control modules and necessary accessories including back box. | Supply,Installation,Testing Commissioning of Horn Strobe rated at 82 dBA @ 3m for Audible annunciation and 75cd flashing at 1 Hz for visual indication with Control modules and necessary accessories including back box. | Nos | 0.000 | .00 | 8250.00 | .00 | 7290.00 | .00 | 6200.00 | .00
20 |  | Supply,Installation,Testing Commissioning of Analogue Addressable Flash scan Type Photoelectric smoke detectors( Below False Ceiling) having Rotary, decimal addressing system with standard base, built in isolation function and junction box. The detector shall be capable to address in the range of 1-159. The detector shall be with Visible bi-color LEDs for 360 deg viewing and shall blink green every time the detector is addressed, and illuminate steady red on alarm. | Supply,Installation,Testing Commissioning of Analogue Addressable Flash scan Type Photoelectric smoke detectors( Below False Ceiling) having Rotary, decimal addressing system with standard base, built in isolation function and junction box. The detector shall be capable to address in the range of 1-159. The detector shall be with Visible bi-color LEDs for 360 deg viewing and shall blink green every time the detector is addressed, and illuminate steady red on alarm. | Nos | 0.000 | .00 | 0.00 | .00 | 4550.00 | .00 | 0.00 | .00
21 |  | Supply,Installation,Testing Commissioning of Analogue Addressable Flash scan Type Photoelectric smoke detectors (Above False Ceiling) having Rotary, decimal addressing system with standard base, built in isolation function and junction box. The detector shall be capable to address in the range of 1-159. The detector shall be with Visible bi-color LEDs for 360 deg viewing and shall blink green every time the detector is addressed, and illuminate steady red on alarm. | Supply,Installation,Testing Commissioning of Analogue Addressable Flash scan Type Photoelectric smoke detectors (Above False Ceiling) having Rotary, decimal addressing system with standard base, built in isolation function and junction box. The detector shall be capable to address in the range of 1-159. The detector shall be with Visible bi-color LEDs for 360 deg viewing and shall blink green every time the detector is addressed, and illuminate steady red on alarm. | Nos | 0.000 | .00 | 0.00 | .00 | 4730.00 | .00 | 0.00 | .00
22 |  | Supply,Installation,Testing Commissioning of Analogue Addressable Flash scan Type Photoelectric Multi Sensor detectors having Rotary, decimal addressing system with standard base, built in isolation function and junction box. The detector shall be capable to address in the range of 1-159. The detector shall be with Visible bi-color LEDs for 360 deg viewing and shall blink green every time the detector is addressed, and illuminate steady red on alarm. (Make- Edward-SIGA PHD) | Supply,Installation,Testing Commissioning of Analogue Addressable Flash scan Type Photoelectric Multi Sensor detectors having Rotary, decimal addressing system with standard base, built in isolation function and junction box. The detector shall be capable to address in the range of 1-159. The detector shall be with Visible bi-color LEDs for 360 deg viewing and shall blink green every time the detector is addressed, and illuminate steady red on alarm. (Make- Edward-SIGA PHD) | Nos | 23.000 | 113,850.00 | 4950.00 | 113,850.00 | 5350.00 | 123,050.00 | 6200.00 | 142,600.00
23 |  | Supply,Installation,Testing Commissioning of Analogue Addressable Flash scan Type Heat Detector having Rotary, decimal addressing system with standard base, built in isolation function and junction box. The detector shall be capable to address in the range of 1-159. The detector shall be with Visible bi-color LEDs for 360 deg viewing and shall blink green every time the detector is addressed, and illuminate steady red on alarm. (Make- Edward-EST-SIGA-HFS) | Supply,Installation,Testing Commissioning of Analogue Addressable Flash scan Type Heat Detector having Rotary, decimal addressing system with standard base, built in isolation function and junction box. The detector shall be capable to address in the range of 1-159. The detector shall be with Visible bi-color LEDs for 360 deg viewing and shall blink green every time the detector is addressed, and illuminate steady red on alarm. (Make- Edward-EST-SIGA-HFS) | Nos | 3.000 | 15,150.00 | 5050.00 | 15,150.00 | 5230.00 | 15,690.00 | 6600.00 | 19,800.00
24 |  | Supply,Installation,Testing Commissioning of Addressable Break Glass Manual Call Point having Rotary, decimal addressing system and having an integrally mounted addressable module that monitors and reports contact status. | Supply,Installation,Testing Commissioning of Addressable Break Glass Manual Call Point having Rotary, decimal addressing system and having an integrally mounted addressable module that monitors and reports contact status. | Nos | 3.000 | 17,340.00 | 5950.00 | 17,850.00 | 5780.00 | 17,340.00 | 5800.00 | 17,400.00
25 | 13.4 | SITC of Fault Isolator. | SITC of Fault Isolator. | Nos | 6.000 | 25,338.00 | 5950.00 | 35,700.00 | 4223.00 | 25,338.00 | 6000.00 | 36,000.00
26 | 13.5 | SITC of 2Cx1.5sq.mm multistranded FRLSZH Cu. Armoured for RED Colour,Mylan Shielded Screened cable. (Make-Polycab) For SLC. | SITC of 2Cx1.5sq.mm multistranded FRLSZH Cu. Armoured for RED Colour,Mylan Shielded Screened cable. (Make-Polycab) For SLC. | Mtrs | 275.000 | 33,000.00 | 145.00 | 39,875.00 | 120.00 | 33,000.00 | 180.00 | 49,500.00
27 | 13.6 | SITC of 2Cx2.5sq.mm multistranded FRLSZH Cu. Armoured for RED Colour,Mylan Shielded Screened cable. (Make-Polycab) For NAC. | SITC of 2Cx2.5sq.mm multistranded FRLSZH Cu. Armoured for RED Colour,Mylan Shielded Screened cable. (Make-Polycab) For NAC. | Mtrs | 30.000 | 4,650.00 | 165.00 | 4,950.00 | 155.00 | 4,650.00 | 180.00 | 5,400.00
28 | 13.7 | Response indicator. (Make- Edwards-SIGA-LED) | Response indicator. (Make- Edwards-SIGA-LED) | Nos | 23.000 | 5,750.00 | 250.00 | 5,750.00 | 750.00 | 17,250.00 | 550.00 | 12,650.00

## Technical Score Detail
|  | RFQ No: R0541 COST COMPARISON REPORT | RFQ No: R0541 COST COMPARISON REPORT | RFQ No: R0541 COST COMPARISON REPORT | Comp. Date : 29/03/2024 | Comp. Date : 29/03/2024 | Comp. Date : 29/03/2024 | Vendor Name : ANJLE MEP PROJECTS PVT LTD |  | Vendor Name : Arrow Electricals |  | Vendor Name : PIONEER PROJECT SOLUTION
|  | RFQ No: R0541 COST COMPARISON REPORT | RFQ No: R0541 COST COMPARISON REPORT | RFQ No: R0541 COST COMPARISON REPORT | RFQ #: R0541 | RFQ #: R0541 | RFQ #: R0541 | Contact Name : Priyanka/Premkant Rajpoot |  | Contact Name : |  | Contact Name : Mohd Ashraf
|  | RFQ No: R0541 COST COMPARISON REPORT | RFQ No: R0541 COST COMPARISON REPORT | RFQ No: R0541 COST COMPARISON REPORT | RFQ Date : 26/03/2024 10:57:56 | RFQ Date : 26/03/2024 10:57:56 | RFQ Date : 26/03/2024 10:57:56 | Vendor City : |  | Vendor City : |  | Vendor City :
|  | RFQ No: R0541 COST COMPARISON REPORT | RFQ No: R0541 COST COMPARISON REPORT | RFQ No: R0541 COST COMPARISON REPORT | BCD Date : 28/03/2024 18:18:00 | BCD Date : 28/03/2024 18:18:00 | BCD Date : 28/03/2024 18:18:00 | Telephone # : |  | Telephone # : |  | Telephone # :
|  | RFQ No: R0541 COST COMPARISON REPORT | RFQ No: R0541 COST COMPARISON REPORT | RFQ No: R0541 COST COMPARISON REPORT |  |  |  | Mobile # : |  | Mobile # : |  | Mobile # :
PR Number : TFSPL-2324-00358 | PR Number : TFSPL-2324-00358 | PR Number : TFSPL-2324-00358 | PR Number : TFSPL-2324-00358 | PR Number : TFSPL-2324-00358 | PR Number : TFSPL-2324-00358 | PR Number : TFSPL-2324-00358 | PR Number : TFSPL-2324-00358 | Email : anjlemepprojects@gmail.com |  | Email : khakesantosh10@gmail.com |  | Email : projectspioneer@gmail.com
Package / RFQ Name : FAS work - International Food Hall - Delhi | Package / RFQ Name : FAS work - International Food Hall - Delhi | Package / RFQ Name : FAS work - International Food Hall - Delhi | Package / RFQ Name : FAS work - International Food Hall - Delhi | Package / RFQ Name : FAS work - International Food Hall - Delhi | Package / RFQ Name : FAS work - International Food Hall - Delhi | Package / RFQ Name : FAS work - International Food Hall - Delhi | Package / RFQ Name : FAS work - International Food Hall - Delhi | Round # : 4 (RFQ) |  | Round # : 4 (RFQ) |  | Round # : 4 (RFQ)
Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Buyer : Binu Balachandran | Quotation Date : |  | Quotation Date : |  | Quotation Date :
Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Currency :INR | Currency :INR | Currency :INR | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date :
Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | Comp. # : 4 | BUDGET PRICE : | .00 |  | Quote Currency : |  | Quote Currency : |  | Quote Currency :
# | Item Code | Item Description | Last PO Details | Unit | Qty | Last PO Unit Rate | Last PO Total Value | Score | Justification | Score | Justification | Score | Justification
1 |  | FAS |  | NOS | 1.000 | 0.00 | 0.00
2 | 13 | FIRE ALARM SYSTEM (MAKE EST-3) |  |  | 0.000 | 0.00 | 0.00
3 | 13.1 | Single Loop Analog Addressable Fire Alarm Control panel (Expandable upto 1 Loop) with battery back up for 4 hours normal operation and 15 minutes alarm operation. The control panel per Loop Capacity 250 Detectrs and Devices, battery charger etc., 8.5 Touch Screen LCD Display, TCP IP Connectivity, 10000 Event Log, Keyless Log on Using RFID Cards. The panel shall be UL listed and preferably FM approved with response time less than 10sec. Installation of fire alarm system shall be done as per IS 2189 or relevant NFPA standard.The panel shall have the web enabled facility which can able to send or receive e-mails with memory of 1000 events recording.Note The vendor shall provide panel UL 9th edition listing certificate. (Make Edwards Honeywell) |  | Nos | 0.000 | 0.00 | 0.00
4 |  | i) Each loop with Min. 99 Devices + 99 Detectors modules connection capability of Addressable FACP) 2 Loop Pannel. |  |  | 0.000 | 0.00 | 0.00
5 |  | ii) FACP with all in-built modules displays. |  |  | 0.000 | 0.00 | 0.00
6 |  | iii) 240 volts AC power supply, automatic battery charger, 24 volts sealed lead acid batteries sufficient for 4 hours normal working. |  |  | 0.000 | 0.00 | 0.00
7 |  | iv) Programming setting up |  |  | 0.000 | 0.00 | 0.00
8 |  | v) system to be capable of operating the system for 2 hours during an emergency condition including all necessary software for remote programming of fire alarm system through central control station. |  |  | 0.000 | 0.00 | 0.00
9 |  | vi) As the number of hooters are 43, additional power supplies to be provided as required. |  |  | 0.000 | 0.00 | 0.00
10 |  | Necessary Integration Facility with BMS for following functions - |  |  | 0.000 | 0.00 | 0.00
11 |  | Alarm, Trouble condition,Supervisory alerts to BMS |  |  | 0.000 | 0.00 | 0.00
12 |  | Share Graphics of Security, Fire and HVAC |  |  | 0.000 | 0.00 | 0.00
13 |  | Fire alarm Addressable control panel (1 Loop) |  |  | 0.000 | 0.00 | 0.00
14 | 13.2 | Active Repeater Panel with 8.5 Touch Screen TFT display with TCP IP Eable Repeater Panel shall monitor and control (Scroll, Acknowledge, Reset Mute) all the events of the FACP to which it is connected and it shall have Port Vectoring Event Filtering capability of showing only ALARMS, TROUBLES or SUPERVISORY or customized combinations of user selected events. |  | Nos | 0.000 | 0.00 | 0.00
15 |  | Supply installation and testing of signal loop components in a suitable galvanised steel junction box. |  |  | 0.000 | 0.00 | 0.00
16 | 13.3 | Detectors and Devices |  |  | 0.000 | 0.00 | 0.00
17 |  | Supply,Installation,Testing Commissioning of Analogue Addressable Monitor module having Rotary, decimal addressing system for monitoring the field devices shall be capable of providing DPDTcontact rated at 24V DC, 2A. |  | Nos | 0.000 | 0.00 | 0.00
18 |  | Supply,Installation,Testing Commissioning of Analogue Addressable Relay module having Rotary, decimal addressing system for AHU tripping and shall be capable of providing DPDTcontact rated at 24v DC, 2A. |  | Nos | 0.000 | 0.00 | 0.00
19 |  | (For all AHU s, Fans Acess Control) |  |  | 0.000 | 0.00 | 0.00
20 |  | Supply,Installation,Testing Commissioning of Horn Strobe rated at 82 dBA @ 3m for Audible annunciation and 75cd flashing at 1 Hz for visual indication with Control modules and necessary accessories including back box. |  | Nos | 0.000 | 0.00 | 0.00
21 |  | Supply,Installation,Testing Commissioning of Analogue Addressable Flash scan Type Photoelectric smoke detectors( Below False Ceiling) having Rotary, decimal addressing system with standard base, built in isolation function and junction box. The detector shall be capable to address in the range of 1-159. The detector shall be with Visible bi-color LEDs for 360 deg viewing and shall blink green every time the detector is addressed, and illuminate steady red on alarm. |  | Nos | 0.000 | 0.00 | 0.00
22 |  | Supply,Installation,Testing Commissioning of Analogue Addressable Flash scan Type Photoelectric smoke detectors (Above False Ceiling) having Rotary, decimal addressing system with standard base, built in isolation function and junction box. The detector shall be capable to address in the range of 1-159. The detector shall be with Visible bi-color LEDs for 360 deg viewing and shall blink green every time the detector is addressed, and illuminate steady red on alarm. |  | Nos | 0.000 | 0.00 | 0.00
23 |  | Supply,Installation,Testing Commissioning of Analogue Addressable Flash scan Type Photoelectric Multi Sensor detectors having Rotary, decimal addressing system with standard base, built in isolation function and junction box. The detector shall be capable to address in the range of 1-159. The detector shall be with Visible bi-color LEDs for 360 deg viewing and shall blink green every time the detector is addressed, and illuminate steady red on alarm. (Make- Edward-SIGA PHD) |  | Nos | 23.000 | 0.00 | 0.00
24 |  | Supply,Installation,Testing Commissioning of Analogue Addressable Flash scan Type Heat Detector having Rotary, decimal addressing system with standard base, built in isolation function and junction box. The detector shall be capable to address in the range of 1-159. The detector shall be with Visible bi-color LEDs for 360 deg viewing and shall blink green every time the detector is addressed, and illuminate steady red on alarm. (Make- Edward-EST-SIGA-HFS) |  | Nos | 3.000 | 0.00 | 0.00
25 |  | Supply,Installation,Testing Commissioning of Addressable Break Glass Manual Call Point having Rotary, decimal addressing system and having an integrally mounted addressable module that monitors and reports contact status. |  | Nos | 3.000 | 0.00 | 0.00
26 | 13.4 | SITC of Fault Isolator. |  | Nos | 6.000 | 0.00 | 0.00
27 | 13.5 | SITC of 2Cx1.5sq.mm multistranded FRLSZH Cu. Armoured for RED Colour,Mylan Shielded Screened cable. (Make-Polycab) For SLC. |  | Mtrs | 275.000 | 0.00 | 0.00
28 | 13.6 | SITC of 2Cx2.5sq.mm multistranded FRLSZH Cu. Armoured for RED Colour,Mylan Shielded Screened cable. (Make-Polycab) For NAC. |  | Mtrs | 30.000 | 0.00 | 0.00
29 | 13.7 | Response indicator. (Make- Edwards-SIGA-LED) |  | Nos | 23.000 | 0.00 | 0.00