## BOQ Price Bid
[5 empty] | Vendor Name : | Vendor Name : Arrow Electricals
Sr No. | Item Code | Item Name | UOM | Qty | Unit Price | Amount
1 |  | Electrical | NOS | 1 |  | 1097090
1 | 1 | PANELS, SWITCHGEARS DISTRIBUTION BOARD
2 | 1.1 | MAIN PANEL-1 | Nos. | 1 | 250000 | 250000
3 |  | Incomer 125 AMPS 4P MCCB, 25kA with TM Based O C SC Release.
4 |  | Meter Protection ELR with CBCT; 150 5A, 15VA, CL-1 CT s -3 Nos. for Schneider make Digital Load Manager (EM 6400 NG)
5 |  | Indication Phase indicating lamps with 6A MCB
6 |  | Busbar 150A TPN Cu Busbar
7 |  | Outgoings
8 |  | a) 40A 4P MCB, 10kA, TM BASED-3 Nos.
9 |  | b) 32A 4P MCB, 10kA, TM BASED-4 Nos.
10 |  | c) 40A SP MCB, 10kA, TM BASED-2 Nos.
11 |  | d) 32A SP MCB, 10kA, TM BASED-5 Nos.
12 |  | e) 20A SP MCB, 10kA, TM BASED-5 Nos.
13 |  | f) 16A SP MCB, 10kA, TM BASED-13 Nos.
14 |  | g) 10A SP MCB, 10kA, TM BASED-4 Nos.
15 |  | h) 6A SP MCB, 10kA, TM BASED-10 Nos.
16 | 2.2 | DISTRIBUTION BOARDS
17 |  | 6 WAY TPN PPI DB - LPDB DB | Nos. | 1 | 18000 | 18000
18 |  | Incomer 40A FP MCB 10KA 1 Nos.
19 |  | Sub- Outgoings 25 A DP RCCB 30mA- 3 Nos.
20 |  | Outgoings 6 10 16 A SP MCB B Type - 12 Nos.
21 | 2 | MV CABLES
22 | 2.1 | POWER CABLING
23 |  | Supply and laying, effecting proper connections, testing commissioning of the following sizes of 1.1 KV XLPE FRLS armoured unarmoured PVC insulated PVC sheathed aluminium copper conductor cables conforming to IS 1554 and IS 694 for Flexible copp
24 |  | Aluminium cables
25 |  | 3.5C x 70 Sq.mm. | Mtr. | 40 | 510 | 20400
26 | 2.2 | CABLE TERMINATION
27 |  | Making cable and terminations including brass single compression glands and crimping type copper lugs for cable sizes mentioned below for aluminium or copper.
28 |  | 3.5C x 70 Sq.mm. AL | Nos. | 2 | 2000 | 4000
29 | 3 | RACEWAYS AND CABLE TRAYS
30 | 3.4 | CABLE TRAY Design manufacture , supply and fixing in position the cable trays of the following sizes for supporting 1.1 KV grade armoured unarmoured aluminium copper conductor cables. Fabricate the cable trays from perforated 1.6 2mm thick M.S. CRCA she
31 |  | 150 mm wide x 50 mm x 2.0 mm thk | Mtr. | 30 | 500 | 15000
32 | 4 | POINT WIRING
33 |  | Point wiring LENGTH from DB to SB or First Light point control be MCB shall be avg. of 15Mtr. of 3C x 2.5 sq mm FRLS PVC insulated stranded copper conductor wires. For SB to SB the length shall be measured in Mtr.
34 |  | The secondary Loop point length shall be 10Mtr from Light fixture to light fixture. If secondary point shall be operated from MCB then the length shall be 10 Mtr.
35 |  | All sockets to be checked with a Check Plug socket tester for live-neutral reverse, no earth,neutral fault, live earth reverse, neutral earth reverse.
36 |  | The Circuit No. and DB no. label shall be provided on all UPS ,RAW sockets and switchboards with label printer.
37 |  | The Length shall be paid as per the actual measurements as per following manner.
38 | 4.1 | Wiring for the Primary light points with 3C x 2.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in GI conduits in F.ceiling walls ceiling as direc­ted from Distribution Board to Switch Board including providing 6 amps flush type switches, 5
39 |  | From DB to Normal Switch Board | Nos. | 3 | 2200 | 6600
40 |  | From DB to Emergency Switch Board | Nos. | 1 | 2200 | 2200
41 | 4.2 | Wiring for the following light points with 3 x 2.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in GI conduits in F.ceiling walls ceiling as direc­ted including providing 6 amps flush type switches, 5 sided G.I Boxes for housing switc­hes a
42 |  | First point controlled by one no. 6 amp switch. (upto 10Mtr.) | Nos. | 7 | 1800 | 12600
43 |  | First point controlled by one no. 6 amp switch. For Emergency Light (upto 10Mtr.) | Nos. | 8 | 1800 | 14400
44 | 4.3 | Same as item No. 4.2.1 4.2.2 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS PVC insulated copper conductor wire in concealed exposed GI conduit and earthing | Nos. | 4 | 1200 | 4800
45 | 4.4 | Same as item No. 4.2.3 4.2.4 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS PVC insulated copper conductor wire in concealed exposed GI conduit and earthing For Emergency Light | Nos. | 4 | 1200 | 4800
46 | 4.5 | Wiring for the following light points controlled by MCB in DB (Cost of MCB has been taken elsewhere in the tender) with 3C x 2.5 sq. mm FRLS PVC insulated copper conductor wires in concealed exposed GI conduits as called for and earthing.
47 |  | First point controlled by existing MCB in D.B. | Nos. | 9 | 2200 | 19800
48 | 4.6 | Same as item No.4.5.1 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS. insulated copper conductor wire in concealed exposed GI conduit and earthing | Nos. | 76 | 1200 | 91200
49 | 4.8 | Wiring for UPS Raw plug outlets points with 3C x 4 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS 694-1990 with latest amendments, in existing Channels con | Mtr. | 654 | 230 | 150420
50 | 4.9 | Wiring for UPS Raw plug outlets points with 4C x 4 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS 694-1990 with latest amendments, in existing Channels con | Mtr. | 400 | 300 | 120000
51 | 4.1 | Providing and fixing in position the following GI RIGID conduits including all accessories concealed in F. ceiling wall floor as required including pull boxes with 3mm thick perspex sheet cover plate complete with 1.6 mm dia. G.I. pull wires in the leng
52 |  | 20 mm dia GI Conduit | Mtr. | 1200 | 140 | 168000
53 |  | 25 mm dia GI Conduit | Mtr. | 300 | 160 | 48000
54 | 5 | MODULAR SWITCHES
55 | 5.1 | Supply, installation, testing commissioning of following types of modular switches, cover plates, 5 sided G.I. Boxes for housing the modular switches earthing complete as required. GI Boxes to have earth pin for body earthing. The Circuit No. and DB n
56 |  | 6A One Way Switch | Nos. | 36 | 150 | 5400
57 |  | 6A 5 pin Socket - 1Nos. 6A Switch - 1Nos. | Nos. | 22 | 400 | 8800
58 |  | 6 16A Socket outlet - 1Nos. 16A Switch - 1Nos.(Raw UPS Power) | Nos. | 20 | 600 | 12000
59 |  | 5 15 amps Switch Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | Nos. | 15 | 1250 | 18750
60 |  | 20 Amp 1- Ph Industrial Socket (Metal Clad) | Nos. | 4 | 2500 | 10000
61 |  | 32 Amp 3- Ph Industrial Socket (Metal Clad) | Nos. | 5 | 3500 | 17500
62 |  | 20 Amp 1- Ph Electrical Outlet | Nos. | 0 |  | 0
63 |  | Data Outlet (RJ-45) | Nos. | 4 | 500 | 2000
64 |  | Telephone Outlet (RJ-11) | Nos. | 2 | 400 | 800
65 | 6 | GENERAL EARTHING
66 | 6.1 | Supplying and erecting following GI strip used for earthing on wall with necessary MS clamps fixed on wall Cable trays Hume pipes etc. The jointes shall be Bolted Welded. The joints shall be painted with bituminous paint in an approved manner.
67 |  | 25 x 3 mm | Mtr. | 22 | 110 | 2420
68 | 6.2 | Supplying and erecting bare Copper conductor of following sizes
69 |  | 8 SWG | Mtr. | 50 | 50 | 2500
70 | 7 | LIGHT FIXTURES INSTALLATION
71 | 7.1 | Receiving from Store, Installation, testing commissioning of following light fixtures with complete installation hardwares including Anchor fastner, supporting Hook Rods as per final approval from Architect Client Consultant
72 |  | 12-15Watt PENDENT LAMP-1 | Nos. | 9 | 200 | 1800
73 |  | 10WATT ZERO WATT BULB | Nos. | 85 | 200 | 17000
74 |  | 600MM*600MM LED PANEL LIGHT | Mtr. | 8 | 200 | 1600
75 |  | 10Watt WALL LAMP | Nos. | 4 | 200 | 800
76 | 8 | MISCELLANEOUS WORKS
77 | 8.1 | Supply fixing in position approved shock treatment chart written in English, Hindi and Local language. These charts shall be framed in wooden frame covered with clear glass. | Nos. | 1 | 250 | 250
78 | 8.2 | Supply fixing in position the best quality danger notice boards of approved shape size as reqd. by the local Electrical Inspecting Authority written in English, Hindi local language. | Nos. | 1 | 250 | 250
79 | 11 | UPS System
80 |  | Supply,Installation, testing and commissioning of following type of Online UPS Inverter as per drawings and specifications with all other accessories. | Nos. | 1 | 45000 | 45000
81 |  | Online UPS
82 |  | 3.0.0KVA UPS
83 |  | 12V DC 25AH maintenance free batteries for 30 minutes battery backup.
84 |  | Input supply voltage -230-250 Volts
85 |  | Output voltage -220-240V+ -1%
86 |  | Voltage Regulation -Less than or equal to + - 1%
87 |  | Output frequency -50 Hz + - 0.05 Hz
88 |  | Type of cooling -Forced air cooled
89 |  | Invertor Efficiency -Better than 85%
90 |  | Output Power factor -0.8

## APPROVED MAKES
1. LIST OF APPROVED MAKES FOR ELECTRICAL EQUIPMENT & MATERIALS
(All major equipment/Materials shall be tested and approved by CPRI/ERDA (NABL accredited laboratory) and shall carry ISI mark. All manufacturer shall possess valid ISO certificate)
Sl. No. | Equipment & materials | Makes
1 | Low voltage switchgear enclosure (415v) (iec 61439 compliant) & switchgears | Schneider / legrand / siemens / abb / l&t
2 | Ups system (uninterruptable power supply) (415/230v) | Apc-schneider /eaton / socomec / vertiv
3 | Vrla smf battery | Excide / amararaja / rocket
4 | Dbs | Legrand - ekinoxe / schneider - acti9 / siemens / abb
5 | Vfd (variable frequency drive) | Allen bradley / alstom / danfoss / siemens/ abb/ l&t yaskawa/honeywell
6 | Motor starter | Abb / schneider / siemens / l&t
7 | Cable (415v) | Rpg/ finolex / universal /havells
8 | Disconnect switch | Schneider / abb / siemens / l&t
9 | Wires/copper flexible cable | Finolex / havells / rajnigandha / rr kabel
10 | Raceways and junction boxes | Mk / legrand / obo bettermann
11 | Cable trays | Obo bettermann / legrand / indiana / profab
12 | Spd (surge arraster) | Obo / legrand / schneider
13 | Meters (analog) | Meco / rishabh / nippen / conserve / ae
14 | Meters (digital) | Ae / schneider / nippen / conserve / l&t
15 | Energy meter , load manager | Schneider (em 6400ng or equivalent) / l&t / nippen / hpl / socomec
16 | Indicating lamps | Schneider / l & t / salzer
17 | Rotary switch | Siemens / keycee / salzer / meco
18 | Push button and push button set | Siemens / schneider electric / l & t / legrand / c&s / abb
19 | Selector switch | Keycee / salzer / meco
20 | Gi conduits and accessories | Bharat / supreme/bec
21 | Control transformer [ pt / ct ] | Ashmor / kappa / elmex
22 | Fire barrier | Obo bettermann / hilti / 3m
23 | Terminal block | Essen / connect well /elmex
24 | Control switch | Alstom/kaycee/switron
25 | Hrc fuse | Siemens /l&t /alstom/s&s /cgl /ge /standard
26 | Limit switch | Siemens /essen /bch /ind syndicate/epcc(kakku)
27 | Elr with cbct | Kalpa / jvc / prok dv’s
28 | Overload relays with built in single phase preventer | Siemens/ abb/ l&t / schneider
29 | Power/aux. Contactor | L&t / schneider
30 | Auxiliary relays | Siemens / ge alstom / abb / jvs / prok dv’s
31 | Protection relay - electromagnetic type | Areva
32 | Protection relay - numeric type | Areva / siemens / l&t / sel
33 | 1.1kv, grade lt fire survival cables | Anchor/finolex/ havells / kei/ kec
34 | Signal cable | Enercon / lapp india / system tek / caliplast / eminent
35 | Cable lugs | Dowell’s / 3d / hex / jainson / comet / hmi
36 | Bimetallic lugs | Hmi / hex / connect
37 | Cable glands | 3d / comet / hmi
38 | Lt cable jointing kits(cold curing) | Reychem/3m
39 | Pvc tape | Steel grip / isi apprved
40 | Pvc junction box | Hensel / clipsal / spelsberg / scame / sintex
41 | Ceiling fan / exhaust fan | Crompton / bajaj / orient / havells
42 | Electric timer | Siemens / legrand / l&t / meco /telemechanique
43 | Connectors (colours as per phase & neutral) | Wago / phoenix contact/ connectwell
44 | Industrial socket with mcb | Legrand / schneider/mennekes
45 | Modular switches, sockets & other accessories | Mk – blenze / legrand-arteor / schnedier-zencelo / norisys / l&t anchor - woods/ hpl - smart / c&s-primo / havells - crabtree
46 | Metal clad socket with mcb | Legrand / hensel / schneider / scame / spelsberg
47 | Public spaces light fixtures | Philips/ lighting technology/ regent/ zumtobel/ jaquar/ iguzzini/ erco / endo / bega / lumenpulse or
As per final approval of fixture by architects.
48 | Insulating mat | Jyoti / premier polyfilm limited (electromat)/
49 | Eathing material | Obo/jef/cape