## Summary
PROJECT : LKO, DOMESTIC CIP LOUNGE AT T3, LUCKNOW AIRPORT - HVAC EQUIPMENT WORKS
| SUMMARY | Toilet & Kitchen | Lounge Works
SL.NO. | DESCRIPTION OF ITEM | AMOUNT | AMOUNT
C | PART-II : HVAC
1 | SUB HEAD I - HVAC EQUIPMENT |  | 607280
| TOTAL PART-II | 0 | 607280

## Hvac - Equipment
DOMESTIC CIP LOUNGE_AMD T2
Part – II: HVAC
S. No. | Item Description | Unit | Quantity | Rate (INR) | Amount (INR) | Installation (INR) |  | Composite (INR)
[6 empty] | Rate | Amount | Rate | Amount
A. | EQUIPMENT
1 | Supplying, installing, testing and commissioning of double skin construction draw thru type AIR HANDLING UNITS (AHU) as per specification, each complete with following:
a) | Supply air centrifugal fan with efficiency >60%
b) | Pre filter (MERV 8) and Bag Filter (MERV 13) in supply air stream.
c) | Six row deep cooling coil of copper tube and aluminum construction sized at maximum face velocity of 500 fpm. Cooling coil frame work and coil end plate shall be of SS304 construction.
d) | VFD designed for HVAC applications for supply air fan
e) | Squirrel cage induction motors IE-2 (EFF-1) suitable for 415 ± 10% volts, 50 Hz, AC supply meeting criterion as per ASHRAE standard 90.1-2013 and 90% or higher efficiency.
f) | Vibration isolators.
g) | Fan outlet velocity not exceeding 10 mps.
h) | Height of Ceiling Suspended AHU shall not exceed 700 mm.
i) | Minimum 30mm(WC) external static pressure shall be considered; however the total static pressure & Motor rating shall be determined by contractor considering pressure drop across all accessories on supply air streams.
j) | Sound level at 1 m distance not exceeding 60 dB(A).
| TAG. SPACE LOCATION CFM TR SUGGESTED SUGGESTED NO. FEED STATIC PRESSURE MOTOR K.W. (MM W.G.) |  |  |  |  | TR | SUGGESTED STATIC PRESS (MM W.G.) | SUGGESTED MOTOR KW
1.1 | AHU- Domestic ---- 6500 17 65 3.8 1 CIP Lounge | No. | 1 | 382950 | 382950
Note:- Quoted prices shall be inclusive of all necessary supports by MS structural steel if required, hangers, clamp supports from walls, floors and ceiling with painting with one coat of primer and two coats of paint to supports of MS work.
2 | Supply, Installation, testing and commissioning of electronic, AUTOMATIC PRESSURE INDEPENDENT BALANCING VALVE type dynamic balancing Valve with integrated 2 way modulating Control valves in a single body. The actuator shall be capable of accepting 2-10VCD, 4- 20 mA electric signal and shall provide similar transduced feedback output signal to control system. The valves & actuators shall be compatible with Building Automation System. HVAC consractor shall ensure the required power supply to the valve for proper working.The minimum close off Pressure of actuator must be 1.5 times shut off head of pump . The valve shall be suitable for following pipe sizes:
2.1 | 50 mm dia pipes for AHU | No. | 1 | 42500 | 42500
3 | Supply, installation, testing and commissioning of THERMOSTAT for cooling. The thermostat shall be electronic room temperature controller with digital display & fan speed control, capable of providing individual space temperature control for cooling application. The controller shall be designed to modulate two control devices such as 2 way motorized valves for chilled water cooling in 2 pipe system.
3.1 | Thermostat for AHU | No. | 1 | 4830 | 4830
| Sub-Total |  |  |  | 430280
B. | PIPING-CHILLED WATER
1 | Providing and fixing in position the following MS class ‘C’ pipes cut to required lengths and installed with all welded joints, providing and fixing in position the necessary fittings like elbows, tees and reducers, sockets for probe meter with necessary supports by MS structural steel if required, hangers, clamp supports from walls, floors and ceiling including cutting holes and chases in brick, R.C.C. work, making good the same to original condition complete in all respects with painting with one coat of primer and two coats of paint to supports of MS work
Note : All chilled water and condenser water pipes and all fittings shall be Mild Steel - Class `C’ (Heavy Class) conforming to relevant BIS-1239 Code from 20 mm to 250 mm dia. Factory rolled pipes 250 mm dia above shall have 8 mm wall thickness confirming to IS-3589. Entire piping shall have welded joints conforming to relevant BIS Codes.
1.1 | 65 mm dia MS pipes | RM | R/o |  | -
1.2 | 50 mm dia MS pipes | RM | 10 | 1750 | 17500
1.3 | 40 mm dia MS pipes | RM | R/o |  | -
1.4 | 32 mm dia MS pipes | RM | R/o
1.5 | 25 mm dia MS pipes | RM | R/o
2 | Providing and fixing in position the following GI class ‘B’ pipes cut to required lengths and installed with all screwed joints, and providing and fixing in position the necessary elbows, tees and reducers as per specifications with necessary supports by MS structural steel if required, hangers, clamp supports from walls, floors and ceiling including cutting holes and chases in brick, R.C.C. work, making good the same to original condition complete in all respects with painting with one coat of primer and two coats of paint to supports of MS work.
2.1 | 32 mm dia GI pipes | RM | R/o |  | -
2.2 | 25 mm dia GI pipes | RM | 10 | 2540 | 25400
2.3 | 20 mm dia GI pipes | RM | R/o |  | -
2.4 | 15 mm dia GI pipes | RM | R/o |  | -
3 | Providing and fixing in position the following Butterfly Valve Valves:
3.1 | 50 mm dia Valves. | No. | 2 | 6500 | 13000
4 | Providing and fixing in position the following ‘Y’ Strainers :
4.1 | 50 mm dia Valves. | No. | 1 | 8600 | 8600
5 | Supplying, installation, testing and commissioning of Auto air vents. | No. | 1 | 1800 | 1800
6 | Providing and fixing in position the industrial type pressure gauges with gun metal including GI nipple valves. | No. | 2 | 5500 | 11000
7 | Providing and fixing in position the mercury-in- glass industrial type thermometers within brass encasing | No. | 1 | 3500 | 3500
| Sub-Total |  |  |  | 80800
C. | THERMAL INSULATION
3 | Supplying, installing and testing of 25 mm thick expanded polystyrene pre moulded pipe section insulation along with aluminium cladding on chilled water piping and fitting like valves, flanges union, etc. as per the approved shop drawings and specifications.
3.1 | 50 mm dia pipes | RM | 10 | 2100 | 21000
3.2 | 40 mm dia pipes | RM | R/o |  | -
3.3 | 32 mm dia pipes | RM | R/o |  | -
3.4 | 25 mm dia pipes | RM | R/o |  | -
3.5 | 25mm dia condensate drain pipes | RM | 10 | 320 | 3200
3.6 | 20 mm dia condensate drain pipes | RM | R/o |  | -
| Sub-Total |  |  |  | 24200
Providing and fixing electric water storage heater (geyser) wall hung with glass lined tank and 40 -50 mm insulation. The system should be single phase 50 Hz it should be all necessary feature like adjustable thermostat, protective anode rod including making inlet / outlet connections.
a) | Capacity : 20 litre | No. | 2 | 18500 | 37000
b) | Capacity : 50 litre | No. | 1 | 35000 | 35000
| Sub-Total |  |  |  | 72000
| Total Carried to Summary |  |  |  | 607280

## LOM-MEP
PROJECT : LKO, DOMESTIC CIP LOUNGE AT T3, LUCKNOW AIRPORT - HVAC EQUIPMENT WORKS
LIST OF MAKES ELECTRICAL
S. No | Equipment/Item/Material | Approved Makes
1 | MCCBs | LEGRAND/L&T/SCHNEIDER/ABB/SIEMENS / C&S
1 | MCBs /ELCBs | LEGRAND/L&T/SCHNEIDER/ABB/SIEMENS / C&S
2 | CABLE TRAYS & RACEWAY ACCESSORIES | SUPERMAX / INDIANA / PELCO / SLOTCO
3 | CABLE TRAY STEEL SUPPORTS | SUPERMAX / INDIANA / PELCO / SLOTCO
4 | GI PIPES | JINDAL (HISSAR)/TATA (ISI)
5 | HDPE (DWC) PIPES | DURALINE/ REX/ TIRUPATI
6 | MCB DISTRIBUTION BOARDS | SCHNEIDER/LEGRAND/SIEMENS/L & T
7 | L.T. CABLES & CONTROL CABLES | POLYCAB /HAVELLS / NATIONAL / ICC / KEI/SKYTONE/ GEMSCAB/ BONTON
8 | CABLE GLAND | COMMET/HMI/GRIPWELL
9 | LUG/ TERMINAL BLOCKS | DOWELL’S/REYCHAM/COMMET/ WAGO/ ELMEC
10 | BATTERIES | EXIDE/HBL/ROCKET/STANDARD/AMCO/CUMMINS
11 | UPS | APC/EMERSON/ABB/ GUTOR
12 | WIRE | FINOLEX/ HAVELLS/ POLYCAB/ KEI
13 | RACEWAYS | MK/LEGRAND/ SCHNEIDER
14 | PLOYCARBONATE JUNCTION BOX | SINTEX/MK/LEGRAND
15 | LED LIGHT FITTINGS | PHILIPS/ THORN/ SCHREDER / SITECO
16 | GI CONDUIT | BEC/AKG/ NIC/STEEL CRAFT/JINDAL
17 | GI CONDUIT ACCESSORIES | RAMA/ SHARMA SALES CORPORATION / FIT WELL/ AKG
18 | JUNCTION BOXES | LEGRAND/ MK/ SCHNEIDER
19 | IP RATED FLOOR BOXES | LEGRAND/ MK/ SCHNEIDER
20 | MODULAR PLATE TYPE SWITHCH / SOCKET GI BOXES / FAN REGULATOR/TELEPHONE SOCKET | MK (WRAPAROUND)/ LEGRAND (MYRIUS)/ SCHNEIDER (ZENCELO) / NORTH WEST (STYLUS) / CRABTREE (ATHENA)
21 | TELEPHONE CABLES / WIRES / CO-AXIAL TV CABLES | FINOLEX/POLYCAB/ HAVELLS/ RR KABLE/ SKYDA/ BCH/ L&T/ DALTON
22 | CAT 6 CABLE / CAT 6A / FIBER OPTIC CABLE & ASSOCIATED ITEMS | SCHNEIDER/ SIEMON/ SYSTIMAX
23 | TELEPHONE TAG BLOCK | KRONE (GERMAN) /POUYET
24 | LUGS / FERRULES / THIMBLES | DOWELLS / JAINSON
25 | OCCUPANCY SENSOR | PHILIPS /WIPRO /GE
26 | RJ-45 MODULAR SOCKET WITH PLATE | AMP/ SCHEINDER/ SIEMON / SYSTIMAX
27 | DATA RACK & ACCESSORIES | SCHNEIDER, RITTAL, VALRACK
28 | MAIN FIRE ALARM CONTROL PANEL | NOTIFIER/HONEYWELL/ EDWARD/SIEMENS/BOSCH
29 | MULTI CRITERIA/SMOKE DETECTOR | NOTIFIER/HONEYWELL/EDWARD/SIEMENS/BOSCH
30 | INTELLIGENT HEAT | NOTIFIER/HONEYWELL/EDWARD/SIEMENS/BOSCH
31 | SPEAKERS | NOTIFIER/HONEYWELL/EDWARD/SIEMENS/BOSCH
32 | DIGITAL VOICE EVACUATION SYSTEM | NOTIFIER/HONEYWELL/GAMEWELL/SIEMENS/BOSCH
33 | CCTV | CP PLUS/HIKVISION/ZICOM/PELCO/SONY
34 | EMERGENCY CALL SYSTEM | ZENTAL- NORWAY, SIEMENS, HONEYWELL
35 | DISTRIBUTION PANEL | NEPTUNE/ABB/ADLEC/ADVANCE
36 | FAULT ISOLATOR | NOTIFIER/HONEYWELL/EDWARD/SIEMENS/BOSCH
37 | RESPONSE INDICATOR | NOTIFIER/HONEYWELL/EDWARD/SIEMENS/BOSCH
38 | CONTROL MODULE | NOTIFIER/HONEYWELL/EDWARD/SIEMENS/BOSCH
39 | HOOTER | NOTIFIER/HONEYWELL/EDWARD/SIEMENS/BOSCH
40 | MANUAL CALL POINT | NOTIFIER/HONEYWELL/EDWARD/SIEMENS/BOSCH
41 | MICROPHONE | NOTIFIER/HONEYWELL/EDWARD/SIEMENS/BOSCH
42 | MICROPHONE WITH TABLE | NOTIFIER/HONEYWELL/EDWARD/SIEMENS/BOSCH
LIST OF MAKES HVAC
1 | AIR HANDLING UNIT | Edgetech / Waves / VTS / Caryaire
2 | AIR CURTAINS | Euronics / Airtecnics /Orchids
3 | INLINE FAN | KRUGER / SYSTEM AIR / GREENHECK
4 | MS PIPES UPTO 200MM DIA | JINDAL / TATA STEEL
5 | BUTTERFLY VALVE | AIP / CASTLE / JAYHIWA
6 | Y-STRAINER | AIP / EMERALD / CASTLE
7 | PRESSURE GAUGE | DWYER / FEIBIG / H GURU
8 | THERMOMETER | EMERALD / H GURU / TAYLOR
9 | AUTO AIR VENT VALVE | OR(ITALY) / AIP
10 | AUTOMATIC PRESSURE INDEPENDENT BALANCING VALVE FOR AHU | BELIMO / DANFOSS / FLOWCON
11 | THERMOSTAT | DANFOSS / HONEYWELL / JOHNSON / SIEMENS
12 | FACTORY FABRICATED DUCT | ZECO/ DUCTOFAB/ ROLASTAR/ALFA DUCT
13 | FIRE DAMPERS MOTORS | SYSTEM AIR / DYNACRAFT / TROX / COSMOS / GREENHEC
14 | G.I. SHEET METAL DUCT | JINDAL HISSAR /NATIONAL/ TATA STEEL
15 | GRILLES/ DIFFUSERS/NOZZLES | RUSKIN TITUS/ SYSTEMAIR/TROX/CARYAIRE
16 | FIRE DAMPERS (UL LISTED & STAMPED) | GREENHECK/ RUSKIN/ TITUS/ SYSTEM AIR/ CARYAIRE
17 | G.I. SHEETS | JINDAL HISSAR/ SAIL
18 | FIRE RATING OF DUCTS | LAF/PROMAT
19 | FLEXIBLE DUCT | ATCO/ CARYAIRE
20 | SOUND ATTENUATOR | SYSTEMAIR/TROX/CARYAIRE
21 | GLASS WOOL/ FIBREGLASS | OWENS CORNING /U.P. TWIGA/ KIMMCO
22 | POLYURETHANE FOAM | MALANPUR /SUPERURETHANE
23 | CROSSED LINKED POLYETHYLENE FOAM | TROCELLENE / SUPREME/ PARAMOUNT/ THERMAFLEX/ K-FLEX
24 | CLOSED CELL ELASTOMERIC NITRILE RUBBER | K-FLEX /A-FLEX/ARMACELL
25 | NON-WOVEN FIBRE MATERIAL | MIKRON/ DU PONT
26 | UV PROTECTIVE COATING | ARMACELL/ARMACHEK/AMICOL/PARAMOUNT/ POLYBOND/PROMARK ASSOCIATES
27 | ALUMINUM TAPE | JOHNSON/BIRLA 3M
28 | ALUMINIUM SHEET/ PERFORATED AL SHEET | BALCO/ HINDALCO
29 | ANCHOR FASTNERS | CANNON/ HILTI/FICHER/RAWL PLUG
30 | VIBRATION ISOLATOR | CORI/RESISTOFLEX/DUNLUP
31 | FIRE SEALANT | BIRLA 3 M/ HILTI/PROMAT
32 | FLEXIBLE PIPE CONNECTION | CORI/RESISTOFLEX
33 | VAPOUR BARRIER COATING/PAINT | FOSTER SEAL PASS COATING
34 | FIBRE GLASS WOVEN CLOTH (7 MIL-APPROX. WT 200 GM./SQ.MT) | OWEN CORNING/ UP TWIGA/ KIMMCO/ARCO
35 | STUCK UP PINS | IDENDEN/ DURODYNE/ DETONATE
36 | PIPE HANGERS’ CLEVIS TYPE | GRINNELL/MUPRO/AMIL/UNISTRUT
37 | VARIABLE FREQUENCY DRIVES | DANFOSS/ABB/SIEMENS
38 | FILTERS | PUROLATOR/THERMODYNE/SPECTRUM
39 | TEMPERATURE AND RH SENSOR | HONEYWELL/SIEMENS-STAEFA/JOHNSON
40 | MOTORS | ABB/SIEMENS/BHARAT BIJLI
41 | VIBRATION ISOLATOR/SUSPENDERS | RESISTOFLEX
42 | FLEXIBLE CONNECTIONS FOR FAN OUTLET | MAPRO/CARYAIRE
43 | 2 WAY VALVE | DANFOSS / BELIMO
LIST OF MAKES PL & FF
1 | Single bowl with drainboard sink | NIRALI / KAFF / EQUIVALENT
2 | Plumbing CP and sanitary fixtures, including flush valves, metering & manual faucets, Urinal,Urinal sensor ,shower line drain, Towel shelf,rain shower, sink mixture etc. | KOHLER / EURONICS / Queo
3 | C.P gratings, floor drains and cockroach traps. | NEER / CHILLY / EQUIVALENT
4 | Grab Bar,baby diaper changing station,robe hook Automatic & Manual soap dispencer,hand drayer,paper towel dispencer,Toilet paper holder. | EURONICS/ EQUIVALENT
5 | Floor drains | SUPREME / KOHLER/ NEER
6 | cPVC Pipe & Fittings for Water Supply | ASTRAL / SUPREME / ASHIRVAD
7 | uPVC pipes & fittings | ASTRAL/ SUPREME/ ASHIRVAD/ FINOLEX
8 | RCC Hume Pipes | INDIAN HUME PIPE / EQUIVALENT
9 | Solvent Cement | ASTRAL / SUPREME / PRINCE
10 | PVC ASTM Schedule pipe | ASTRAL / SUPREME/ EQUIVALENT
11 | Insulation ( Hot water ) | ARMAFLEX / VIDOFLEX /EQUIVALENT
12 | Brass & Gun metal, Gate valve | ZOLOTO / RB / SANT/ L&T
13 | Ball Valves | ZOLOTO / ITAP/ EQUIVALENT/ L&T
14 | Butterfly Valves | ZOLOTO / AUDCO/ EQUIVALENT/L&T
15 | Auto Sensors | AOS / ASKON/ EQUIVALENT
16 | Water meter ( Mechanical Type) | ITRON / KAYCEE / CAPSTAN / KRANTI
17 | Pipe Supports | HITECH/ EQUIVALENT
18 | Paints | ASIAN PAINTS / BERGER / SHALIMAR PAINTS
19 | Prefabricated, Fiberglass, Steel, PVC Etc. for Flushing Tank and Holding Tank, Overhead water Tank) | BELCO / RHINO / SINTEX
FIRE_FIGHTING SYSTEM
20 | Pipe And Fittings | TATA/ JINDAL/ SURYA
21 | Valves | KBL/ INTERVALVE/ LEADER / SANT / ZOLOTO
22 | Pressure Gauge | H GURU / FIEBG / DANFOSS
23 | Flow Switches | DANFOSS / HONEYWELL / SWITZER
24 | Coating & Wrapping | IWL / RUSTEK / EQUIVALENT / PYPKOTE/ COALTECK
25 | Enamel Paint | ASIAN/ NEROLAC/ BERGER
26 | Paint Primers | ASIAN/ JENSON NICHOLSON
27 | Sprinklers | H.D. FIRE / TYCO / VIKING
28 | Fire Extinguishers | PADMINI/ SUPEREX/ OMEX/ MINIMAX / NEWAGE / GETECH / SAFEGUARD/ FIREX/ LIFEGUARD
29 | Pipe Hangers | CAMRY/ CHILLY/ GMGR
30 | Sprinkler Flexible Connection Pipe | NEWAGE/YOUNGJIN/FLEXHEAD