## Fire BoQ
R0
|  |  |  | Date- | 09.12.2023
AJ KITCHEN OUTLET FIRE BOQ
BOQ FOR FIRE FIGHTING SYSTEMS
S/NO | DESCRIPTION | QUANTITY | UNIT | Rate | Amount | Remarks
1 | Providing, laying, jointing, testing and commissioning of G.I. `C' Class pipes (IS:1239 (Part-I)-1979) including cutting,threading welding etc providing all malleable galvanized iron fittings conforming to IS 1879, viz. Flanges, bends, tees, elbows,reducers, unions, supporting with G. I. clamps, hangers, M.S. brackets etc. including cutting holes and chases in brick or RCC wall / slabs and making good the same to the Approval of Architect / consultant,complete including painting with one coat of primer and two or more coats of synthetic enamel paint of approved make and shade. ( Note- Rigid/flexible pipe extension from existing line is considered) |  |  |  |  | GI Pipe- Jindal Hissar
i) | 25 mm dia. | 25 | RMT | 1015 | 25375
ii) | 32 mm dia. | 5 | RMT | 1276 | 6380
iii) | 40 mm dia. | 5 | RMT | 1544 | 7720
iv) | 50 mm dia. | 10 | RMT | 1957 | 19570
v) | 65 mm dia. | 5 | RMT | 2784 | 13920
vi) | 80 mm dia. | 0 | RMT | 3263 | 0
vii) | 100 mm dia. | 0 | RMT | 3886 | 0
2 | Providing , fixing testing and commissioning of pendant type sprinkler heads 68 deg. Temp.(Quick response type)-UL listed & FM approved | 0 | No. | 545 | 0 | Tyco / HD
3 | Providing , fixing testing and commissioning of concealed type sprinkler heads 68 deg. Temp.(Quick response type)-UL listed & FM approved | 5 | No. | 2175 | 10875 | Tyco / HD
4 | Providing , fixing testing and commissioning of concealed type sprinkler heads 79 deg. Temp.(Quick response type)-UL listed & FM approved | 2 | No. | 2393 | 4786 | Tyco / HD
5 | Providing , fixing testing and commissioning of upright type sprinkler heads 68 deg. temp(Quick response type)- Optional Subject to liasion team requirements | 5 | No. | 544 | 2720 | Tyco / HD
6 | Providing , fixing testing and commissioning of upright type sprinkler heads 79 deg. Temp (Quick response type)-UL listed & FM approved | 2 | No. | 798 | 1596 | Tyco / HD
7 | Providing & fixing testing and commissioning of braided UL listed & FM approved SS Flexible pipe
i) | 1 MT Long | 4 | No. | 2175 | 8700 | Tyco / HD
ii) | 1.6 MT Long | 3 | No. | 2538 | 7614
7 | Gun metal chrome finished Ball valves (PN 16) with fittings of screwedend type.
I) | 40 mm dia. | R.O. | No. | 3625 | 0 | Zoloto / Sant
I) | 32 mm dia. (Sprinkler drain-OPTIONAL) | R.O. | Nos. | 2683 | 0
8 | Wheel operated Butterfly Valves (PN 16) with inbuilt supervisory switch (UL listed and FM approved) with CI Body, Black Nitrile Body Liner and Nylon Coated SG Iron Disc with material and labour including hydraulic testing etc. complete as per drawing, specification & to the level of satisfaction of Site- Incharge. |  |  |  |  | Zoloto / Sant
I) | 150 mm dia. | R.O. | No. | 15225
I) | 100 mm dia. (OPTIONAL) | 0 | No.
I) | 65 mm dia. | 1 | No.
9 | 6kg capacity ABC type dry chemical powder fire Extinguishers with wall mounting brackets | 4 | Nos. | 6017 | 24068 | Minimax / Agni
10 | 6kg capacity K type fire Extinguishers with wall mounting brackets | 1 | No. | 18560 | 18560 | Minimax / Agni
11 | 5kg capacity CO2 type fire Extinguishers with wall mounting brackets | 1 | No. | 12905 | 12905 | Minimax / Agni
12 | 9Lit AR-AFFF type fire Extinguishers with wall mounting brackets | R.O. | Nos. | 5771 | 0 | Minimax / Agni
13 | Flow switch on sprinkler distribution header on floor with 2 SPDT contacts suitably rated, capable of the high pressure system and connected to fire alarm panel through cable. (OPTIONAL IF REQUIRED BY CLIENT)
i) | 65 mm dia. | 1 | No. | 7540 | 7540 | SystemSenser / Honneywell
14 | Ceasefire 5 Kg Ceiling Mounted Fire Extinguisher Clean Agent FE-36, Zero ODP, Stored Pressure Type, Pressure Gauge, Gross Weight 7.7 Kg, empty Weight 2.7 Kg, Can Height 264MM, Diameter 240MM,Discharge Time less than 8 Secs, Auto discharge mechanism on temperature rise, applicable on Class A,B,C and electrically started Fire, Can Construction : Deep drawn & Co2 Mig welded, Valve Construction : Forging & Machining, Internal Coating of Can : Epoxy Powder coating, External Coating of Can : Epoxy Polyster Powder coating, Sheet metal thickness : 2.0MM, Helium Leak Detection Test, 5 Years Warranty-model no 1CH21CF | 0 | No. | 52925
| SUB-TOTAL |  |  |  | 172329
Note : | Taxes Extra as applicable.