## Electrical
Client Name: |  |  |  | FL Group
Travel Food Service private Limited |  |  |  | New no:7, Old no:4, 4th Cross Street,
K Hospitality |  |  |  | Shenoy Nagar West , Chennai-600030
GSTIN: 33AACCF7383A1ZY
Quote: FL-2011/ 871
|  |  |  | Date:05-03-24 | Revision :1
Kind Attn: Mr.Binu Balachandran
Mr. Jogeshwar
Mr.Stephen
IV | Electrical work
ITEM | DESCRIPTION | QTY | UNITS | RATE | TOTAL AMOUNT
A | ELECTRICAL
Notes
All materials and workman ship shall be to standards / consultants' approval and shall comply with Local electrical rules & Electrical Inspectorate.
Colour conduits should be used for data, raw power, UPS & access control as listed below coding
Data - Grey
Raw Power and Lighting - Blue
UPS - Black
All Civil work required for the electrical work such as chipping of walls, floor, etc and rough plastering with chicken mesh shall be deemed included.
1 | MV Cables
1.1 | Copper Cables
Supplying, laying, testing and commissioning of YY/YFY insulated PVC sheathed, Cu. conductor steel armoured 1100V grade cable. The cable shall be laid underground OR on wall / in pipe / trench as required as per site condition. For cables laid underground the rate shall exclude earth excavation, providing brick and sand protection. refilling, compacting etc. For cables laid on wall / on tray/ in pipe / trench - the rate shall include necessary clamping arrangements.
Standards applicable For below cable
YY/YFY/AYFY - IS 1554 PART I
1.1 | Armoured type Copper cables
1.1.2 | 3.5C X 35 Sq.mm Aluminium Armour Cable | 70 | Mtr | 425.5 | 29785 | We required only 3.5C X 35 Sq.mm Aluminium Armour Cable
1.2 | PVC Cable End Termination |  |  | 0
| Providing and termination for the below listed cross |  |  | 0
| section cable with single compression brass glands, |  |  | 0
| solderless tinned Cu crimping type lugs, gland earthing, |  |  | 0
| etc., complete. |  |  | 0
| Armoured type Copper cables |  |  | 0
2 | MAIN INCOMER ISOLATOR BOX |  |  | 0
| Supply, Erection and commissioning of Cubical type dust and vermin proof free standing floor mounting panel board as per technical specifications and drawing consisting of the following complete with all interconnections, painting and control wiring etc., as per IS and general specifications. |  |  | 0
2.1 | Incomer: | 1 | Nos | 152766 | 152766
| 100A 4P 36kA MCCB(Microprocessor based) - 1 No |  |  | 0
| Out going: |  |  | 0
| 100A 4P ISOLATOR - 1 No |  |  | 0
| 32A 4P ISOLATOR - 2 No |  |  | 0
| Bus bar: 1 set TPN AL bus bar suitably rated for 125A. |  |  | 0
3 | DISTRIBUTION BOARDS |  |  | 0
| S I T & C of surface mounting / flush mounting 10kA phase segregated TPN MCB distribution boards (MCB DB). The DB shall be made out of 1.2 mm CRCA sheet steel enclosure and powder coated complete with cable gland plate with knock out at the top & bottom. The DB shall have double door with hinged lock able external door. The DB's shall be phase segregated type and shall have 4P MCB / MCB isolator as incomer, DP RCCB / RCBO as phase incomer and SP MCB as outgoing with the rating as specified. The busbar shall be tinned copper; Insulated fork type for phases, Independent neutral bus for each phase including inter connecting wiring & earth bus on insulation mount. DB & Electrcial meter should be covered with wooden boxes |  |  | 0 |  | DB & Electrcial meter should be covered with wooden boxes
| The RCCB / RCBO shall be Hpi / Si series & MCBs shall be 'C' Curve for UPS DBs (UDB) and 'C' Curve for other application. |  |  | 0
3.1 | 8way SPN DB with 25A DP RCBO 100mA as incomer, and outgoings-10A-5Nos. SP 'C' curve MCB and 16A-1Nos. SP 'C' curve MCB as outgoings as per SLD drawing. | 1 | Nos | 8234 | 8234
3.2 | 12way VTPN MCCB DB with 100A 4P MCCB as incomer, and outgoings- 36nos. 10/16/20A SP 'C' curve MCB-25nos,25A DP MCB-1nos,20A TP MCB-3nos.as outgoings as per SLD drawing. | 1 | Nos | 38939 | 38939
4 | CIRCUIT MAINS |  |  | 0
| Supply and laying of sub/ circuit mains using 2mm thick MS conduit, access- ories like pvc bends,& M.S junction boxes, GI cleat and saddles etc., 660/ 1100V grade FRLS flexible copper wires and wiring accessories, terminating wires on either ends by providing copper lugs and carrying out surface / concealed wiring. Most of the area have false ceiling and conduits / Raceways shall run exposed above false ceiling. |  |  | 0
| The rate shall include grooving of walls, floors chipping, rough plastering, providing MS brackets for conduit suspension. Circuit mains shall be measured from DB to switch board and looping from switch board to switch board |  |  | 0
4.1 | 3C x 6.0 qmm FRLS insulated copper flexible cables in Existing Conduit / raceway-Lighting/ general raw power | 40 | Mtr | 322 | 12880 | We required over all 400 Mtrs wiring for all this works
4.2 | 3C x 4.0 Sqmm FRLS insulated copper flexible cables in Existing Conduit / raceway-Lighting/ general raw power | 90 | Mtr | 218.5 | 19665
4.3 | 3C x 2.5 Sqmm FRLS insulated copper flexible cables in Existing Conduit / raceway-ups | 130 | Mtr | 149.5 | 19435
4.4 | 3C x 2.5 Sqmm FRLS insulated copper flexible cables in Existing Conduit / raceway-Lighting/ general raw power | 100 | Mtr | 149.5 | 14950
4.5 | 3C x 1.5 Sqmm FRLS insulated copper flexible cables in Existing Conduit / raceway-Lighting/ general raw power | 60 | Mtr | 149.5 | 8970
5 | POINT WIRING |  |  | 0
| Wiring of light points, fan points, socket outlets by using 2mm thick FRLS conduit of required dia as per IS 732, PVC conduit accessories, flexible conduit with PVC gland for drops with accessories & 2R X 1.5Sqmm + 1 Sqmm FRLS Cu. Wire approved 5A modular type switches and sockets, GI / PVC boxes, and other point wiring accessories and caring out surface /concealed conduit point wiring. (it should be legrand brand) |  |  | 0
| All points shall be earthed with 1sqmm FRLS flexible copper wire. Points shall be terminated at light fixtures with ferrules, 15A 4 way connector; wire ends shall not be loose / bare. |  |  | 0
| The rate shall include necessary civil works for embedding conduits and boxes. |  |  | 0
| Note: Ceiling height is 2.7mt. Point wiring shall not be measured on RM basis. |  |  | 0
5.1 | 1 light points controlled by 6/16A switch & Socket | 15 | Nos | 2024 | 30360 | It need to mentioned Switch & Socket, and 15 nos each required anf it should be legrand brand
5.2 | 2 light points controlled by 6/16A switch & Socket | 15 | Nos | 2679.5 | 40192.5
5.3 | 3 light points controlled by 6/16A switch & Socket | 0 | Nos | 3323.5 | 0
5.4 | 4 light points controlled by 6/16A switch & Socket | 0 | Nos | 3979 | 0
5.5 | 7 light points controlled by 6/16A switch & Socket | 0 | Nos | 5945.5 | 0
6 | SWITCH AND SOCKETS AND MS ENCLOSURE UNITS |  |  | 0
6.1 | S I T & C of the following components like approved make / type switches, socket etc,. housed in MS / GI enclosure, duly wired and painted. All the switch sockets are without boxes since the same is covered under different item |  |  | 0
6.1.1 | 1no. 5A controlled by 5A SP Switch with indicator and different colour front plates with box. (General) | 4 | Nos | 862.5 | 3450
6.1.2 | 1no. 5/15A controlled by 5/15A SP Switch with indicator and different colour front plates with box. (Raw power) | 9 | Nos | 1138.5 | 10246.5
6.1.3 | 1no. 20/32A controlled by 20/32A SP Switch with indicator and different colour front plates with box. (Raw power) | 0 | Nos | 736 | 0
6.1.4 | 1no. 32A 3 Phase Industrial socket controlled by 32A TP MCB with indicator and different colour front plates with box. (Raw power) | 0 | Nos | 6463 | 0
6.1.5 | 3M MS GI Coated Box | 0 | Nos | 138 | 0
6.1.6 | 6M MS GI Coated Box | 0 | Nos | 264.5 | 0
6.1.7 | 8M MS GI Coated Box | 0 | Nos | 310.5 | 0
7 | EARTHING |  |  | 0
| Supply and laying of earth wire in PVC conduit |  |  | 0
7.1.1 | GI wire for double earthing | 80 | Mtr | 34.5 | 2760 | We required 80 mtrs GI wire for double earthing
8 | SAFETY ITEMS |  |  | 0
| Providing and laying / fixing the below mentioned safety items |  |  | 0
8.1 | Shock and First Aid charts in T/W frame | 1 | Nos | 2530 | 2530
8.2 | First Aid Box | 1 | Nos | 3105 | 3105
8.3 | 415V 150mm x 150mm enamel type danger board | 1 | Nos | 402.5 | 402.5
8.4 | Drawing display board suitable for A3 size with As built drawing laminated. | 1 | Set | 3105 | 3105
8.5 | No Admission board | 1 | Nos | 1092.5 | 1092.5
8.6 | Rubber Mat on floor for Electricric DB Panels | 1 | Nos | 1610 | 1610
9 | MISCELLANEOUS ITEMS |  |  | 0
9.1 | Temporary lighting during the construction of the project sockets, ELCB, MCB / fuse cut-outs, wiring, etc., complete. | 1 | Set | 71300 | 71300
9.2 | Fabrication and providing MS items, like angles, channels, plates and flats with hardware, duly painted/ powder coated etc., | 25 | Kg | 207 | 5175
9.3 | Supply and installation of 2kVA UPS 1 Phase input /1ph output with SMF Battery bank with stand for 30min.Backup | 1 | Nos | 66884 | 66884
9.4 | 25mm PVC heavy duty conduit 2mm thick FRLS as per IS 732 for connectivity of the wires. | 100 | Mtr | 92 | 9200
9.5 | Cable tray - (As per site conditions) | 1 | Lot | 0 | 0
9.6 | Electrical race way for floor conduit - 150mm width | 10 | Mtr | 1173 | 11730
10 | Light Fittings |  |  | 0
10.1 | Providing & Fixing of approved spot lights - 12 Watts | 6 | Nos | 3921.5 | 23529
10.2 | Providing & Fixing of approved hanging lights | 10 | Nos | 4519.5 | 45195
0
B | CCTV SYSTEM |  |  | 0
| NOTES: 1. CCTV cameras as per the design. 2. Location of the DVR/NVR in the services closet as per the design |  |  | 0
1 | Supply, Installation, Testing & Commissioning of Digital video recorder with bundled server machine, Preloaded of Enterprises Software & with remote monitoring facilities. Protocol : TCP/IP/ANALOG , DHCP, SMTP. Power supply source : 240V, 50Hz, AC. Video output : Monitor - A :- 1 BNC, RCA, VGA. : Monitor - B :- 1 BNC (single / multi) Compression : H.264, MPEG-4 & MJPEG on IP cameras. Display resolution : 720 x 480 / 720 x 576 (PAL) Motion based Recording of 70% (Speed/Resolution) Resolution : a). 720p @ 10fps. H.264 format for 30Days. HDD Backup : 30 Days Motion based recording 70% Motion recording per day. 16 Channel dVR | 0 | Nos | 40250 | 0
2 | Supplly, Installation, Testing & Commissioning of Camera | 0 | Nos | 7475 | 0
3 | Supply, Installation, Testing & Commissioning of RG 59 Grade 75 Ohm's Co-Axial Cable | 0 | Mtr | 46 | 0
4 | Supplying and laying of approved make -GI conduits on ceiling / wall / floor etc. complete with accessories like, Junction boxes, Collars, Bends, clamps, saddles etc. 25 mm dia. Conduit. | 0 | Mtr | 322 | 0
C | IT NETWORKING SYSTEM |  |  | 0
| NOTES: 1. 24 port switch panel provided as per the design and location in the service closet. 2. Wifi location as per the design. |  |  | 0
1 | 8 Port Network Switch for the Wifi and LAN networks for the store | 1 | Nos | 12109.5 | 12109.5
2 | CAT 6 cable for the Wifi and networking of the store | 210 | Mtr | 57.5 | 12075 | Required 200 mtrs CAT 6 cable is required and it should be layed by us
3 | Data outlet with RJ-45 jack | 4 | Nos | 1012 | 4048
4 | Patch Cords of 1.5 meters length | 4 | Nos | 299 | 1196
5 | Wifi Router | 0 | Nos | 7647.5 | 0
| GRAND TOTAL |  |  |  | 666919.5
GST Extra
For FL Group ( FL Traders Pvt Ltd)