## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
109521 |  | Chilled Water Piping with Nitrile Rubber Insulation - Supplying, laying or fixing, testing and commissioning of MS C class chilled water piping (cut of required length and installed with welded joints. The necessary fittings such as elboues, tees etc. shall all to included in this item). The Insulation shall be Class O nitrile Rubber pre-slit, pipe sleeve upto 100 mm dia and sheet for bigger dia with factory Laminated 7 mill woven glass cloth of thicknesses as specified, with approved adhesive. Manufactured supplied, suitable sized nitrile rubber pipe supports with PUF or PIR inserts shall be used. Thermal conductivity should not exceed 0.035 W or MK at 0 degree celsius and water vaper resisitance > 7000. Manufactures tapes and adhesive to used only. The pipe supports should also be of nitrile rubber with PUF or PIR inserts and are to be installed as per manufacturer s recomendation. The pipe fittings shall be MS. class for pipes upto 150 mm and for 200mm and above, same material of the pipe shall be usee all bends or Reducess or Tee upto 150 mm shall be factory fabricated ready made MS C class. Note Use proper template for marking block colour Arrows pipe. for supply or return. 40mm dia with 38mm (25 mm + 13 mm) dia thick insulation | Mtrs. | 0.00 | 20.00 |  | 0
109522 |  | Insulated Valves |  | 0.00 | 0.00 |  | 0
109523 |  | Dynamic Balancing Valve-PID type - Supply installation, testing and commissioning of BMS Compatible electronic self balancing valve with integrated two way modulating control valves in a single body. The actuator shall be capable of accepting 230V or 24V or 2-10VDC or 4-20 mA electrical signed and shall provided similar transduced feed back output singed to control system. The minimum close off pressure of actuator must be 1.5 times shut of head of pump as per Specification of following size. The actuator shall be microprocessor based with self calibration feature. All the valve shall be complete with step down transformers, thermostat, control wiring and probe. 20-30 USGPM (50 mm dia) Insulation as per pipes | Nos. | 0.00 | 1.00 |  | 0
109524 |  | Manual Butterfly Valves (Insulated) - Providing and Fixing of the following valves with PN-16 Ratings complete with flanges or nuts or bolts or gaskets etc. Butterfly valve shall have CI body seal of black nitrile rubber (tight shutoff) S.G. iron disc(nylon coated) PTFE coated shafts etc. as required. These valves should be suitable for flow in either direction and seal in both directions and should be integral moulded design. 40 mm dia -PN16 -- Insulation as per Chilled water pipe | Nos. | 0.00 | 2.00 |  | 0
109525 |  | Y- Strainer (Insulated) - Providing and Fixing of the insulated Y-Strainer fabricated out of MS with removable bronze screen, 3mm perforation and permanent magnet etc. complete in all respect and as per specifications and drawings. 40 mm dia -PN16 -- Insulation as per Chilled water pipe | Nos. | 0.00 | 1.00 |  | 0
109526 |  | Providing and Fixing digital type thermometers with copper well, valve probe suitable for binder test point application. 12 inch long (Insulated) | Nos. | 0.00 | 2.00 |  | 0
109527 |  | Dial Presure Guages (glycerine filled Type) with SS Encasing with isolating valve piping etc.The gauge should be with appropriate range and valve and fitted with probe suitable for binder test point application as well. 6 inch Dial (Insulated) | Nos. | 0.00 | 2.00 |  | 0
109528 |  | Providing and Fixing of automatic air vent of approved make with insulation valves as per specifications or drawings - 20mm dia | Nos. | 0.00 | 2.00 |  | 0
109529 |  | Drain Piping - Supply, Installation, testing and commissioning of UPVC condensate drain pipe along with necessary clamps, fittings sich as bends, tees, etc. it shall be insulated with 9 mm thick nitrile foam insulation in tubular form as per specifications. 32 mm dia | Mtrs. | 0.00 | 5.00 |  | 0
109530 |  | DUCTING - G.I. Sheet Metal Ducting - Factory Fabricated - Installation, Testing and Commissioning of factory fabricated GSS sheet metal rectangular ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required. |  | 0.00 | 0.00 |  | 0
109531 |  | 0.50 MM (26 Gauge) | Sqm. | 0.00 | 55.00 |  | 0
109532 |  | 0.63 MM (24 Gauge) | Sqm. | 0.00 | 60.00 |  | 0
109533 |  | 0.80 MM (22 Gauge) | Sqm. | 0.00 | 70.00 |  | 0
109534 |  | 1.00 MM (20 Gauge) | Sqm. | 0.00 | 10.00 |  | 0
109535 |  | G.I. Sheet Metal Ducting - Site Fabricated - Installation, Testing and Commissioning of site fabricated GSS sheet metal rectangular ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required. |  | 0.00 | 0.00 |  | 0
109536 |  | 0.63 MM (24 Gauge) | Sqm. | 0.00 | 15.00 |  | 0
109537 |  | 0.80 MM (22 Gauge) | Sqm. | 0.00 | 10.00 |  | 0
109538 |  | 1.00 MM (20 Gauge) | Sqm. | 0.00 | 5.00 |  | 0
109539 |  | INSULATION |  | 0.00 | 0.00 |  | 0
109540 |  | Nitrile Rubber Insulation- Class O - Supplying and fixing of closed cell elastomeric insulation of density 55 kg or cu.m.and K valueof not less than 0.037W or mk at 20 deg C as per specifications and drawings (For indoor applications) with factory Laminated 7 mill woven glass cloth |  | 0.00 | 0.00 |  | 0
109541 |  | 19 mm thick (AC Supply or Return ducts) | Sqm. | 0.00 | 120.00 |  | 0
109542 |  | 25 mm thick (Exhaust Air ducts) | Sqm. | 0.00 | 20.00 |  | 0
109543 |  | Acoustic Lining - Supplying and Application of Acoustic lining within the Supply Air duct with 15 mm thick class O open cell nitrile Rubber of density 140-160 kg. or Cubm. as per spefications. 15 MM Thick | Sqm | 0.00 | 30.00 |  | 0
109544 |  | DUCT ACCESSORIES |  | 0.00 | 0.00 |  | 0
109545 |  | Supply, Installation, Testing and Commissioning of GI multiblade volume control duct damper complete with neoprene rubber gaskets, nuts, bolts, screws linkages, flanges etc., as per specifications. | Sqm. | 0.00 | 1.00 |  | 0
109546 |  | Supply, Installation, Testing and Commissioning fixing of powder coated extruded aluminium Supply or Exhaust Air Grills with damper as per specifications | Sq.m | 0.00 | 2.00 |  | 0
109547 |  | Supply, Installation, Testing and Commissioning of Exhaust Air Opening damper complete with suitable links, lever and quadrants for manual control of airflow and with suitable links , lever and quadrants for manual control of airflow and neoprene rubber gaskets, nuts, bolts, screws, flanges etc., as per specifications | Sqm | 0.00 | 1.00 |  | 0
109548 |  | Canvas - Supply Installation of double skin fire retardant canvas connection for AHU Fan Section , Exhaust Units etc. | Sqm. | 0.00 | 10.00 |  | 0