## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
133378 | 1 | MAIN Panel |  | 0.00 | 0.00 |  | 0
133379 | A | Incoming |  | 0.00 | 0.00 |  | 0
133380 |  | 1 No. 250 amps 16 kA 440 volt TPN MCCB with Thermal Magnetic overcurrent and short circuit and with following |  | 0.00 | 0.00 |  | 0
133381 | B | Metering, Indication Protection |  | 0.00 | 0.00 |  | 0
133382 | a | 1 Nos. 6 Parameter Multi Function Mater with 3 Nos. Cast Resin CTs and MCBs |  | 0.00 | 0.00 |  | 0
133383 | b | Breaker ON OFF indication Lamps |  | 0.00 | 0.00 |  | 0
133384 | c | R-Y-B indication lamps with MCBs |  | 0.00 | 0.00 |  | 0
133385 | d | ELR with CBCT |  | 0.00 | 0.00 |  | 0
133386 | C | Bus Bar |  | 0.00 | 0.00 |  | 0
133387 |  | 300 A, TPN Al. Bus Bar of suitable length having Current density 1Amp sq.mm having high conductivity electrical grade suitable to withstand symmetrical fault level of 25 kA. Neutral busbar shall be of 100% capacity. |  | 0.00 | 0.00 |  | 0
133388 | D | Outgoings |  | 0.00 | 0.00 |  | 0
133389 | a | 7 No. 63 amps 4P MCB ( Type C) |  | 0.00 | 0.00 |  | 0
133390 | b | 5 No. 20 25 32 amps 4P MCB ( Type C) |  | 0.00 | 0.00 |  | 0
133391 | c | 8 No. 32 25 amps 2P MCB ( Type C) |  | 0.00 | 0.00 |  | 0
133392 |  | Main MDB as described above |  | 0.00 | 1.00 |  | 550000
133393 | 1.1 | DISTRIBUTION BOARDS |  | 0.00 | 0.00 |  | 0
133394 |  | Supply, erection, testing and commissioning of the following sheet steel clad wall recess mounting dust and vermin proof double door type distribution boards constructed from 16 SWG sheet steel IP 42 construction, finished with rust proof duly powder coa |  | 0.00 | 0.00 |  | 0
133395 |  | Note All MCBs in distribuition board for power circuits shall be of C curve |  | 0.00 | 0.00 |  | 0
133396 | i | Type A |  | 0.00 | 0.00 |  | 0
133397 |  | 1-63 amp FP MCB with 3 single phase banks each comprising of 63A DP RCCB(30 mA) and 6 nos. 6 16 20 25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. |  | 0.00 | 2.00 |  | 46500
133398 | ii | Type B |  | 0.00 | 0.00 |  | 0
133399 |  | 1-32 amp DP MCB + DP RCCB ( 30mA) and 12 nos. 6 16 20 25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. |  | 0.00 | 1.00 |  | 24000
133400 | ii | Type C |  | 0.00 | 0.00 |  | 0
133401 |  | 1-32 amp DP MCB + DP RCCB ( 30mA) and 8 nos. 6 16 20 25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. |  | 0.00 | 2.00 |  | 11200
133402 | iv | Type D |  | 0.00 | 0.00 |  | 0
133403 |  | 1-25 amp DP MCB + DP RCCB ( 30mA) and 6 nos. 6 16 20 25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. |  | 0.00 | 0.00 | RO | 0
133404 | 2 | Supply installation testing and commisioning 3.0 kVA online ( 1ph input and 1ph output) UPS with 15 Min power back up complete with in buit Static by pass switch , Mannual external maintenance by pass switch , Rectifiers , Sealed MF batteries etc as requ |  | 0.00 | 2.00 |  | 110000
133405 | 3 | Supply, laying, testing commissioning of following sizes of Al Cu. conductor 1.1 kV grade, armoured, XLPE insulated FRLS LT Cables Control Cables including necessary cleats, clamps etc. (Cables shall be partly laid in Pipes, O H cable tray, on wall as |  | 0.00 | 0.00 |  | 0
133406 | 3.1 | 3.5C – 120.0 (Al.) FRLS Armoured XLPE Cable |  | 0.00 | 20.00 |  | 11500
133407 | 3.2 | 4C – 4.0 (Cu.) FRLS Armoured XLPE Cable |  | 0.00 | 130.00 |  | 564
133408 | 3.3 | 3C – 4.0 (Cu.) FRLS Armoured XLPE Cable |  | 0.00 | 50.00 |  | 385
133409 | 4 | Supply, erection, testing commissioning of following sizes of cable end terminations with Double compression gland for 1.1 kV grade, XLPE insulated, Al Cu Conductor cable |  | 0.00 | 0.00 |  | 0
133410 | 4.1 | 3.5C – 120.0 (Al.) FRLS Armoured XLPE Cable |  | 0.00 | 2.00 |  | 2800
133411 | 4.2 | 4C – 4.0 (Cu.) FRLS Armoured XLPE Cable |  | 0.00 | 4.00 |  | 645
133412 | 4.3 | 3C – 4.0 (Cu.) FRLS Armoured XLPE Cable |  | 0.00 | 4.00 |  | 460
133413 | 5 | Wiring for DB Submains with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in surface concealed MS surface concealed conduit including cost of providing saddles etc as required for surface conduiting and or cost of cutting and fillin |  | 0.00 | 0.00 |  | 0
133414 | 5.1 | 4 x 16 sq.mm + 2 No. 6.0 Sq. mm in 40 mm dia MS Conduit |  | 0.00 | 95.00 |  | 1400
133415 | 5.2 | 4 x 6 sq.mm + 2 No. 4.0 Sq. mm in 32 mm dia MS Conduit |  | 0.00 | 22.00 |  | 1058
133416 | 5.3 | 2 x 6 sq.mm + 1 No. 4 Sq. mm in 25 mm dia MS Conduit |  | 0.00 | 90.00 |  | 529
133417 | 5.4 | 2 x 4 sq.mm + 1 No. 2.5 Sq. mm in 25 mm dia MS Conduit |  | 0.00 | 290.00 |  | 462
133418 | 6 | Supplying and laying of the following earthing clamped to wall with suitable clamps saddles and fixing bolts in ground including the cost of digging and back filling as required and complete as required to comply with IS 3043 1987. All copper joints shal |  | 0.00 | 0.00 |  | 0
133419 | 6.1 | 50X6 mm GI Strip |  | 0.00 | 10.00 |  | 525
133420 | 6.2 | 25X6 mm GI Strip |  | 0.00 | 20.00 |  | 225
133421 | 6.3 | 25X3 mm GI Strip |  | 0.00 | 140.00 |  | 205
133422 | 6.4 | 8 SWG Copper Wire |  | 0.00 | 70.00 |  | 210
133423 | 6.5 | 8 SWG GI Wire |  | 0.00 | 100.00 |  | 35
133424 | 6.6 | 1 Core 6.0 Sq. Mm FRLS Green Wire |  | 0.00 | 60.00 |  | 105
133425 | 7 | Supply, erection, testing commissioning of prefabricated GI Perforated type cable trays including Tees Bends Crossing Reducers Couping to be laid in cable trench, overhead on wall or hanged from ceiling complete with all accessories as require |  | 0.00 | 0.00 |  | 0
133426 | 7.1 | 150 mm x 40 x 40 x 2 mm thick |  | 0.00 | 85.00 |  | 975
133427 | 7.2 | 300 mm x 40 x 40 x 2 mm thick |  | 0.00 | 35.00 |  | 1400
133428 | 8 | Wiring for MCB controlled normal primary light points Wall Point Floor Point with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm dia 16 SWG MS conduit in wall ceiling including cost of cutting and filling chases |  | 0.00 | 9.00 |  | 3924
133429 | 9 | Wiring for secondary MCB controlled normal light points Wall Point Floor Point( Looped from above point) with 2.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm 16 SWG MS conduit in wall ceiling including cost of c |  | 0.00 | 14.00 |  | 1645
133430 | 10 | Wiring for MCB controlled Emergency primary light points Wall Point Floor Point with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm dia 16 SWG MS conduit in wall ceiling including cost of cutting and filling cha |  | 0.00 | 1.00 |  | 3924
133431 | 11 | Wiring for secondary MCB controlled Emergency light points Wall Point Floor Point( Looped from above point) with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm 16 SWG MS conduit in wall ceiling including cost o |  | 0.00 | 5.00 |  | 3924
133432 | 12 | Wiring for switch controlled primary light points with 2.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade wires (FRLS) in 25 mm dia 16 SWG MS concealed surface conduit including cost of cutting and filling chases for recessed conduiting a |  | 0.00 | 3.00 |  | 3680
133433 | 13 | Wiring for secondary Switch controlled light points ( Looped from above point) with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm dia 16 SWG MS concealed surface conduit including cost of cutting and filling chase |  | 0.00 | 1.00 |  | 1645
133434 | 14 | Wiring for a 5 pin 240 volt 6 amp single phase and neutral switch socket outlet with 2.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall ceiling including cost of providing circuit wirin |  | 0.00 | 9.00 |  | 5710
133435 | 15 | Wiring same as in Item 14 above looped from an adjacent 6 amp switch socket outlet as required and providing and fixing of a modular type 5 pin 240 Volt 6 amp shuttered socket outlet and a modular type 6 amp 240 Volt single pole switch in a recessed GI bo |  | 0.00 | 16.00 |  | 2300
133436 | 15 | Same as above but switch and socket provided at separate location including wiring berween switch and socket and complete as required |  | 0.00 | 0.00 | RO | 0
133437 | 17 | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (1 outlet wired on 1 circuit) with 2.5 sq. mm PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall Ceiling including t |  | 0.00 | 7.00 |  | 6300
133438 | 18 | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (1 outlet wired on 1 circuit) with 4.0 sq. mm PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall Ceiling including t |  | 0.00 | 5.00 |  | 7900
133439 | 19 | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (2 outlets wired on 1 circuit) with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS), 4.0 sq mm upto the first outlet and 2.5 sq mm from first to the secon |  | 0.00 | 3.00 |  | 10400
133440 | 20.1 | Wiring for primary switch board consisting of 3 Nos. 5 pin 240 volt 6 amp single phase and neutral switch socket outlets with 1 Nos.16A switch with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS), 2.5 sq FRLS copper wire mm in 25mm |  | 0.00 | 4.00 |  | 10400
133441 | 20.2 | Wiring for secondary switch board ( Looped from Above) consisting of 3 Nos. 5 pin 240 volt 6 amp single phase and neutral switch socket outlets with 1 Nos. 16A switch with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS), 2.5 sq FRLS |  | 0.00 | 1.00 |  | 6400
133442 | 21 | Supply installation testing and fixing 3 pin 16A 20A , 240V , single Phase metal Clad industrial socket outlet with 16A 20A DP MCB and complete in all respects( Wiring Excluded from scope of this item) |  | 0.00 | 17.00 |  | 3020
133443 | 22 | Supply installation testing and fixing 3 pin 25A 32A , 240V , single Phase metal Clad industrial socket outlet with 25A 32A DP MCB and complete in all respects( Wiring Excluded from scope of this item) |  | 0.00 | 7.00 |  | 4036
133444 | 23 | Supply installation testing and fixing 3 pin 40A , 240V , single Phase metal Clad industrial socket outlet with 40A DP MCB and complete in all respects( Wiring Excluded from scope of this item) |  | 0.00 | 0.00 | RO | 0
133445 | 24 | Supply installation testing and fixing 5 pin 32A , 415V , Three Phase metal Clad industrial socket outlet with 32A FP MCB and complete in all respects( Wiring Excluded from scope of this item) |  | 0.00 | 1.00 |  | 15200
133446 | 25 | Supply installation testing and fixing 5 pin 63A , 415V , three Phase metal Clad industrial socket outlet with 63A FP MCB and complete in all respects( Wiring Excluded from scope of this item) |  | 0.00 | 3.00 |  | 15200
133447 | 26.1 | Supply and Installation of following in wall mounted MS enclosure |  | 0.00 | 0.00 |  | 0
133448 | i | 32A 25A DP RCBO |  | 0.00 | 5.00 |  | 8400
133449 | 26.2 | Supply and Installation of following in IP 67 Rated Poly carbonate Enclosure |  | 0.00 | 0.00 |  | 0
133450 | i | 25A FP MCB + RCCB (300 mA) |  | 0.00 | 2.00 |  | 5300
133451 | 27 | Supply and installation of flush mounted (Enhanced Category 6T 568 A or B) outlets with 2 mm thick GI box complete including cutting, chases, fixing of GI boxes and making good. The plastic shall be high impact, flame-retardant, UL rate thermoplastic. |  | 0.00 | 0.00 |  | 0
133452 | i | Single outlet face plate with RJ-45 Jack with information outlet |  | 0.00 | 14.00 |  | 1075
133453 | ii | Duplex outlet face plate with RJ-45 Jack with information outlet |  | 0.00 | 4.00 |  | 600
133454 | 28 | Supply, installation, testing, commissioning and laying of Category 6A cable in existing conduits raceways including Numbering-ferruling, bunching, tagging, computerised labeling of utp cable , Input Output termination Punching at both the ends , ( |  | 0.00 | 225.00 |  | 275
133455 | 29 | Supplying,installation and commisioning of CAT-6A patch cords 2 mtrs. |  | 0.00 | 25.00 |  | 625
133456 | 30 | Supplying,installation and commisioning of CAT-6A patch cords 1 mtr. |  | 0.00 | 25.00 |  | 550
133457 | 31 | Supply , fixing Laying 16 SWG MS conduits on surface or concealed complete with PVC junction boxes, cover plates, bends, saddles, base and other accessories all made in PVC with GI screws as required to complete the job. . |  | 0.00 | 0.00 |  | 0
133458 | i | 25 mm dia 16 SWG MS conduit |  | 0.00 | 60.00 |  | 223
133459 | ii | 20 mm dia 16 SWG MS conduit |  | 0.00 | 100.00 |  | 196
133460 | 32 | Installation of following light fixtures including connections and complete in all respects |  | 0.00 | 0.00 |  | 0
133461 | i | 25 15 12Watt Recessed Down Lighter |  | 0.00 | 15.00 |  | 350
133462 | ii | Signage |  | 0.00 | 5.00 |  | 300
133463 | iii | 600mmX600mm 36-48 W LED Light |  | 0.00 | 12.00 |  | 500
133464 | iv | 2 X 26W LED FTL |  | 0.00 | 3.00 |  | 250
133465 | v | LED Strip Light |  | 0.00 | 10.00 |  | 230