## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
167041 | B | FIRE SPRINKLER SYSTEM |  | 0.00 | 0.00 |  | 0
167042 |  | AUTOMATIC FIRE SPRINKLER HEADS ACCESSORIES |  | 0.00 | 0.00 |  | 0
167043 | B.1 | Supply, Installation, Testing Commissioning of Automatic Concealed Fire Sprinkler Heads (Bulb type Sprinklers) with adjustable Escutcheon plates (Rosette plates). Standard Temperature Response with 5mm glass bulb, Temperature rating of 68° C, K-factor of 80, Nominal Thread size of 1 2 NPT (15mm) and a Orifice size of 13mm with a Max. Working Pressure of 12 Bar (Factory hydrostatic test presure of 35 Bar) and to be Manufactured Certified to UL 199. Shall also include suspending arrangement with ceiling wall etc. |  | 0.00 | 0.00 |  | 0
167044 | B.1.1 | Pendant type of 68° C (Finishing - Chrome Plated) | Nos | 0.00 | 6.00 |  | 0
167045 | B.1.2 | Pendant type of 93° C (Finishing - Chrome Plated) | Nos | 0.00 | 2.00 |  | 0
167046 |  | FIRE SPRINKLER PIPE VALVES ACCESSORIES |  | 0.00 | 0.00 |  | 0
167047 | B.2 | Supply, Installation, Testing Commissioning of Cast Iron Butterfly Valve slim seal PN16 (working pressure of 16 Bar) of approved make, standard flow control lever operated with stainless steel shaft disc, seat material with Black Nitrile EPDM, flanges nuts and bots etc. |  | 0.00 | 0.00 |  | 0
167048 | B.2.1 | 50 mm Dia | Nos | 0.00 | 1.00 |  | 0
167049 |  | FIRE SPRINKLER PIPING |  | 0.00 | 0.00 |  | 0
167050 | B.3 | Supply, Installation, Testing Commissioning of MS C Class Fire Sprinkler Pipe confirming to IS 1239 with all fittings like bends, tees, flanges, nut, bolt and washers etc, and proper pipe supports to not more than 3 meter apart of the pipe length. The pipe work shall be hydrostatically tested for not less than 2 hours at 15 Bar (or 1.5 times the working) pressure without leak. The pipes are to be applied with 2 coats of primer (indicated film thickness, dry 50 microns) and 2 coats of enamel finish paint of approved colour (indicated film thickness, dry 30 microns) |  | 0.00 | 0.00 |  | 0
167051 | B.3.1 | 25 mm Dia | Mtr | 0.00 | 13.00 |  | 0
167052 | B.3.2 | 32 mm Dia | Mtr | 0.00 | 4.00 |  | 0
167053 | B.3.3 | 40 mm Dia | Mtr | 0.00 | 7.00 |  | 0
167054 | B.3.4 | 50 mm Dia | Mtr | 0.00 | 4.00 |  | 0
167055 | B.3 | Supply Fixing of UL Listed Stainless Steal Braided Flexible Sprinkler Hose with a working pressure of 12 Bar, Inlet Nipple(1 (25mm) BSPT NPT connection),Outlet Reducer (1 2 (15mm) BSPT NPT connection), Isolation Ring, Gasket, Snap Clamp, T-bar bracket (TBL or TBS),Stock bar and Nuts etc. |  | 0.00 | 0.00 |  | 0
167056 | B.3.1 | Assembly Length of (1500 mm) | Nos | 0.00 | 8.00 |  | 0