## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
179174 | A | EQUIPMENTS |  | 0.00 | 0.00 |  | 0
179175 | 1 | Ductable Split unit |  | 0.00 | 0.00 |  | 0
179176 |  | Supply, installation, testing and commissioning of CONCEALED Duct type units with Scroll compressor with green Regrigerant R-410A R-32. The unit should be complete with indoor outdoor unit, condensing unit, controls, control panel, tubular type refrigerant, canvas connection remote control and drain piping. The refrigerant piping, control wiring should be based on the indoor unit and outdoor unit distance being 3 mtrs Ckt along with 13 mm thk nitrile rubber insulation. The insulated drain piping should be of 32 mm dia. and distance 3 mtrs unit. Indoor unit should be provided with thermostats and remote control. The installation should be complete with all the required accessories like the supports, clamps required to make the installation complete. The cost should also include Chasing in walls as well as all the supports needed to install the units at the higher level. |  | 0.00 | 0.00 |  | 0
179177 |  | The quoted price shall include the GI frame structure to mount the outdoor unit or to suit the site condition. |  | 0.00 | 0.00 |  | 0
179178 | 1.1 | 11 TR ( 4400 cfm) HSP split air conditioning units as described above | No. | 0.00 | 2.00 |  | 0
179179 | 2 | Supply, Installation, Testing and Commissioning of split type 4 way cassette airconditioning units, each comprising of an outdoor and a single indoor unit. Condensing unit shall be complete with hermatically sealed scroll compressor s, with aluminium fins, thermostatic expansion valve and air cooled condenser with fan. Evaporating unit shall suitable as per site requirement with swing louvers and adjustable blades from sides. Indoor Units complete with in-built drainage arrangements, fan, refrigerant liquid and refrigerant piping, cordless remote control, and fresh air port etc . The outdoor unit enclosure shall be factory painted to a smooth finish. The quoted price shall be inclusive of Anti Corrosion Treatment for remote aircooled condensers, full refrigerant charge, vibration isolation arrangement, associated electrical work and MS base frame duly painted with black enamel paint for mounting of condensing units. |  | 0.00 | 0.00 |  | 0
179180 | 2.1 | 3 TR nominal capacity split unit with scroll compressor and single Cassette type indoor unit. | Nos. | 0.00 | 1.00 |  | 0
179181 | 3 | Supplying, installing, testing and commissioning of INLINE FANS suitable for installing in any position in vertical or horizontal ducts. The casing shall be double skin, internally acoustically lined and constructed of galvanised steel. The fan shall be DIDW with forward curve impeller fitted with maintenance free external rotor motor. The motor shall be suitable for 220±10% volt single phase 50 cycles AC supply. All units shall be complete with duct flexible connector and volume control damper and static pressure or to suit the system, shall be as follows |  | 0.00 | 0.00 |  | 0
179182 | 3.1 | Capacity 100-200 CFM Static Pressure 15 mmwg | No. | 0.00 | 1.00 |  | 0