## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
154616 |  | Design, fabrication, assembling, wiring , supply Erection , Installation , testing , commissioning , delivery and shifting from store of MDB Panels fabricated out of 2mm thick for structural members (Load bearing members) and 1.6mm thick for door and covers (Non load bearing members) CRCA painted sheet steel in cubicle formation with reinforcement of suitable size angle iron, channels, T irons, flats wherever necessary for large meter boards. Cable gland plates shall be provided at top and bottom both and windows for meter reading, locking arrangement (pad-lock and seal) with wiring upto KWH meter and meter to MCB shall be done by using adequately rated flexible single core copper wire. The boards shall be treated with all anticorrosive process before painting as per standards with final approved shade of powder coated as approved, 2 nos. earthing terminals shall be provided for all panels. The boards shall be suitable for 415 V, 3 phase, 4 wire, 50 Hz supply system. Boards shall be fabricated in length, height, depth etc to match with site conditions. An approval shall be taken for each panel before manufacturing. Galvanised hardwares with zinc passivation shall be used in fabrication of boards. Note The following provisions shall be required to be made in the switchboard detailed below The Switchboard shall have provision for entry of all PVCA cables from the top or bottom as required. All live accessible parts shall be shrouded and all equipment shall be finger touch proof. The busbar insulation shall be with heat shrinkable sleeves. SMC or DMC shrouds and busbar supports shall be used. Control circuits includes breaker control switch, auto manual selector switch, anti pumping relay, spring charging trip indication, TIMER, control wiring, Auxiliary contactors MCB’s as required at site. Positive isolation of all breakers. All fault level breaking capacity indicates shall be ICS value at 415 volts (ICS = ICU = ICW = 100%). Space Heater or light or air filter shall be provided for each vertical compartment Link and drops from MCCB shall be designed for full rated current of MCCB ratings at same current density as of Main Bus Bar 2 nos. GI earth strip throughout the panel. 1 MDB A Incoming 1 No. 160 amps 16 kA 440 volt TP+NL MCCB with Thermal Magnetic overcurrent and short circuit and with following B Metering, Indication and Protection a 1 Nos. 6 Parameter Multi Function Meter with 3 Nos. Cast Resin CTs and MCBs b Breaker ON OFF indication Lamps c R-Y-B indication lamps with MCBs d Earth Leakage Relay with CBCT C Bus Bar 200 A, TPN Al. Bus Bar of suitable length having Current density 1Amp or sq.mm and having high conductivity electrical grade suitable to withstand symmetrical fault level of 16 kA. Neutral busbar shall be of 100% capacity. D Outgoings a 1 No.32 amps 4P MCB ( Type C)+ 4P RCCB (30mA) b 2 No. 63 amps 4P MCB ( Type C) c 1 No. 32 amps 4P MCB ( Type C) d 1 No. 25 amps 4P MCB ( Type C) e 2 No. 32 amps 2P MCB ( Type C) f 1 No. 25 amps 2P MCB ( Type C) DB In built(Refer SLD) 1-63 amp FP MCB with 3 single phase banks each comprising of 63A DP RCCB(30 mA) and 6 nos. 6 or 16 or 20 or 25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. Main MDB as described above, tagging to be done as per layout | Set | 0.00 | 1.00 |  | 186250
154617 |  | Supply installation testing and commisioning of 1 Incoming and 2 Outgoing panel and complete with 1 No. 200A TP+NL MCCB with TM released , R-Y-B Indication and ON-OFF Lamp as incomer and following outgoings -1 No. 160A TP+NL MCCB with TM releases -1 No. 63A FP MCB Type C and complete as required | Set | 0.00 | 1.00 |  | 52500
154618 |  | Lighting DB ( Idli ), tagging to be done as per drawings - 1-32 amp DP MCB + DP RCCB ( 30mA) and 10 nos. 6 or 16 or 20 or 25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. | Set | 0.00 | 1.00 |  | 21875
154619 |  | UPS DB, tagging to be done as per drawings. - 1-32 amp DP MCB + DP RCCB ( 30mA) and 10 nos. 6 or 16 or 20 or 25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. | Set | 0.00 | 1.00 |  | 21875
154620 |  | Supply installation testing and commisioning 3.0 kVA online ( 1ph input and 1ph output) UPS with 30 Min power back up complete with in buit Static by pass switch , Mannual external maintenance by pass switch , Rectifiers , Sealed MF batteries etc as required, stand to be included with proper fittings. | No. | 0.00 | 1.00 |  | 78750
154621 |  | Supply, laying, testing and commissioning of following sizes of Al or Cu. conductor 1.1 kV grade, armoured, XLPE insulated FRLS LT Cables or Control Cables including necessary cleats, clamps etc. (Cables shall be partly laid in Pipes, O or H cable tray, on wall as required ) |  | 0.00 | 0.00 |  | 0
154622 |  | 3.5C – 70.0 (Al.) FRLS Armoured XLPE Cable * | Mtrs | 0.00 | 20.00 |  | 812.50
154623 |  | 4C – 4.0 (Cu.) FRLS Armoured XLPE Cable | Mtrs | 0.00 | 30.00 |  | 475
154624 |  | 3C – 6.0 (Cu.) FRLS Armoured XLPE Cable | Mtrs | 0.00 | 40.00 |  | 537.50
154625 |  | *Approx and shall be as per location of point of supply |  | 0.00 | 0.00 |  | 0
154626 |  | Supply, erection, testing and commissioning of following sizes of cable end terminations with Double compression gland for 1.1 kV grade, XLPE insulated, Al or Cu Conductor cable |  | 0.00 | 0.00 |  | 0
154627 |  | 3.5C – 70.0 (Al.) FRLS Armoured XLPE Cable * | Nos. | 0.00 | 2.00 |  | 1000
154628 |  | 4C – 4.0 (Cu.) FRLS Armoured XLPE Cable | Nos. | 0.00 | 2.00 |  | 537.50
154629 |  | 3C – 6.0 (Cu.) FRLS Armoured XLPE Cable | Nos. | 0.00 | 6.00 |  | 437.50
154630 |  | Wiring for DB Submains with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in surface or concealed MS surface or concealed conduit including cost of providing saddles etc as required for surface conduiting and or or cost of cutting and filling chases as required and making suitable end termination with copper lugs complete as required and as below |  | 0.00 | 0.00 |  | 0
154631 |  | 2 x 6 sq.mm + 1 No. 4 Sq. mm in 25 mm dia MS Conduit | Mtrs | 0.00 | 20.00 |  | 1062.50
154632 |  | 2 x 4 sq.mm + 1 No. 2.5 Sq. mm in 25 mm dia MS Conduit | Mtrs | 0.00 | 65.00 |  | 625
154633 |  | Supplying and laying of the following earthing clamped to wall with suitable clamps saddles and fixing bolts or in ground including the cost of digging and back filling as required and complete as required to comply with IS 3043 1987. All copper joints shall be tinned. The rates shall be inclusive of making test joints where ever required |  | 0.00 | 0.00 |  | 0
154634 |  | 25X6 mm GI Strip | Mtrs | 0.00 | 30.00 |  | 500
154635 |  | 25X3 mm GI Strip | Mtrs | 0.00 | 60.00 |  | 300
154636 |  | 8 SWG Copper Wire | Mtrs | 0.00 | 70.00 |  | 275
154637 |  | 8 SWG GI Wire | Mtrs | 0.00 | 40.00 |  | 137.50
154638 |  | 1 Core 6.0 Sq. Mm FRLS Green Wire | Mtrs | 0.00 | 30.00 |  | 150
154639 |  | Supply, erection, testing and commissioning of prefabricated GI Perforated type cable trays including Tees or Bends or Crossing or Reducers or Couping to be laid in cable trench, overhead on wall or hanged from ceiling complete with all accessories as required including support at every 1500mm as required 150 mm x 40 x 40 x 2 mm thick | Mtrs | 0.00 | 40.00 |  | 600
154640 |  | Wiring for MCB controlled normal primary light points or Wall Point or Floor Point with 2.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm dia 16 SWG MS conduit in wall or ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq. mm PVC insulated copper conductor wire for loop earthing etc. complete as required. (Cost of MCB included in the item for per DB). | Pt | 0.00 | 8.00 |  | 2750
154641 |  | Wiring for secondary MCB controlled normal light points or Wall Point or Floor Point( Looped from above point) with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm 16 SWG MS conduit in wall or ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq mm PVC insulated copper conductor wire for loop earthing etc. complete as required. | Pt | 0.00 | 16.00 |  | 1500
154642 |  | Wiring for MCB controlled Emergency primary light points or Wall Point or Floor Point with 2.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm dia 16 SWG MS conduit in wall or ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq. mm PVC insulated copper conductor wire for loop earthing etc. complete as required. (Cost of MCB included in the item for per DB). | Pt | 0.00 | 1.00 |  | 2750
154643 |  | Wiring for secondary MCB controlled Emergency light points or Wall Point or Floor Point( Looped from above point) with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm 16 SWG MS conduit in wall or ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq mm PVC insulated copper conductor wire for loop earthing etc. complete as required. | Pt | 0.00 | 4.00 |  | 1500
154644 |  | Wiring for a 5 pin 240 volt 6 amp single phase and neutral switch socket outlet with 2.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall or ceiling including cost of providing circuit wiring with 2.5 sq mm PVC insulated stranded copper conductor 1100 volt grade wires and including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and providing and fixing of a combined 5 pin 240 volt 6 amp socket outlet with safety shutters and 6 amp 240 volt single pole grid plate mounted switch with moulded cover plate in recessed GI box and including earthing of the 3rd pin with 1.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wires complete as requied( Switch and socket shall be as approved by the architect or Client) | Pt. | 0.00 | 2.00 |  | 3625
154645 |  | Wiring same as in Item 15 above looped from an adjacent 6 amp switch socket outlet as required and providing and fixing of a modular type 5 pin 240 Volt 6 amp shuttered socket outlet and a modular type 6 amp 240 Volt single pole switch in a recessed GI boxes with internal wiring and moulded front plates complete as required. ( Switch and socket shall be as approved by the architect or Client) | Pt. | 0.00 | 3.00 |  | 1625
154646 |  | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (1 outlet wired on 1 circuit) with 2.5 sq. mm PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall or Ceiling including the cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including providing and fixing 6 pin 240 volt 16 amp socket outlet with safety shutters and 16 amp 240 volt single pole grid plate mounted modular type switch with moulded cover plate in recessed GI box and including earthing of the 3rd pin with 1.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wires and complete as requied( Switch and socket shall be as approved by the architect or Client) | Pt. | 0.00 | 5.00 |  | 4000
154647 |  | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (1 outlet wired on 1 circuit) with 4.0 sq. mm PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall or Ceiling including the cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including providing and fixing 6 pin 240 volt 16 amp socket outlet with safety shutters and 16 amp 240 volt single pole grid plate mounted modular type switch with moulded cover plate in recessed GI box and including earthing of the 3rd pin with 2.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wires and complete as requied( Switch and socket shall be as approved by the architect or Client) | Pt. | 0.00 | 6.00 |  | 4000
154648 |  | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (2 outlets wired on 1 circuit) with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS), 4.0 sq mm upto the first outlet and 2.5 sq mm from first to the second outlet in 25mm dia 16 SWG MS conduit in wall or Ceiling including cost of providing saddles etc as required for surface conduiting and or or cost of cutting and filling chases and including providing and fixing of two sets of 6 pin 240 volt 16 amp socket outlet with safety shutters and 16 amp 240 volt single pole grid plate mounted switches with moulded cover plate in a recessed GI box including earthing of the 3rd pin with 2.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wire complete as required. (Switch or Socket Shall be as per approved sample by Architect) | Pt. | 0.00 | 3.00 |  | 4625
154649 |  | Wiring for primary switch board consisting of 3 Nos. 5 pin 240 volt 6 amp single phase and neutral switch socket outlets with 1 Nos.16A switch with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS), 2.5 sq FRLS copper wire mm in 25mm dia 16 SWG MS conduit in wall or Ceiling including cost of providing saddles etc as required for surface conduiting and or or cost of cutting and filling chases and including providing and fixing prewired switch board each consisting of 3 Nos. 5 pin 240 volt 6 amp single phase and neutral switch socket outlets with 1 Nos. 16A modular switch , safety shutters in a recessed or surface GI box including earthing of the 3rd pin with 1.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wire complete as required. (Switch or Socket Shall be as per approved sample by Architect) | Pt. | 0.00 | 1.00 |  | 4500
154650 |  | Supply installation testing and fixing 3 pin 16A or 20A , 240V , single Phase metal Clad industrial socket outlet with 16A or 20A DP MCB and complete in all respects( Wiring Excluded from scope of this item) | Nos. | 0.00 | 4.00 |  | 2875
154651 |  | Supply installation testing and fixing 3 pin 25A or 32A , 240V , single Phase metal Clad industrial socket outlet with 25A or 32A DP MCB and complete in all respects( Wiring Excluded from scope of this item) | Nos. | 0.00 | 1.00 |  | 3250
154652 |  | Supply and Installation of following in wall mounted MS enclosure - 32A or 25A DP RCBO | Nos | 0.00 | 2.00 |  | 8500
154653 |  | Supply and installation of flush mounted (Enhanced Category 6T 568 A or B) outlets with 2 mm thick GI box complete including cutting, chases, fixing of GI boxes and making good. The plastic shall be high impact, flame-retardant, UL rate thermoplastic. Dust cover or blank shall be provided to protect unused faceplate openings. Termination caps and plastic cover shall be provided to protect jack wiring. |  | 0.00 | 0.00 |  | 0
154654 |  | Single outlet face plate with RJ-45 Jack with information outlet | Nos. | 0.00 | 3.00 |  | 750
154655 |  | Duplex outlet face plate with RJ-45 Jack with information outlet | Nos. | 0.00 | 1.00 |  | 1062.50
154656 |  | Supply, installation, testing, commissioning and laying of Category 6A cable in existing conduits or raceways including Numbering-ferruling, bunching, tagging, computerised labeling of utp cable , Input and Output termination or Punching at both the ends , (both side i.e. user and rack) Cable Dressing etc as required . | Mtrs | 0.00 | 11.00 |  | 118.75
154657 |  | Supplying,installation and commisioning of CAT-6A patch cords 2 mtrs. | Nos | 0.00 | 5.00 |  | 687.50
154658 |  | Supplying,installation and commisioning of CAT-6A patch cords 1 mtr. | Nos | 0.00 | 5.00 |  | 562.50
154659 |  | Supply , fixing and Laying 16 SWG MS conduits on surface or concealed complete with PVC junction boxes, cover plates, bends, saddles, base and other accessories all made in PVC with GI screws as required to complete the job. . |  | 0.00 | 0.00 |  | 0
154660 |  | 25 mm dia 16 SWG MS conduit | Mtrs | 0.00 | 30.00 |  | 187.50
154661 |  | 20 mm dia 16 SWG MS conduit | Mtrs | 0.00 | 40.00 |  | 168.75
154662 |  | Supply of rubber mat (eletrically approved) infornt of LT panel - 4ft * 2ft | nos | 0.00 | 1.00 |  | 5625
154663 |  | Eelctrical meter as approved from airport authority | nos | 0.00 | 1.00 |  | 22500
154664 |  | Installation of following light fixtures including connections and complete in all respects |  | 0.00 | 0.00 |  | 0
154665 |  | 25 or 15 or 12Watt Recessed Down Lighter | No. | 0.00 | 24.00 |  | 250
154666 |  | Signage | No. | 0.00 | 3.00 |  | 1500
154667 |  | LED Strip Light | Mtrs | 0.00 | 8.00 |  | 187.50