## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
109516 |  | Hi Side Works Air Handling Units (Indoor Type) Installation , testing commissioning Of Double skin Floor mounted or Ceiling Suspended Type air handling units of extruded aluminium section with 0.6 mm preplasticized or precoated GI sheet outside and 0.6 mm plain Galvanized sheet inside, minimum of 25 mm thick PUF insulation of 38KG or m3 , Plug Fans or DIDW Blower with TEFC motors, copper cooling coils as mentioned below , with aluminium fins, MERV-8 and MERV 13 Filters. The drain pan shall be constructed out of 18G stainless steel duly insulated. All the AHU s installed under this tender shall have IE3 motor. All the cooling coils shall be AHRI or Eurovent Certified . The AHU Coil shall be selected at 9 deg C Chilled water Inlet Temp Temperature. Approval of AHU Technical Data by consultant prior to fabrication is required. Design Parameters- 25 deg C -R.A.Temp, 55 percent RH, 9 deg C- CHW IN Water Flow Rate- 2.4 GPM or TR Ceiling Suspended Type 10035 CMH(5903 CFM)at 30 mm External Static Pressure, 6 RD Cooling Coil, Approx 9.7 TR, 1 x 2.25 KW Motor | Nos | 0.00 | 1.00 |  | 0
109517 |  | Supply , Installation, Testing and Commissioning of Digital Heating or Cooling Thermostat for Air Handling Units | Nos. | 0.00 | 1.00 |  | 0
109518 |  | Kitchen Scrubber (Dry Type)-With Fan Section Supply , Installation, Testing and Commissioning of Dry Type Scrubber each comprising of extract air intake section, electrostatic precipitation technology, dry type air cleaner to remove oil, smoke and fumes from exhaust air, as per the Specifications. Electrostatic section shall be made of 16 gauge galvanised sheet, high bake epoxy powder coated, washable type aluminium mesh filters, stainless steel spiked ionizers to create high voltage DC field, aluminum collector plates which should be alternatively charged positive and negative with large collecting area with 14 inch inch deep cell, to work as magnet for charged smoke and oil particles. Average efficiency of 90-95 percent in single pass as per ASHRAE test method. Electrostatic Precipitator should be able to charge particles from 0.01 micron to 10 microns through solid state power supply. Collector cell should be of permanent type and incorporate slide out facility for easy removal for cleaning. Power supplies shall be 100 percent solid state UL Listed, Module of capacity above 3000 CFM shall be equipped with Pulse width modulating (PWM) The system should be fitted with interlock switch for safety . The system should allow connection to a fan section to achieve 500 FPM velocity across the air Operating Voltage 220V, 50 Hz Ionizing Voltage 12.5 to 13 KVDC Collector Cell Voltage 6 to 6.5 KVDC Power Consumption Not more than 50W per cell. Capacities 5000 CFM DIDW Blower DIDW Blower, motor, V belt drive, A.V mounting, supports etc. as per Specifications Drawings Casing Factory fabricated Double Skin construction shall have 25 mm thick PUF injected Panels having density 42Kg or Cum with 0.6 mm pre-plasticized or pre-coated Galvanised steel sheet outside 0.6 mm plain Galvanised steel sheet inside and fixed on 30x30 mm hollow extruded aluminium section. Casing shall be appropriately housed both Electrostatic Modules and Fan with Drive. Accessories The cost shall include all accessories like Adjusting motor brackets,base,vee drive belt pulleys, vibration isolators, internal frame works ,canvas connection, Inlet or Outlet flange connection etc 6800 CMH (4000 CFM) DIDW Blower Capacity at 80 MM ESP 3.75 KW (3 Phase) motor | Nos | 0.00 | 1.00 |  | 0
109519 |  | Chilled Water Coil Section Supply , Installation , testing commissioning Of Double skin Floor mounted or Ceiling Suspended Type coil section enclosed in extruded aluminium section with 0.6 mm preplasticized or precoated GI sheet outside and 0.6 mm plain Galvanized sheet inside, minimum of 25 mm thick PUF insulation of 38KG or m3 , copper cooling coils as mentioned below , with aluminium fins . The drain pan shall be constructed out of 18G stainless steel duly insulated. All the cooling coils shall be AHRI or Eurovent Certified . The AHU Coil shall be selected at 9 deg C Chilled water Inlet Temp Temperature. Approval of coil section Technical Data by consultant prior to fabrication is required. 1800 CFM 6 Rd cooling coil | Nos | 0.00 | 1.00 |  | 0
109520 |  | AHU Fan Section Supply, Installation, Testing and Commissioning of Double Skin Type AHU Fan section with 0.6 mm preplasticized or precoated GI sheet outside and 0.6 mm plain Galvanized sheet inside with 25mm injected PUF insulation of 38KG or m3 , G.I. blower section, VFD Operated Plug Fans with motors , base , drive arrangement ,Filter, motor drive suitable for Outdoor Application complete as per specifications and drawings . 3600 CFM (with Backward Curve Type DIDW Blowers 2.25 KW Motor ; ESP 30 mm of wg | Nos | 0.00 | 1.00 |  | 0