## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
140154 | A | POINT WIRING - Legrand - Myrius (mechanisms - white) Range switch socket Supply, Instalation, testing comissioning of Point wiring in heavy quality (HMS (in ground slab) MMS (in wall False ceiling)) PVC electrical conduit concealed in walls, RCC slabs, RCC columns complete with necessary conduit fittings and accessories directly concealed in walls, columns etc (The point shall be measured from Switch board. Up to Six meter payment on account of DB to Switch board circuit mains is payable seperately). Conduit to be laid in columns, beams, slabs before concreting and in walls before or after the walls are raised as requird by structural restraints. making chases in wall employing motorised cutting wheels. i) Wiring with single PVC insulated stranded copper wires as current carrying conductors of specified sizes. ii ) Single PVC insulated stranded copper Internal earth conductor size 1.0 sq. mm. For light, Ceilng fn exaust fan, 6 Amp plug socket points and 2.5 4.0 Sq. mm for power plug points.(1 Nos earth wire from switch board power AC power board to DB circuit) iii) Requisite electrical accessories such as Modular Type single pole switches,3 Pin plug sockets, A oler, B Holer, ceiling roses etc. iv) Concealed switch boxes of the same make as that of modular switching accessories all for light fan bells 6 Amp plug 16 Amp plug 20 Amp AC starter switch as specified below and as per additional specifications. v) 75 mm deep junction boxes pull boxes shall be used for conduiting in slabs and 25 mm deep boxes shall be used for conduiting in unplastered walls 50mm deep junction boxes for conduting in plastered walls.The box diameter shall be 65 mm. |  | 0.00 | 0.00 |  | 0
140155 | 1.1 | Point wiring all as above for one light Ex Fan first light of a group controlled by one 6 Amp moduler type single pole switch complete with 1.5 Sq. mm single PVC insulated stranded copper wires. (Up to 6 meter) Myrius-6730 00 switch | Nos. | 0.00 | 13.00 |  | 0
140156 | 1.2 | Point wiring all as above for one light Ex Fan first light of a group controlled by one 6 Amp MCB complete with 1.5 Sq. mm single PVC insulated stranded copper wires. (Up to 6 meter) | Nos. | 0.00 | 15.00 |  | 0
140157 | 1.3 | Point wiring all as per item No. A -1.1 for every additional light controlled by the switch of first light point. (Looping Pont). | Nos. | 0.00 | 57.00 |  | 0
140158 | 1.4 | Same as per item No. A - 1.1 above but for chimney point, one 6A plug controlled by one switch at switch board with 3 Pin 6 Amp socket at chimney location. Up to 6meter. More than 6mtr charge extra | Nos. | 0.00 | 1.00 |  | 0
140159 | 1.5 | Same as per item No.A-1.1 above but for 3 Pin 5 Amp moduler type plug socket on light fan switch board including 1.5 Sq. mm PVC insulated earth wire drawn in the same conduit. | Nos. | 0.00 | 2.00 |  | 0
140160 | B | LIGHTING FITTING AND OTHER FIXTURE. |  | 0.00 | 0.00 |  | 0
140161 | 1 | Suply, Installaton,testin and commissioning in position in an approved manner, testing comissioning of fixtures as per Cat. Nos. Quoted below (wired up with necessary materials and 3 core x 22 0.3 Sq. mm insulated copper flexible wire leads.) |  | 0.00 | 0.00 |  | 0
140162 | 1.1 | Supplying and erecting Hanging Light, having mounting arrangement with board for surface type or hanging arrangement complete with 3 years warranty. | Nos. | 0.00 | 9.00 |  | 0
140163 | 1.2 | Supplying and erecting LED circular 12 W light COB Light having pressure die-cast aluminium housing, polystyrene diffuser having system lumens output of Min. 2000 Lumens, min. efficacy of 110 lumen W, CRI>80, CCT upto 6500K, Beam Angle of 120 deg., max. ripple of 5%, THD<10%, p.f. >0.95, operating range of 120-270V, surge protection of 2.5 kV, Life class of 50,000 Hrs. at L70B50, including driver, having mounting arrangement with board for surface type or spring loaded mounting clips complete with 3 years warranty. | Nos. | 0.00 | 62.00 |  | 0
140164 | 1.3 | Supplying and erecting 7 W Spot Light having pressure die-cast aluminium housing, polystyrene diffuser having system lumens output of Min. 2000 Lumens, min. efficacy of 110 lumen W, CRI>80, CCT upto 6500K, Beam Angle of 120 deg., max. ripple of 5%, THD<10%, p.f. >0.95, operating range of 120-270V, surge protection of 2.5 kV, Life class of 50,000 Hrs. at L70B50, including driver, having mounting arrangement with board for surface type or spring loaded mounting clips complete with 3 years warranty. | Nos. | 0.00 | 15.00 |  | 0
140165 | 1.4 | Supplying erecting COVE Light LED Including driver fixing all required material for strip fitting. | Mtr. | 0.00 | 120.00 |  | 0
140166 | 1.5 | Supplying erecting Decorative wall lamp fitiing Including driver fixing all required material for wall lamp fitting. | Mtr. | 0.00 | 120.00 |  | 0
140167 | C | MAINS AND CABLES AND CABLE PROTECTING PIPES. |  | 0.00 | 0.00 |  | 0
140168 | 1 | Suppling erection laying for erecting mains using following types and size of PVC insulated copper FR, stranded wires in PVC (HMS MMS) electrical conduit concealed in walls, columns , beams, slabs etc. including provision of conduit fittings conduit accessories , conduit fixing material. making chases in wall employing motorised cutting wheels. (Contractor note that every circuit should have ferual number arrangements as shown in the drawing.) |  | 0.00 | 0.00 |  | 0
140169 | 1.1 | 2 x 1.5 Sq. mm stranded copper wires in 20 25 mm conduit (Lighting ckt extra above 6 mtr) | Mtr. | 0.00 | 180.00 |  | 0
140170 | 1.2 | 2 x 1.5 + 1 x 1.5 Sq. mm stranded copper wires in 20 25 mm conduit.. (Lighting SB IP) | Mtr. | 0.00 | 150.00 |  | 0
140171 | 1.3 | 2 x 2.5 + 1 x 1.5 Sq. mm stranded copper wires in 20 25 mm conduit. (SB Power circuit for each power ) | Mtr. | 0.00 | 387.00 |  | 0
140172 | 1.4 | 2 x 4 Sq. mm + 1 x 2.5 Sq. mm stranded copper wires in 20 25mm conduit.(Geyser Power) | Mtr. | 0.00 | 210.00 |  | 0
140173 | 1.5 | 4x 10 Sq. mm + 2 x 4 Sq. mm stranded copper wires in 25 mm conduit.(ACD LDB PDB mains) | Mtr. | 0.00 | 150.00 |  | 0
140174 | D | MCB DBs, MCBs and switchgear. |  | 0.00 | 0.00 |  | 0
140175 | 1 | Supply erection for erecting by chasing in wall consealing with front face flush with wall surface complete with double single earth connection TP and N SPN MCB DBs. Similar to catalogue Nos quoted in relevent item below. Similar to ETPN VTPN of MDS HAGGER ABB in IP-43 , IK-9 construction complete with PAN BUS ASSEMBLY ,neutral bar , internal earth bus suitable for mounting ELCB RCCB, Isolator as per SLD. |  | 0.00 | 0.00 |  | 0
140176 |  | DISTRIBUTION BOARDS |  | 0.00 | 0.00 |  | 0
140177 | 1.1 | 6-way SPN Double Door DB | Nos. | 0.00 | 1.00 |  | 0
140178 | 1.2 | 6 8-way TPN Double Door DB | Nos. | 0.00 | 3.00 |  | 0
140179 |  | MCB s (SWITCHGEAR) |  | 0.00 | 0.00 |  | 0
140180 | 2 | Supply erection for erecting MCBs,Isolators, ELCB,ELMCBS in following Thermal rating. (LEGRAND- Lexic or equivalent from list of approved makes). (All switchgear are consider in panel) |  | 0.00 | 0.00 |  | 0
140181 | 2.1 | 6A to 32A SP MCB (B- series for lighting circuit and C- series for power circuit) | Nos. | 0.00 | 54.00 |  | 0
140182 | 2.2 | 20 25Amp 2-pole RCBO, 100ma leakage current. | Nos. | 0.00 | 1.00 |  | 0
140183 | 2.3 | 63 Amp 3-Phase, RCCB 100ma leakage current. | Nos. | 0.00 | 2.00 |  | 0
140184 | 2.4 | 63 Amp 3-Phase, MCB (For DISH WASH) | Nos. | 0.00 | 1.00 |  | 0
140185 | E | Supply Erection of TV RG 6 cable with ISI HMS MMS PVC pipe on in surface of walls, slabs, beams, columns through 20 25mm MMS PVC pipe with all accessories. | Mtr. | 0.00 | 90.00 |  | 0
140186 | F | Supply Erection of CAT-6 LAN cable with ISI HMS MMS PVC pipe on in surface of walls, slabs, beams, columns through 25 mm MMS PVC pipe with all accessories. | Mtr. | 0.00 | 65.00 |  | 0
140187 | G | Supply Erection of Telephone 2 pair wire cable with ISI HMS MMS PVC pipe on in surface of walls, slabs, beams, columns through 20 25 mm MMS PVC pipe with all accessories. | Mtr. | 0.00 | 45.00 |  | 0
140188 | H | 1 No 6A switch socket on 3-Mod for independent switch board Same as per item No.A-1.1 but for supply erection a set of 1 Nos. 3 pin 6 Amp flush mounting socket (shutter type), 1 Nos. 3 pin 6 Amp flush mounting switches. Circuit for the board is seperate payble. | Nos. | 0.00 | 6.00 |  | 0
140189 | I | 2 No 6A switch socket on 6-Mod for independent switch board Same as per item No.A-1.1 but for supply erection a set of 2 Nos. 3 pin 6 Amp flush mounting socket (shutter type), 2 Nos. 3 pin 6 Amp flush mounting switches (for computer TV point) Circuit for the board is seperate payble. | Nos. | 0.00 | 12.00 |  | 0
140190 | J | 1 No 16A switch socket on 3-Mod for Power board Supply erection of 1No. 16 Amp one way switch and 1 No. 16 Amp 3 pin plug socket .Complete with modular socket all required accessary wiring testing etc.Circuit for the board is separate pable. | Nos | 0.00 | 13.00 |  | 0
140191 | K | 2 No 16A switch socket on 6-Mod for Power board Supply erection of 1No. 16 Amp one way switch and 1 No. 16 Amp 3 pin plug socket .Complete with modular socket all required accessary wiring testing etc.Circuit for the board is separate pable. | Nos | 0.00 | 6.00 |  | 0
140192 | L | 3 No 16A switch socket on 12-Mod for Power board Supply erection of 1No. 16 Amp one way switch and 3 No. 16 Amp 3 pin plug socket .Complete with modular socket all required accessary wiring testing etc.Circuit for the board is separate pable. | Nos | 0.00 | 3.00 |  | 0
140193 | M | Geyser Point Supply Erection of 1No. 20 Amp DP 1-way moduler switch on 2-Mod board 20A socket on seperate 2-Mod board Complete with all required accessary wiring testing etc.Circuit for the board is separate payable. | Nos | 0.00 | 1.00 |  | 0
140194 | N | 1 No 16A switch socket with POP UP Box 3-Mod for Power board Supply erection of 1No. 16 Amp one way switch and 1 No. 16 Amp 3 pin plug socket .Complete with modular socket all required accessary wiring testing etc.Circuit for the board is separate pable. Required forTable top Board. | Nos | 0.00 | 13.00 |  | 0
140195 | O | A LAN point consisting of GI box with RJ45 Cat-6 LAN socket outlet consisting with necessary pipe entries and suitable for modular accessary with modular plate and Jack type socket suitable for T.V. system duly connected to incoming cable. erected in furniture or consealed in wall | Nos | 0.00 | 3.00 |  | 0
140196 | P | Providing Fixing plug point with 3 phase industrial socket having CRCA sheet metal enclosure with 63A, 3 pin plug and earth socket and 63A, 3 pin, plug top with 30A, triple pole MCB, mains, switchgears with continuous earth wire. | Nos | 0.00 | 1.00 |  | 0
140197 | Q | EARTHING |  | 0.00 | 0.00 |  | 0
140198 | 1 | Supply Erection of Safe Earthing Electrode, copper bonded 250 micron using mild steel pipes, super quality made of low carbon high tensile strength steel rods-99.9% pure electrolytec quality copper is molecularly bonded to nickel coated steel rods ensuring greater performance and double protection 250 mocrons copper coating under UL 467 and IEEE specificationlife span is excellent in corrosive soil. Top of the rod should be with flat of tinned copper bonded, bounding of steel with pure electrolytic quality copper, tin is applied over the copper, as per IEC-61439 recommends 12 micron of tin coating. total protection from corrosion, prevent galvanic corrosion, batter electrical contacts, complete with earthing compound powder to increased the earth conductivity by enhansing its absorption power and increases its reachness with charge carring ions, , compound is mixture of minurals having the caractor of rudusing soil resistivity absorbing retaining moisture for long period with contineous resistance agains corrosion, compound should be physically chamically stable, eco friendly certified, leaching test sulpher test to be conducted as per IEC-62561-7 standered. outer electrode dia 17.2 20 mm dia, 2 meter long as per IS 3043 1987 (code of Practice for Earthing) CI funnel with maintanance free chemical, earth masonary enclosure with CI frame with RCC fiber cover having locking arrangement complete as per IS 3043 1987 along with Electrode backfill. (Maintanance free Earthing). | Nos | 0.00 | 1.00 |  | 0
140199 | 2 | Supply Erection of Alluminiun Strip 25x5mm with supports in existing trench, duct or wall. | Mtr | 0.00 | 10.00 |  | 0