## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
94255 | 1 | PANELS, SWITCHGEARS DISTRIBUTION BOARD |  | 0.00 | 0.00 |  | 0
94256 | 1.1 | MAIN PANEL-1 | Nos. | 0.00 | 1.00 |  | 0
94257 |  | Incomer 125 AMPS 4P MCCB, 25kA with TM Based O C SC Release. |  | 0.00 | 0.00 |  | 0
94258 |  | Meter Protection ELR with CBCT; 150 5A, 15VA, CL-1 CT s -3 Nos. for Schneider make Digital Load Manager (EM 6400 NG) |  | 0.00 | 0.00 |  | 0
94259 |  | Indication Phase indicating lamps with 6A MCB |  | 0.00 | 0.00 |  | 0
94260 |  | Busbar 150A TPN Cu Busbar |  | 0.00 | 0.00 |  | 0
94261 |  | Outgoings |  | 0.00 | 0.00 |  | 0
94262 |  | a) 40A 4P MCB, 10kA, TM BASED-3 Nos. |  | 0.00 | 0.00 |  | 0
94263 |  | b) 32A 4P MCB, 10kA, TM BASED-4 Nos. |  | 0.00 | 0.00 |  | 0
94264 |  | c) 40A SP MCB, 10kA, TM BASED-2 Nos. |  | 0.00 | 0.00 |  | 0
94265 |  | d) 32A SP MCB, 10kA, TM BASED-5 Nos. |  | 0.00 | 0.00 |  | 0
94266 |  | e) 20A SP MCB, 10kA, TM BASED-5 Nos. |  | 0.00 | 0.00 |  | 0
94267 |  | f) 16A SP MCB, 10kA, TM BASED-13 Nos. |  | 0.00 | 0.00 |  | 0
94268 |  | g) 10A SP MCB, 10kA, TM BASED-4 Nos. |  | 0.00 | 0.00 |  | 0
94269 |  | h) 6A SP MCB, 10kA, TM BASED-10 Nos. |  | 0.00 | 0.00 |  | 0
94270 | 2.2 | DISTRIBUTION BOARDS |  | 0.00 | 0.00 |  | 0
94271 |  | 6 WAY TPN PPI DB - LPDB DB | Nos. | 0.00 | 1.00 |  | 0
94272 |  | Incomer 40A FP MCB 10KA 1 Nos. |  | 0.00 | 0.00 |  | 0
94273 |  | Sub- Outgoings 25 A DP RCCB 30mA- 3 Nos. |  | 0.00 | 0.00 |  | 0
94274 |  | Outgoings 6 10 16 A SP MCB B Type - 12 Nos. |  | 0.00 | 0.00 |  | 0
94275 | 2 | MV CABLES |  | 0.00 | 0.00 |  | 0
94276 | 2.1 | POWER CABLING |  | 0.00 | 0.00 |  | 0
94277 |  | Supply and laying, effecting proper connections, testing commissioning of the following sizes of 1.1 KV XLPE FRLS armoured unarmoured PVC insulated PVC sheathed aluminium copper conductor cables conforming to IS 1554 and IS 694 for Flexible copp |  | 0.00 | 0.00 |  | 0
94278 |  | Aluminium cables |  | 0.00 | 0.00 |  | 0
94279 |  | 3.5C x 70 Sq.mm. | Mtr. | 0.00 | 40.00 |  | 0
94280 | 2.2 | CABLE TERMINATION |  | 0.00 | 0.00 |  | 0
94281 |  | Making cable and terminations including brass single compression glands and crimping type copper lugs for cable sizes mentioned below for aluminium or copper. |  | 0.00 | 0.00 |  | 0
94282 |  | 3.5C x 70 Sq.mm. AL | Nos. | 0.00 | 2.00 |  | 0
94283 | 3 | RACEWAYS AND CABLE TRAYS |  | 0.00 | 0.00 |  | 0
94284 | 3.4 | CABLE TRAY Design manufacture , supply and fixing in position the cable trays of the following sizes for supporting 1.1 KV grade armoured unarmoured aluminium copper conductor cables. Fabricate the cable trays from perforated 1.6 2mm thick M.S. CRCA she |  | 0.00 | 0.00 |  | 0
94285 |  | 150 mm wide x 50 mm x 2.0 mm thk | Mtr. | 0.00 | 30.00 |  | 0
94286 | 4 | POINT WIRING |  | 0.00 | 0.00 |  | 0
94287 |  | Point wiring LENGTH from DB to SB or First Light point control be MCB shall be avg. of 15Mtr. of 3C x 2.5 sq mm FRLS PVC insulated stranded copper conductor wires. For SB to SB the length shall be measured in Mtr. |  | 0.00 | 0.00 |  | 0
94288 |  | The secondary Loop point length shall be 10Mtr from Light fixture to light fixture. If secondary point shall be operated from MCB then the length shall be 10 Mtr. |  | 0.00 | 0.00 |  | 0
94289 |  | All sockets to be checked with a Check Plug socket tester for live-neutral reverse, no earth,neutral fault, live earth reverse, neutral earth reverse. |  | 0.00 | 0.00 |  | 0
94290 |  | The Circuit No. and DB no. label shall be provided on all UPS ,RAW sockets and switchboards with label printer. |  | 0.00 | 0.00 |  | 0
94291 |  | The Length shall be paid as per the actual measurements as per following manner. |  | 0.00 | 0.00 |  | 0
94292 | 4.1 | Wiring for the Primary light points with 3C x 2.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in GI conduits in F.ceiling walls ceiling as direc­ted from Distribution Board to Switch Board including providing 6 amps flush type switches, 5 |  | 0.00 | 0.00 |  | 0
94293 |  | From DB to Normal Switch Board | Nos. | 0.00 | 3.00 |  | 0
94294 |  | From DB to Emergency Switch Board | Nos. | 0.00 | 1.00 |  | 0
94295 | 4.2 | Wiring for the following light points with 3 x 2.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in GI conduits in F.ceiling walls ceiling as direc­ted including providing 6 amps flush type switches, 5 sided G.I Boxes for housing switc­hes a |  | 0.00 | 0.00 |  | 0
94296 |  | First point controlled by one no. 6 amp switch. (upto 10Mtr.) | Nos. | 0.00 | 7.00 |  | 0
94297 |  | First point controlled by one no. 6 amp switch. For Emergency Light (upto 10Mtr.) | Nos. | 0.00 | 8.00 |  | 0
94298 | 4.3 | Same as item No. 4.2.1 4.2.2 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS PVC insulated copper conductor wire in concealed exposed GI conduit and earthing | Nos. | 0.00 | 4.00 |  | 0
94299 | 4.4 | Same as item No. 4.2.3 4.2.4 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS PVC insulated copper conductor wire in concealed exposed GI conduit and earthing For Emergency Light | Nos. | 0.00 | 4.00 |  | 0
94300 | 4.5 | Wiring for the following light points controlled by MCB in DB (Cost of MCB has been taken elsewhere in the tender) with 3C x 2.5 sq. mm FRLS PVC insulated copper conductor wires in concealed exposed GI conduits as called for and earthing. |  | 0.00 | 0.00 |  | 0
94301 |  | First point controlled by existing MCB in D.B. | Nos. | 0.00 | 9.00 |  | 0
94302 | 4.6 | Same as item No.4.5.1 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS. insulated copper conductor wire in concealed exposed GI conduit and earthing | Nos. | 0.00 | 76.00 |  | 0
94303 | 4.8 | Wiring for UPS Raw plug outlets points with 3C x 4 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS 694-1990 with latest amendments, in existing Channels con | Mtr. | 0.00 | 654.00 |  | 0
94304 | 4.9 | Wiring for UPS Raw plug outlets points with 4C x 4 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS 694-1990 with latest amendments, in existing Channels con | Mtr. | 0.00 | 400.00 |  | 0
94305 | 4.1 | Providing and fixing in position the following GI RIGID conduits including all accessories concealed in F. ceiling wall floor as required including pull boxes with 3mm thick perspex sheet cover plate complete with 1.6 mm dia. G.I. pull wires in the leng |  | 0.00 | 0.00 |  | 0
94306 |  | 20 mm dia GI Conduit | Mtr. | 0.00 | 1200.00 |  | 0
94307 |  | 25 mm dia GI Conduit | Mtr. | 0.00 | 300.00 |  | 0
94308 | 5 | MODULAR SWITCHES |  | 0.00 | 0.00 |  | 0
94309 | 5.1 | Supply, installation, testing commissioning of following types of modular switches, cover plates, 5 sided G.I. Boxes for housing the modular switches earthing complete as required. GI Boxes to have earth pin for body earthing. The Circuit No. and DB n |  | 0.00 | 0.00 |  | 0
94310 |  | 6A One Way Switch | Nos. | 0.00 | 36.00 |  | 0
94311 |  | 6A 5 pin Socket - 1Nos. 6A Switch - 1Nos. | Nos. | 0.00 | 22.00 |  | 0
94312 |  | 6 16A Socket outlet - 1Nos. 16A Switch - 1Nos.(Raw UPS Power) | Nos. | 0.00 | 20.00 |  | 0
94313 |  | 5 15 amps Switch Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | Nos. | 0.00 | 15.00 |  | 0
94314 |  | 20 Amp 1- Ph Industrial Socket (Metal Clad) | Nos. | 0.00 | 4.00 |  | 0
94315 |  | 32 Amp 3- Ph Industrial Socket (Metal Clad) | Nos. | 0.00 | 5.00 |  | 0
94316 |  | 20 Amp 1- Ph Electrical Outlet | Nos. | 0.00 | 0.00 |  | 0
94317 |  | Data Outlet (RJ-45) | Nos. | 0.00 | 4.00 |  | 0
94318 |  | Telephone Outlet (RJ-11) | Nos. | 0.00 | 2.00 |  | 0
94319 | 6 | GENERAL EARTHING |  | 0.00 | 0.00 |  | 0
94320 | 6.1 | Supplying and erecting following GI strip used for earthing on wall with necessary MS clamps fixed on wall Cable trays Hume pipes etc. The jointes shall be Bolted Welded. The joints shall be painted with bituminous paint in an approved manner. |  | 0.00 | 0.00 |  | 0
94321 |  | 25 x 3 mm | Mtr. | 0.00 | 22.00 |  | 0
94322 | 6.2 | Supplying and erecting bare Copper conductor of following sizes |  | 0.00 | 0.00 |  | 0
94323 |  | 8 SWG | Mtr. | 0.00 | 50.00 |  | 0
94324 | 7 | LIGHT FIXTURES INSTALLATION |  | 0.00 | 0.00 |  | 0
94325 | 7.1 | Receiving from Store, Installation, testing commissioning of following light fixtures with complete installation hardwares including Anchor fastner, supporting Hook Rods as per final approval from Architect Client Consultant |  | 0.00 | 0.00 |  | 0
94326 |  | 12-15Watt PENDENT LAMP-1 | Nos. | 0.00 | 9.00 |  | 0
94327 |  | 10WATT ZERO WATT BULB | Nos. | 0.00 | 85.00 |  | 0
94328 |  | 600MM*600MM LED PANEL LIGHT | Mtr. | 0.00 | 8.00 |  | 0
94329 |  | 10Watt WALL LAMP | Nos. | 0.00 | 4.00 |  | 0
94330 | 8 | MISCELLANEOUS WORKS |  | 0.00 | 0.00 |  | 0
94331 | 8.1 | Supply fixing in position approved shock treatment chart written in English, Hindi and Local language. These charts shall be framed in wooden frame covered with clear glass. | Nos. | 0.00 | 1.00 |  | 0
94332 | 8.2 | Supply fixing in position the best quality danger notice boards of approved shape size as reqd. by the local Electrical Inspecting Authority written in English, Hindi local language. | Nos. | 0.00 | 1.00 |  | 0
94333 | 11 | UPS System |  | 0.00 | 0.00 |  | 0
94334 |  | Supply,Installation, testing and commissioning of following type of Online UPS Inverter as per drawings and specifications with all other accessories. | Nos. | 0.00 | 1.00 |  | 0
94335 |  | Online UPS |  | 0.00 | 0.00 |  | 0
94336 |  | 3.0.0KVA UPS |  | 0.00 | 0.00 |  | 0
94337 |  | 12V DC 25AH maintenance free batteries for 30 minutes battery backup. |  | 0.00 | 0.00 |  | 0
94338 |  | Input supply voltage -230-250 Volts |  | 0.00 | 0.00 |  | 0
94339 |  | Output voltage -220-240V+ -1% |  | 0.00 | 0.00 |  | 0
94340 |  | Voltage Regulation -Less than or equal to + - 1% |  | 0.00 | 0.00 |  | 0
94341 |  | Output frequency -50 Hz + - 0.05 Hz |  | 0.00 | 0.00 |  | 0
94342 |  | Type of cooling -Forced air cooled |  | 0.00 | 0.00 |  | 0
94343 |  | Invertor Efficiency -Better than 85% |  | 0.00 | 0.00 |  | 0
94344 |  | Output Power factor -0.8 |  | 0.00 | 0.00 |  | 0