## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
136056 | 1 | MAIN Panel |  | 0.00 | 0.00 |  | 0
136057 | A | Incoming |  | 0.00 | 0.00 |  | 0
136058 |  | 1 No. 250 amps 16 kA 440 volt TPN MCCB with Thermal Magnetic overcurrent and short circuit and with following |  | 0.00 | 0.00 |  | 0
136059 | B | Metering, Indication Protection |  | 0.00 | 0.00 |  | 0
136060 | a | 1 Nos. 6 Parameter Multi Function Mater with 3 Nos. Cast Resin CTs and MCBs |  | 0.00 | 0.00 |  | 0
136061 | b | Breaker ON OFF indication Lamps |  | 0.00 | 0.00 |  | 0
136062 | c | R-Y-B indication lamps with MCBs |  | 0.00 | 0.00 |  | 0
136063 | d | ELR with CBCT |  | 0.00 | 0.00 |  | 0
136064 | C | Bus Bar |  | 0.00 | 0.00 |  | 0
136065 |  | 300 A, TPN Al. Bus Bar of suitable length having Current density 1Amp sq.mm having high conductivity electrical grade suitable to withstand symmetrical fault level of 25 kA. Neutral busbar shall be of 100% capacity. |  | 0.00 | 0.00 |  | 0
136066 | D | Outgoings |  | 0.00 | 0.00 |  | 0
136067 | a | 7 No. 63 amps 4P MCB ( Type C) |  | 0.00 | 0.00 |  | 0
136068 | b | 5 No. 20 25 32 amps 4P MCB ( Type C) |  | 0.00 | 0.00 |  | 0
136069 | c | 8 No. 32 25 amps 2P MCB ( Type C) |  | 0.00 | 0.00 |  | 0
136070 |  | Main MDB as described above |  | 0.00 | 1.00 |  | 0
136071 | 1.1 | DISTRIBUTION BOARDS |  | 0.00 | 0.00 |  | 0
136072 |  | Supply, erection, testing and commissioning of the following sheet steel clad wall recess mounting dust and vermin proof double door type distribution boards constructed from 16 SWG sheet steel IP 42 construction, finished with rust proof duly powder coa |  | 0.00 | 0.00 |  | 0
136073 |  | Note All MCBs in distribuition board for power circuits shall be of C curve |  | 0.00 | 0.00 |  | 0
136074 | i | Type A |  | 0.00 | 0.00 |  | 0
136075 |  | 1-63 amp FP MCB with 3 single phase banks each comprising of 63A DP RCCB(30 mA) and 6 nos. 6 16 20 25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. |  | 0.00 | 2.00 |  | 0
136076 | ii | Type B |  | 0.00 | 0.00 |  | 0
136077 |  | 1-32 amp DP MCB + DP RCCB ( 30mA) and 12 nos. 6 16 20 25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. |  | 0.00 | 1.00 |  | 0
136078 | ii | Type C |  | 0.00 | 0.00 |  | 0
136079 |  | 1-32 amp DP MCB + DP RCCB ( 30mA) and 8 nos. 6 16 20 25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. |  | 0.00 | 2.00 |  | 0
136080 | iv | Type D |  | 0.00 | 0.00 |  | 0
136081 |  | 1-25 amp DP MCB + DP RCCB ( 30mA) and 6 nos. 6 16 20 25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. |  | 0.00 | 0.00 | RO | 0
136082 | 2 | Supply installation testing and commisioning 3.0 kVA online ( 1ph input and 1ph output) UPS with 15 Min power back up complete with in buit Static by pass switch , Mannual external maintenance by pass switch , Rectifiers , Sealed MF batteries etc as requ |  | 0.00 | 2.00 |  | 0
136083 | 3 | Supply, laying, testing commissioning of following sizes of Al Cu. conductor 1.1 kV grade, armoured, XLPE insulated FRLS LT Cables Control Cables including necessary cleats, clamps etc. (Cables shall be partly laid in Pipes, O H cable tray, on wall as |  | 0.00 | 0.00 |  | 0
136084 | 3.1 | 3.5C – 120.0 (Al.) FRLS Armoured XLPE Cable |  | 0.00 | 20.00 |  | 0
136085 | 3.2 | 4C – 4.0 (Cu.) FRLS Armoured XLPE Cable |  | 0.00 | 130.00 |  | 0
136086 | 3.3 | 3C – 4.0 (Cu.) FRLS Armoured XLPE Cable |  | 0.00 | 50.00 |  | 0
136087 | 4 | Supply, erection, testing commissioning of following sizes of cable end terminations with Double compression gland for 1.1 kV grade, XLPE insulated, Al Cu Conductor cable |  | 0.00 | 0.00 |  | 0
136088 | 4.1 | 3.5C – 120.0 (Al.) FRLS Armoured XLPE Cable |  | 0.00 | 2.00 |  | 0
136089 | 4.2 | 4C – 4.0 (Cu.) FRLS Armoured XLPE Cable |  | 0.00 | 4.00 |  | 0
136090 | 4.3 | 3C – 4.0 (Cu.) FRLS Armoured XLPE Cable |  | 0.00 | 4.00 |  | 0
136091 | 5 | Wiring for DB Submains with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in surface concealed MS surface concealed conduit including cost of providing saddles etc as required for surface conduiting and or cost of cutting and fillin |  | 0.00 | 0.00 |  | 0
136092 | 5.1 | 4 x 16 sq.mm + 2 No. 6.0 Sq. mm in 40 mm dia MS Conduit |  | 0.00 | 95.00 |  | 0
136093 | 5.2 | 4 x 6 sq.mm + 2 No. 4.0 Sq. mm in 32 mm dia MS Conduit |  | 0.00 | 22.00 |  | 0
136094 | 5.3 | 2 x 6 sq.mm + 1 No. 4 Sq. mm in 25 mm dia MS Conduit |  | 0.00 | 90.00 |  | 0
136095 | 5.4 | 2 x 4 sq.mm + 1 No. 2.5 Sq. mm in 25 mm dia MS Conduit |  | 0.00 | 290.00 |  | 0
136096 | 6 | Supplying and laying of the following earthing clamped to wall with suitable clamps saddles and fixing bolts in ground including the cost of digging and back filling as required and complete as required to comply with IS 3043 1987. All copper joints shal |  | 0.00 | 0.00 |  | 0
136097 | 6.1 | 50X6 mm GI Strip |  | 0.00 | 10.00 |  | 0
136098 | 6.2 | 25X6 mm GI Strip |  | 0.00 | 20.00 |  | 0
136099 | 6.3 | 25X3 mm GI Strip |  | 0.00 | 140.00 |  | 0
136100 | 6.4 | 8 SWG Copper Wire |  | 0.00 | 70.00 |  | 0
136101 | 6.5 | 8 SWG GI Wire |  | 0.00 | 100.00 |  | 0
136102 | 6.6 | 1 Core 6.0 Sq. Mm FRLS Green Wire |  | 0.00 | 60.00 |  | 0
136103 | 7 | Supply, erection, testing commissioning of prefabricated GI Perforated type cable trays including Tees Bends Crossing Reducers Couping to be laid in cable trench, overhead on wall or hanged from ceiling complete with all accessories as require |  | 0.00 | 0.00 |  | 0
136104 | 7.1 | 150 mm x 40 x 40 x 2 mm thick |  | 0.00 | 85.00 |  | 0
136105 | 7.2 | 300 mm x 40 x 40 x 2 mm thick |  | 0.00 | 35.00 |  | 0
136106 | 8 | Wiring for MCB controlled normal primary light points Wall Point Floor Point with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm dia 16 SWG MS conduit in wall ceiling including cost of cutting and filling chases |  | 0.00 | 9.00 |  | 0
136107 | 9 | Wiring for secondary MCB controlled normal light points Wall Point Floor Point( Looped from above point) with 2.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm 16 SWG MS conduit in wall ceiling including cost of c |  | 0.00 | 14.00 |  | 0
136108 | 10 | Wiring for MCB controlled Emergency primary light points Wall Point Floor Point with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm dia 16 SWG MS conduit in wall ceiling including cost of cutting and filling cha |  | 0.00 | 1.00 |  | 0
136109 | 11 | Wiring for secondary MCB controlled Emergency light points Wall Point Floor Point( Looped from above point) with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm 16 SWG MS conduit in wall ceiling including cost o |  | 0.00 | 5.00 |  | 0
136110 | 12 | Wiring for switch controlled primary light points with 2.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade wires (FRLS) in 25 mm dia 16 SWG MS concealed surface conduit including cost of cutting and filling chases for recessed conduiting a |  | 0.00 | 3.00 |  | 0
136111 | 13 | Wiring for secondary Switch controlled light points ( Looped from above point) with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm dia 16 SWG MS concealed surface conduit including cost of cutting and filling chase |  | 0.00 | 1.00 |  | 0
136112 | 14 | Wiring for a 5 pin 240 volt 6 amp single phase and neutral switch socket outlet with 2.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall ceiling including cost of providing circuit wirin |  | 0.00 | 9.00 |  | 0
136113 | 15 | Wiring same as in Item 14 above looped from an adjacent 6 amp switch socket outlet as required and providing and fixing of a modular type 5 pin 240 Volt 6 amp shuttered socket outlet and a modular type 6 amp 240 Volt single pole switch in a recessed GI bo |  | 0.00 | 16.00 |  | 0
136114 | 15 | Same as above but switch and socket provided at separate location including wiring berween switch and socket and complete as required |  | 0.00 | 0.00 | RO | 0
136115 | 17 | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (1 outlet wired on 1 circuit) with 2.5 sq. mm PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall Ceiling including t |  | 0.00 | 7.00 |  | 0
136116 | 18 | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (1 outlet wired on 1 circuit) with 4.0 sq. mm PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall Ceiling including t |  | 0.00 | 5.00 |  | 0
136117 | 19 | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (2 outlets wired on 1 circuit) with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS), 4.0 sq mm upto the first outlet and 2.5 sq mm from first to the secon |  | 0.00 | 3.00 |  | 0
136118 | 20.1 | Wiring for primary switch board consisting of 3 Nos. 5 pin 240 volt 6 amp single phase and neutral switch socket outlets with 1 Nos.16A switch with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS), 2.5 sq FRLS copper wire mm in 25mm |  | 0.00 | 4.00 |  | 0
136119 | 20.2 | Wiring for secondary switch board ( Looped from Above) consisting of 3 Nos. 5 pin 240 volt 6 amp single phase and neutral switch socket outlets with 1 Nos. 16A switch with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS), 2.5 sq FRLS |  | 0.00 | 1.00 |  | 0
136120 | 21 | Supply installation testing and fixing 3 pin 16A 20A , 240V , single Phase metal Clad industrial socket outlet with 16A 20A DP MCB and complete in all respects( Wiring Excluded from scope of this item) |  | 0.00 | 17.00 |  | 0
136121 | 22 | Supply installation testing and fixing 3 pin 25A 32A , 240V , single Phase metal Clad industrial socket outlet with 25A 32A DP MCB and complete in all respects( Wiring Excluded from scope of this item) |  | 0.00 | 7.00 |  | 0
136122 | 23 | Supply installation testing and fixing 3 pin 40A , 240V , single Phase metal Clad industrial socket outlet with 40A DP MCB and complete in all respects( Wiring Excluded from scope of this item) |  | 0.00 | 0.00 | RO | 0
136123 | 24 | Supply installation testing and fixing 5 pin 32A , 415V , Three Phase metal Clad industrial socket outlet with 32A FP MCB and complete in all respects( Wiring Excluded from scope of this item) |  | 0.00 | 1.00 |  | 0
136124 | 25 | Supply installation testing and fixing 5 pin 63A , 415V , three Phase metal Clad industrial socket outlet with 63A FP MCB and complete in all respects( Wiring Excluded from scope of this item) |  | 0.00 | 3.00 |  | 0
136125 | 26.1 | Supply and Installation of following in wall mounted MS enclosure |  | 0.00 | 0.00 |  | 0
136126 | i | 32A 25A DP RCBO |  | 0.00 | 5.00 |  | 0
136127 | 26.2 | Supply and Installation of following in IP 67 Rated Poly carbonate Enclosure |  | 0.00 | 0.00 |  | 0
136128 | i | 25A FP MCB + RCCB (300 mA) |  | 0.00 | 2.00 |  | 0
136129 | 27 | Supply and installation of flush mounted (Enhanced Category 6T 568 A or B) outlets with 2 mm thick GI box complete including cutting, chases, fixing of GI boxes and making good. The plastic shall be high impact, flame-retardant, UL rate thermoplastic. |  | 0.00 | 0.00 |  | 0
136130 | i | Single outlet face plate with RJ-45 Jack with information outlet |  | 0.00 | 14.00 |  | 0
136131 | ii | Duplex outlet face plate with RJ-45 Jack with information outlet |  | 0.00 | 4.00 |  | 0
136132 | 28 | Supply, installation, testing, commissioning and laying of Category 6A cable in existing conduits raceways including Numbering-ferruling, bunching, tagging, computerised labeling of utp cable , Input Output termination Punching at both the ends , ( |  | 0.00 | 225.00 |  | 0
136133 | 29 | Supplying,installation and commisioning of CAT-6A patch cords 2 mtrs. |  | 0.00 | 25.00 |  | 0
136134 | 30 | Supplying,installation and commisioning of CAT-6A patch cords 1 mtr. |  | 0.00 | 25.00 |  | 0
136135 | 31 | Supply , fixing Laying 16 SWG MS conduits on surface or concealed complete with PVC junction boxes, cover plates, bends, saddles, base and other accessories all made in PVC with GI screws as required to complete the job. . |  | 0.00 | 0.00 |  | 0
136136 | i | 25 mm dia 16 SWG MS conduit |  | 0.00 | 60.00 |  | 0
136137 | ii | 20 mm dia 16 SWG MS conduit |  | 0.00 | 100.00 |  | 0
136138 | 32 | Installation of following light fixtures including connections and complete in all respects |  | 0.00 | 0.00 |  | 0
136139 | i | 25 15 12Watt Recessed Down Lighter |  | 0.00 | 15.00 |  | 0
136140 | ii | Signage |  | 0.00 | 5.00 |  | 0
136141 | iii | 600mmX600mm 36-48 W LED Light |  | 0.00 | 12.00 |  | 0
136142 | iv | 2 X 26W LED FTL |  | 0.00 | 3.00 |  | 0
136143 | v | LED Strip Light |  | 0.00 | 10.00 |  | 0