## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
84675 | B.1 | Supply, Installation, Testing Commissioning of Fire Rated LS LSZH PVC insulated PVC sheathed, Copper conductor, Steel Tape Wire Armoured, 1100V grade cable, Number of Cable Core as per SLD Load Calculation Sheet (Main Cable) Unarmoured Single Core Wire (ECC), complete with Termination of the same with Single Compression Brass Glands, Solderless Tinned Copper Lugs, Gland earthing, etc. The cable shall be laid Underground on Cable Tray through Cable Trunking in Pipe on Wall Trench as required. Make Electrical Wires Cables Finolex, Polycab, RR Kables, KEI or equivalent. For cables laid on Cable Tray in Pipe on Wall Trench - the rate shall include necessary supporting clamping arrangements. |  | 0.00 | 0.00 |  | 0
84679 | B.1.6 | 4R x 4 SQ.MM | Mtr. | 0.00 | 20.00 |  | 0
84695 | D.1.2 | CEILING LAMP (Point Wiring only) | Nos. | 0.00 | 3.00 |  | 0
84702 | D.1.8 | Lighting Control Switch board with switches as required (Point Wiring only) | Nos. | 0.00 | 1.00 |  | 0
84713 | E.1.9 | 16A UNSWITCHED FUSED CONNECTION OUTLET WITH-OUT NEON INDICATOR | Nos. | 0.00 | 1.00 |  | 0
84715 | E.1.10 | 20A DOUBLE POLE SWITCH WITH NEON INDICATOR | Nos. | 0.00 | 1.00 |  | 0
84671 | A | METER METER PANEL |  | 0.00 | 0.00 |  | 0
84681 | B.1.7 | 1C x 16 SQ.MM | Mtr. | 0.00 | 10.00 |  | 0
84683 | B.1.9 | 1C x 4 SQ.MM | Mtr. | 0.00 | 20.00 |  | 0
84670 | A.1 | If any termination or connection of the unit services is required outside the site location (i.e., connection termination of the MEP unit to the airport MEP service or airport external façade or roof, etc.), then the contractor has to work in consultation with the airport to plan, design, and detail such connections. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor is to make good on any penetrations after installation, including providing fire seals as required as per airport requirements. |  | 0.00 | 0.00 |  | 0
84673 | A.1.1 | 250A 5A ENERGY METER (CT TYPE) | Nos. | 0.00 | 1.00 |  | 0
84669 | A | CONNECTING INTEGRATING UNIT MEP SERVICES TO AIRPORT MEP SERVICES BUILDING |  | 0.00 | 0.00 |  | 0
84678 | B.1.5 | 4R x 6 SQ.MM | Mtr. | 0.00 | 10.00 |  | 0
84677 | B.1.3 | 4R x 35 SQ.MM | Mtr. | 0.00 | 10.00 |  | 0
84682 | B.1.8 | 1C x 6 SQ.MM | Mtr. | 0.00 | 20.00 |  | 0
84690 |  | UPS DB |  | 0.00 | 0.00 |  | 0
84687 | C.1.1 | 10Way TPN Panel Board with 250A 4P MCCB incomer,and outgoings as per SLD Load Calculation Sheet. | Nos. | 0.00 | 1.00 |  | 0
84680 | B.1.7 | 1C x 35 SQ.MM | Mtr. | 0.00 | 20.00 |  | 0
84672 | A.1 | Supply, Installation, Testing Commissioning of kWH MFM Energy Meter Panel complete with Enclosure (If required as per site condition Airport TDM). Energy Meter shall be of Digital kVAH Type and Make Manufacturer from below list, or any other make with kVAH option with Approval from TS Department. For Make refer list below, Single Phase (For load below 40A) Make - MID (Algodue Electronica), Model - UEM 40-2C. Type - Direct. Three Phase (For load below 60A) Make - Secure, Model - Sprint 350, Type - Direct. Three Phase (For load above 60A) 1) Make - Secure, Model - Elite 445, Type - C.T. 2) Make - Conzerv (Schneider Electric), Model - EM6438, Type - C.T. 3) Make - L T, Model - Vega TM (WDM303FDWA1), Type - C.T. |  | 0.00 | 0.00 |  | 0
84692 | D | LIGHT FIXTURES POINT WIRING |  | 0.00 | 0.00 |  | 0
84686 |  | SMDB |  | 0.00 | 0.00 |  | 0
84674 | B | LV CABLING |  | 0.00 | 0.00 |  | 0
84694 | D.1.1 | CEILING LAMP (Point Wiring only) | Nos. | 0.00 | 4.00 |  | 0
84688 |  | LPDB |  | 0.00 | 0.00 |  | 0
84685 | C.1 | Supply, Installation, Testing Commissioning of Surface Flush mounting 10kA 25kA (As per Panel requirement) Distribution Boards. The DB shall be made out of 1.2 mm CRCA sheet steel enclosure and powder coated complete with cable gland plate knock out at the top and bottom. The DB shall have hinged lockable door. The busbar shall be tinned copper, for phases mounted on suitable type Insulator, Independent neutral busbar including inter connecting wiring earth bus on insulation mount. Make Electrical Panel DB s Breakers (MCB, RCBO, ELCB MCCB) Legrand, Siemens, ABB, Schneider or equivalent. All DB s must named as per the SLD Load Calculation Sheet. Laminated SLD Load Calculation Sheet shall be placed near to DB Panel Locations. The RCCB RCBO shall be Hpi Si series MCB s shall be B C Curve (As per requirement). |  | 0.00 | 0.00 |  | 0
84706 | E.1.1 | 13A SINGLE SWITCHED SOCKET OUTLET | Nos. | 0.00 | 18.00 |  | 0
84693 | D.1 | Supply, Installation, Testing Commissioning of Light Fixture Point wiring (Light Fixtures to be as approved by Architect Design BOQ) with Lamps, Ballasts Drivers Starters, Switches Lighting Control Switch Board with Fire Rated LS LSZH PVC insulated Flexible Copper Wires 660 1100V grade through suitable size GI Conduit Heavy Duty PVC Conduit GI Trunking (Containment size Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. carrying out Surface Concealed wiring as per site condition maintain aesthetic of the unit. Wiring shall be as per IS 732. Make Light Fixtures Philips, Wipro, Crompton, Syska or equivalent. Make PVC Conduits Sudhakar, Shakti or equivalent. Make GI Conduits Techno Flex India, K. M. Cables Conduits or equivalent with Airport approval. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports brackets for conduit and Trunking suspension. |  | 0.00 | 0.00 |  | 0
84696 | D.1.3 | DOWN LIGHT (Point Wiring only) | Nos. | 0.00 | 55.00 |  | 0
84707 | E.1.2 | 13A DUAL SWITCHED SOCKET OUTLET | Nos. | 0.00 | 9.00 |  | 0
84703 | D.1.9 | EXIT LIGHT (Wall Ceiling Mounted) | Nos. | 0.00 | 3.00 |  | 0
84697 | D.1.4 | 600 X 600MM LED PANEL LIGHT(Point Wiring only) | Nos. | 0.00 | 13.00 |  | 0
84708 | E.1.4 | 13A DUAL SWITCHED SOCKET OUTLET + DUAL USB PORT | Nos. | 0.00 | 5.00 |  | 0
84698 | D.1.5 | TRACK LIGHT BLACK FINISH (600X600MM) (Point Wiring only) | Nos. | 0.00 | 5.00 |  | 0
84700 | D.1.8 | INDICATIVE LOCATION OF SUSPENDED LIT SIGNAGE(Point Wiring only) | Nos. | 0.00 | 1.00 |  | 0
84714 | E.1.9 | 20A UNSWITCHED FUSED CONNECTION OUTLET WITH-OUT NEON INDICATOR | Nos. | 0.00 | 1.00 |  | 0
84711 | E.1.7 | 20A SINGLE SWITCHED METAL CLAD SOCKET OUTLET | Nos. | 0.00 | 1.00 |  | 0
84712 | E.1.8 | 20A SINGLE SWITCHED METAL CLAD SOCKET OUTLET | Nos. | 0.00 | 1.00 |  | 0
84684 | C | DISTRIBUTION BOARDS |  | 0.00 | 0.00 |  | 0
84716 | E.1.10 | 16A DOUBLE POLE SWITCH WITH NEON INDICATOR | Nos. | 0.00 | 1.00 |  | 0
84689 | C.1.2 | 16Way TPN Panel Board with 125A 30 mA 4 P RCBO incomer,and outgoings as per SLD Load Calculation Sheet. | Nos. | 0.00 | 1.00 |  | 0
84691 | C.1.3 | 6 Way SPN Panel Board with 20A 30 mA 2P RCBO incomer and outgoings as per SLD Load Calculation Sheet. | Nos. | 0.00 | 1.00 |  | 0
84718 | E.1.13 | 63A THREE PHASE INDUSTRIAL SWITCHED SOCKET (5 PIN) (WALL MOUNTED) | Nos. | 0.00 | 1.00 |  | 0
84699 | D.1.6 | LED STRIP LIGHT WITH DIFFUSER(Point Wiring only) | Nos. | 0.00 | 1.00 |  | 0
84719 | E.1.14 | 32A THREE PHASE INDUSTRIAL SWITCHED SOCKET (5 PIN) (WALL MOUNTED) | Nos. | 0.00 | 4.00 |  | 0
84717 | E.1.11 | 20A SINGLE SWITCHED SOCKET OUTLET | Nos. | 0.00 | 1.00 |  | 0
84704 | E | WIRING DEVICES (SWITCHES SOCKETS) |  | 0.00 | 0.00 |  | 0
84720 | F | CONTAINMENT (CABLE TRAY TRUNKING) |  | 0.00 | 0.00 |  | 0
84710 | E.1.6 | 16A SINGLE SWITCHED METAL CLAD SOCKET OUTLET | Nos. | 0.00 | 19.00 |  | 0
84721 | F.1 | Supply Installation of GI Cable Tray GI Cable Trunking, through Wall Ceiling Floor as per drawings, complete with standard accessories factory made fittings, earthing throughout the run with copper braids, wall ceiling suspended supports, etc. Make Cable Management System Dudhat, Super, K.R. Power supports or equivalent with Airport approval. |  | 0.00 | 0.00 |  | 0
84725 | G | UPS SYSTEM |  | 0.00 | 0.00 |  | 0
84726 | G.1 | Supply, Installation, Testing Commissioning of UPS along with required Battery for specified back-up time, complete with Battery Stand (If required) standard accessories equipments required for complete functioning of the system, earthing, support system (if required), etc. Make UPS System Luminous, APC, Microtek or equivalent with Airport approval. |  | 0.00 | 0.00 |  | 0
84722 | F.1.1 | 100 x 100 MM CABLE TRUNKING | Mtr. | 0.00 | 9.00 |  | 0
84723 | F.1.1 | 75 x 75 MM CABLE TRUNKING | Mtr. | 0.00 | 9.00 |  | 0
84724 | F.1.2 | 50 x 50 MM CABLE TRUNKING | Mtr. | 0.00 | 18.00 |  | 0
84727 | G.1.1 | 3 KVA Single phase UPS with 30 Minute Back-up | Nos. | 0.00 | 1.00 |  | 0
84676 | B.1.1 | 4R x 95 SQ.MM | Mtr. | 0.00 | 20.00 |  | 0
84701 | D.1.7 | INDICATIVE SIGNAGE (Point Wiring only) | Nos. | 0.00 | 6.00 |  | 0
84705 | E.1 | Supply, Installation, Testing Commissioning of Wiring Devices (Switches Sockets - Face Plate Finish as approved by Architect Matching to Architecture Finishes) with Fire Rated LS LSZH PVC insulated Flexible Copper Wires 660 1100V grade through suitable size GI Conduit Heavy Duty PVC Conduit GI Trunking (Containment size Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. carrying out Surface Concealed wiring as per site condition maintain aesthetic of the unit. Wiring shall be as per IS 732. Make Switch Sockets Anchor Roma Penta, Legrand, Havells Crabtree, Finolex, L T Switchgear or equivalent. Make PVC Conduits Sudhakar, Shakti or equivalent. Make GI Conduits Techno Flex India, K. M. Cables Conduits or equivalent with Airport approval. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports brackets for conduit and Trunking suspension. |  | 0.00 | 0.00 |  | 0
84709 | E.1.5 | 16A SINGLE SWITCHED SOCKET OUTLET | Nos. | 0.00 | 12.00 |  | 0