## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
147447 | A | CONNECTING INTEGRATING UNIT MEP SERVICES TO AIRPORT MEP SERVICES BUILDING |  | 0.00 | 0.00 |  | 0
147448 | A.1 | If any termination or connection of the unit services is required outside the site location (i.e., connection termination of the MEP unit to the airport MEP service or airport external façade or roof, etc.), then the contractor has to work in consultation with the airport to plan, design, and detail such connections. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor is to make good on any penetrations after installation, including providing fire seals as required as per airport requirements. | sum | 0.00 | 0.00 | Provisional Sum | 0
147449 | B | LV CABLING |  | 0.00 | 0.00 |  | 0
147450 | B.1 | Supply, Installation, Testing Commissioning of Fire Rated LS LSZH PVC insulated PVC sheathed, Copper conductor, Steel Tape Wire Armoured, 1100V grade cable, Number of Cable Core as per SLD Load Calculation Sheet (Main Cable) Unarmoured Single Core Wire (ECC), complete with Termination of the same with Single Compression Brass Glands, Solderless Tinned Copper Lugs, Gland earthing, etc. The cable shall be laid Underground on Cable Tray through Cable Trunking in Pipe on Wall Trench as required. Make Electrical Wires Cables Finolex, Polycab, RR Kables, KEI or equivalent. For cables laid on Cable Tray in Pipe on Wall Trench - the rate shall include necessary supporting clamping arrangements. |  | 0.00 | 0.00 |  | 0
147451 | B.1.1 | 1C x 6 SQ.MM | Mtr. | 0.00 | 55.00 |  | 180
147452 | C | DISTRIBUTION BOARDS CONTROL PANELS (MDB SMDB DB HVAC CONTROL) |  | 0.00 | 0.00 |  | 0
147453 | C.1 | Supply, Installation, Testing Commissioning of Surface Flush Floor mounting 10kA 25kA Distribution Boards. The DB shall be made out of 1.2 mm CRCA sheet steel enclosure and powder coated complete with cable gland plate knock out at the top and bottom. The DB shall have hinged lockable door. The busbar shall be tinned copper, for phases mounted on suitable type Insulator, Independent neutral busbar including inter connecting wiring earth bus on insulation mount, complete with Protective devices (MCCB, MCB, RCCB, RCBO, etc.), Indicative Devices (Phase Indicative Lamps, kWH Meter, MFM, Voltmeter, Ammeter, Switches, etc.), Control Devices (Bus Coupling Contactors, Earth Leakage, Control, Over Load Relays, CT, PT, Low Voltage Power Supply Transformers Protective relays, etc.), Starter Panels (DOL Starters, Star Delta Starters, Soft Starters, VFD s, etc), Fire Alarm Interfacing circuit devices relays as per Electrical SLD Load Calculation Sheet. Make Electrical Panel DB s Breakers (MCB, RCBO, ELCB MCCB) Legrand, Siemens, ABB, Schneider or equivalent. All DB s must named as per the SLD Load Calculation Sheet. Laminated SLD Load Calculation Sheet shall be placed near to DB Panel Locations. The RCCB RCBO shall be Hpi Si series MCB s shall be B C Curve (As per requirement).LPDB |  | 0.00 | 0.00 |  | 0
147454 | C.1.1 | 6Way VTPN Panel Board with 25A 30 mA 4 P RCBO incomer,and outgoings as per SLD Load Calculation Sheet. | Nos. | 0.00 | 1.00 |  | 35000
147455 | D | WIRING DEVICES (SWITCHES SOCKETS) |  | 0.00 | 0.00 |  | 0
147456 | D.1 | Supply, Installation, Testing Commissioning of Wiring Devices (Switches Sockets - Face Plate Finish as approved by Architect Matching to Architecture Finishes) with Fire Rated LS LSZH PVC insulated Flexible Copper Wires 660 1100V grade through suitable size GI Conduit Heavy Duty PVC Conduit GI Trunking (Containment size Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. carrying out Surface Concealed wiring as per site condition maintain aesthetic of the unit. Wiring shall be as per IS 732. Make Switch Sockets Anchor Roma Penta, Legrand, Havells Crabtree, Finolex, L T Switchgear or equivalent. Make PVC Conduits Sudhakar, Shakti or equivalent. Make GI Conduits Techno Flex India, K. M. Cables Conduits or equivalent with Airport approval. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports brackets for conduit and Trunking suspension. |  | 0.00 | 0.00 |  | 0
147457 | D.1.1 | 13A SINGLE SWITCHED SOCKET OUTLET | Nos. | 0.00 | 2.00 |  | 2500
147458 | D.1.2 | 16A SINGLE SWITCHED SOCKET OUTLET | Nos. | 0.00 | 7.00 |  | 3000
147459 | D.1.3 | 20A SINGLE SWITCHED METAL CLAD SOCKET OUTLET | Nos. | 0.00 | 1.00 |  | 4500
147460 | F | DATA NETWORK SYSTEM |  | 0.00 | 0.00 |  | 0
147461 | F.1 | Supply, Installation, Testing Commissioning of Data Telephone Network System with required cabling through suitable size GI Conduit Heavy Duty PVC Conduit GI Trunking (Containment size Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with IDF Rack, etc. carrying out Surface Concealed wiring as per site condition maintain aesthetic of the unit. Make IT Cables Accessories Belden (Part Code - 7834ANC). The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports brackets for conduit and Trunking suspension. |  | 0.00 | 0.00 |  | 0
147462 | F.1.1 | Single Data outlet (RJ45) | Nos. | 0.00 | 1.00 |  | 800
147463 | G | CONTAINMENT (CABLE TRAY TRUNKING) |  | 0.00 | 0.00 |  | 0
147464 | G.1 | Supply Installation of GI Cable Tray GI Cable Trunking, through Wall Ceiling Floor as per drawings, complete with standard accessories factory made fittings, earthing throughout the run with copper braids, wall ceiling suspended supports, etc. Make Cable Management System Dudhat, Super, K.R. Power supports or equivalent with Airport approval. |  | 0.00 | 0.00 |  | 0
147465 | G.1.1 | 100 x 100 MM CABLE TRUNKING | Mtr. | 0.00 | 6.00 |  | 500