## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
164241 | 1.1 | Ceiling suspended Air Handling Unit - CHW Type |  | 0.00 | 0.00 |  | 0
164242 |  | Installation, testing and comissioning of double skin ceiling suspended air handling units complete with 25mm thick insulated panels, Forward curved DIDW Blower, cooling coil section with 6 Row CHW coil, filter section with filters, fan motor, drive set, mounting base damper etc.as per below a. Chilled water temperature entering 7 deg C exit 12 deg C b. Fan Outlet Velocity should not exceed 1800 FPM c. Coil face velocity should not exceed 500 FPM d. Filter velocity should not exceed 400 FPM (Access door and CHW pipe connection should be on LHS when viewed from filter side). |  | 0.00 | 0.00 |  | 0
164243 | a | 2000 CFM, 3.0 TR | Nos. | 0.00 | 1.00 |  | 0
164244 | b | 1600 CFM, 2.2 TR | Nos. | 0.00 | 1.00 |  | 0
164245 | 1.2 | Starter Panel |  | 0.00 | 0.00 |  | 0
164246 |  | Installation, testing and comissioning of Direct online starters suitable for motors of Air handling units of below mentioned capacities (KW HP).The starter shall comprise of all necessary power and control equipments including, Auto manual selector switch. |  | 0.00 | 0.00 |  | 0
164247 | a | 1.16 KW (1.5HP) | Nos. | 0.00 | 1.00 |  | 0
164248 | b | 1.45 KW (2 HP) | Nos. | 0.00 | 1.00 |  | 0
164249 | 1.3 | Chilled Water pipe |  | 0.00 | 0.00 |  | 0
164250 |  | Installation, testing and comissioning of chilled water pipes in MS class C with necessary clamps, vibration isolator and fittings such as bends, tees etc. but excluding valves, strainers, gauges etc. Adequately supported on rigid supports duly painted as per specification and as requirements. Note piping quantity is for single run of pipe (Measurement of Supply Return pipe individually) |  | 0.00 | 0.00 |  | 0
164251 | a | 25 mm dia. | Rmt | 0.00 | 32.00 |  | 0
164252 | b | 32 mm dia. | Rmt | 0.00 | 12.00 |  | 0
164253 | 1.4 | Chilled Water pipe Insulation |  | 0.00 | 0.00 |  | 0
164254 |  | Installation, testing and comissioning OF NITRILE RUBBER INSULATION of 19MM THICKNESS FOR FOLLOWING DIA OF PIPES. It includes insulation with self cold adhesive, tapping on chilled water pipes and fittings like valves, flanges and unions, etc. as per the approved shop drawings specifications . Note Insulation quantity is for single run of pipe (Measurement of Supply Return pipe individually) |  | 0.00 | 0.00 |  | 0
164255 | a | 25 mm dia. | Rmt | 0.00 | 32.00 |  | 0
164256 | b | 32 mm dia. | Rmt | 0.00 | 12.00 |  | 0
164257 | 2.0 | CHW AHU Valve Station |  | 0.00 | 0.00 |  | 0
164258 |  | Installation, testing and comissioning of following valve station with necessary insulation for air handling Unit. It shall include following Item 1. Ball Valve for AHU drain - 1 nos. 2. Y-Strainer - 1 nos. 3. PIBCV - 1 nos. 4. Temperature gauge - 2 nos. 5. Pressure gauge - 2 nos. 6.Air release purge valve-1 nos 7.Butterfly valve Ball valve for isolation-5 nos 8. Necessary Insulated copper Pipe - as per site condition |  | 0.00 | 0.00 |  | 0
164259 | a | 25 mm dia. | Lot | 0.00 | 1.00 |  | 0
164260 | b | 32 mm dia. | Lot | 0.00 | 1.00 |  | 0