## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
130922 |  | 1 - Kitchen Scrubber (Dry Type)-With Fan Section 1.1 - Supply , Installation, Testing and Commissioning of Dry Type Scrubber each comprising of extract air intake section, electrostatic precipitation technology, dry type air cleaner to remove oil, smoke and fumes from exhaust air, as per the Specifications. Electrostatic section shall be made of 16 gauge galvanised sheet, high bake epoxy powder coated, washable type aluminium mesh filters, stainless steel spiked ionizers to create high voltage DC field, aluminum collector plates which should be alternatively charged positive and negative with large collecting area with 14 inch deep cell, to work as magnet for charged smoke and oil particles. Average efficiency of 90-95 percent in single pass as per ASHRAE test method. Electrostatic Precipitator should be able to charge particles from 0.01 micron to 10 microns through solid state power supply. Collector cell should be of permanent type and incorporate slide out facility for easy removal for cleaning. Power supplies shall be 100 percent solid state UL Listed, Module of capacity above 3000 CFM shall be equipped with Pulse width modulating (PWM) The system should be fitted with interlock switch for safety . The system should allow connection to a fan section to achieve 500 FPM velocity across the air Operating Voltage 220V, 50 Hz Ionizing Voltage 12.5 to 13 KVDC Collector Cell Voltage 6 to 6.5 KVDC Power Consumption Not more than 50W per cell. Capacities 3000 CFM 1.2 - DIDW Blower DIDW Blower, motor, V belt drive, A.V mounting, supports etc. as per Specifications and Drawings 1.3 - Casing Factory fabricated Double Skin construction shall have 25 mm thick PUF injected Panels having density 42Kg or Cum with 0.6 mm pre-plasticized or pre-coated Galvanised steel sheet outside and 0.6 mm plain Galvanised steel sheet inside and fixed on 30x30 mm hollow extruded aluminium section. Casing shall be appropriately housed both Electrostatic Modules and Fan with Drive. 1.4 - Accessories The cost shall include all accessories like Adjusting motor brackets,base,vee drive belt and pulleys, vibration isolators, internal frame works ,canvas connection, Inlet or Outlet flange connection etc Note The Dry Scrubber shall be a single unit with 1x3000 CFM Dry Scrubber and DIDW Blower 5100 CMH (3000 CFM) DIDW Blower Capacity at 80 MM ESP 2.25 KW (3 Phase) motor | Nos | 0.00 | 1.00 |  | 0
130923 |  | AHU Fan Section Supply, Installation, Testing and Commissioning of Double Skin Type AHU Fan section with 0.6 mm preplasticized or precoated GI sheet outside and 0.6 mm plain Galvanized sheet inside with 25mm injected PUF insulation of 38KG or m3 , G.I. blower section, VFD Operated Plug Fans with motors , base , drive arrangement ,Filter, motor drive suitable for Outdoor Application complete as per specifications and drawings . 2500 CFM (with Backward Curve Type DIDW Blowers 1.5 KW Motor ; ESP 30 mm of w | Nos | 0.00 | 1.00 |  | 0
130924 |  | Inline Fans (Cabinet Type with acoustic enclosure) 200 CFM at 15 MM ESP | Nos. | 0.00 | 1.00 |  | 0