## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
87369 | C | AC PIPING AND ACCESSORIES |  | 0.00 | 0.00 |  | 0
87370 |  | AC CONDENSATE DRAIN PIPE |  | 0.00 | 0.00 |  | 0
87371 | C.1 | Supply, installation and testing of Rigid PVC condensate drain water piping of approved make with necessary supports and fittings like, U-traps, elbows, tees and reducers insulated with 9mm nitrile rubber and BOPP tape. (Make Astral, Supreme or equivalent with airport approval). |  | 0.00 | 0.00 |  | 0
87372 | C.1.1 | 25 mm Ø | Mtr | 0.00 | 7.00 |  | 340
87373 |  | AC CHILLED WATER PIPING |  | 0.00 | 0.00 |  | 0
87374 | C.2 | Supply, installation and testing of MS class (C) Pre-Insulated Chilled Water Pipe of approved make with expanded polyurethane foam (PUF) insulation of 36 kg m3 minimum density, thickness as specified below and 26 G aluminum cladding with supports and all fittings such as bends, tees, elbows, reducers, flanges, special fittings, suspension hangers, supports as applicable as per site conditions. The insulation shall completely fill the annular space between service pipe and jacket and shall be bonded to both by Cold adhesive. Rubber saddles shall be considered below supports for all the piping works. (Make Jindal (Hissar), Tata steel, Sail) |  | 0.00 | 0.00 |  | 0
87375 | C.2.1 | 32 mm Ø - (Insulation - 30 mm thick) | Mtr | 0.00 | 30.00 |  | 430
87376 | D | AC PIPING VALVES ACCESSORIES |  | 0.00 | 0.00 |  | 0
87377 | D.1 | Supply, Installation, Testing, and Commissioning BTU Meter of approved make with direct pipe connection type or operated via sensor module connected supply and return pipe with all necessary fixing and valve arrangements. LCD display (shows all water parameters), with flow rate, temperature inputs, data storage up to 365 days. The display panel shall be mounted at readable height and it shall include interconnecting wiring between the flow meter and the display panel. The unit shall be housed in a totally tamper proof box with all necessary fixing arrangements. Unit shall be compatible with facility Building Management System. (Make and model shall be as per Airport requirement) |  | 0.00 | 0.00 |  | 0
87378 | D.1.1 | 32 mm Ø - 13.2 GPM | Nos | 0.00 | 1.00 |  | 25000
87379 | D.2 | Supply, Installation, testing and commissioning of electronic, Self-balancing, Pressure independent type dynamic balancing Valve (PICV) of approved make with integrated 2 way modulating Control valves in a single body. The actuator shall be capable of accepting 0(2)-10VCD, 0(4)- 20 mA electric signal and shall provide similar transduced feedback output to control system. Valve insulation shall be same thickness for corresponding size as chilled hot water pipe insulation with all necessary fixing arrangements. Unit shall be compatible with facility Building management system. (Make Danfoss,Siemen,Flowcon,Honeywell,Anergy,Belimo,Johnsons Control) |  | 0.00 | 0.00 |  | 0
87380 | D.2.1 | 32 mm Ø - 13.2 GPM | Nos | 0.00 | 1.00 |  | 4500
87381 | D.3 | Supply, Installation, Testing, and Commissioning of Forged Brass Ball Valve with Y - Strainer of approved make with full bore lever operated and removable perforated SS mesh screen with a pressure rating of PN 16. Valve insulation shall be same thickness for corresponding size as chilled hot water pipe insulation with threaded connection ends with all necessary fixing arrangements. (Make Rapidcool,RB,Emerald,Sant,Zoloto (Itshould be PN 16.) |  | 0.00 | 0.00 |  | 0
87382 | D.3.1 | 32 mm Ø | Nos | 0.00 | 1.00 |  | 16500
87383 | D.4 | Supply, Installation, Testing, and Commissioning Forged Brass Ball Valve of approved make with full bore lever operated with a pressure rating of PN 16. Valve insulation shall be same thickness for corresponding size as chilled hot water pipe insulation with threaded connection ends with all necessary fixing arrangements. (Make Rapidcool,RB,Emerald,Sant,Zoloto (Itshould be PN 16.) |  | 0.00 | 0.00 |  | 0
87384 | D.4.1 | 32 mm Ø | Nos | 0.00 | 5.00 |  | 8600
87385 | D.5 | Supply, Installation, Testing, and Commissioning of Analog type Pressure Gauge of approved make with all necessary fixing arrangements. (Make H.Guru, Fiebig, Emerald) |  | 0.00 | 0.00 |  | 0
87386 | D.5.1 | Dial Size - 63 mm Ø | Nos | 0.00 | 2.00 |  | 4300
87387 | D.6 | Supply, Installation, Testing, and Commissioning of Analog type Thermometer of approved make with all necessary fixing arrangements. (Make H.Guru, Fiebig, Emerald) |  | 0.00 | 0.00 |  | 0
87388 | D.6.1 | Dial Size - 63 mm Ø | Nos | 0.00 | 2.00 |  | 4500
87389 | D.7 | Supply, Installation, Testing, and Commissioning of Forged Brass Drain Valve Drain Cock, of approved make rubber seal, O rings e with all necessary fixing arrangements. (Make shall be as per Airport requirement) |  | 0.00 | 0.00 |  | 0
87390 | D.7.1 | Drain Valve connected in chilled water supply line | Nos | 0.00 | 1.00 |  | 6500
87391 | D.8 | Supply, Installation, Testing, and Commissioning of Forged Brass Automatic Air Vent of approved make with all necessary fixing arrangements. (Make shall be as per Airport requirement) |  | 0.00 | 0.00 |  | 0
87392 | D.8.1 | Automatic Air Vent connected in chilled water return line | Nos | 0.00 | 1.00 |  | 12500
87393 | D.9 | Supply, installation, testing commissioning of Test point of approved make with all necessary fixing arrangements. (Make shall be as per Airport requirement) |  | 0.00 | 0.00 |  | 0
87394 | D.9.1 | Test point for supply and return lines | Nos | 0.00 | 2.00 |  | 7500
87395 | E | AIR DISTRIBUTION DUCTS |  | 0.00 | 0.00 |  | 0
87396 |  | RECTANGULAR DUCTS |  | 0.00 | 0.00 |  | 0
87397 | E.1 | Supply, installation and testing of Galvanized Iron (GI) Galvanized Steel (GS) 120GSM Zinc coated factory fabricated Square Rectangular Ducts of approved make with all necessary fittings, connections, vanes, flanges, bracings, gaskets, duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, slotted rails, threaded rods, anchor bolts, nuts, bolts, structural beam clamps as applicable. The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport local regulatory or approval body having jurisdiction. (Make Zeco, Ductofab, Waves, Rolastar or equivalent with airport approval). |  | 0.00 | 0.00 |  | 0
87398 | E.1.1 | 24 Gauge - (0.70 mm Thick) - Supply Air Duct | Sq.mtr | 0.00 | 75.00 |  | 1450
87399 | E.1.2 | 22 Gauge - (0.85 mm Thick) - Supply Air Duct | Sq.mtr | 0.00 | 3.00 |  | 1650
87400 | E.1.3 | 24 Gauge - (0.70 mm Thick) - Make-Up Air Duct | Sq.mtr | 0.00 | 33.00 |  | 1540
87401 | E.2 | Supply, installation and testing of Mild Steel (MS) Ducts fabricated with hot rolled or cold rolled black steel sheets Square Rectangular Ducts of approved make with fully welded leak proof construction with Fire rated spay coat conforming to NFPA 96 Standards. with all necessary fittings, connections, vanes, flanges, bracings, gaskets, duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, threaded rods, anchor bolts, nuts, bolts, structural beam clamps as applicable. Duct and all other accessories shall be fire resistant, The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport local regulatory or approval body having jurisdiction. (Make Zeco, Ductofab, Waves, Rolastar or equivalent with airport approval). |  | 0.00 | 0.00 |  | 0
87402 | E.2.1 | 18 Gauge - (1.21 mm Thick) - Kitchen Exhaust Air Duct | Sq.mtr | 0.00 | 42.00 |  | 2300
87403 |  | DUCT ACCESS DOORS |  | 0.00 | 0.00 |  | 0
87404 | E.3 | Supply, installation, and testing of Hinged type Duct Access Doors as per drawings and to allow easy and convenient access to equipment or any other component within ductwork with all necessary fittings, accessories and airtight gaskets etc. (Make Zeco, Ductofab, Waves, Rolastar or equivalent with airport approval). |  | 0.00 | 0.00 |  | 0
87405 | E.3.1 | 250 mm X 250 mm - (MS) | Nos | 0.00 | 4.00 |  | 15400
87406 | E.4 | Supply, installation, and testing of Insulated Flexible Duct Connectors (Canvas connection) of approved make to isolate vibrations and noises caused by air handling units or any other equipment s connected to the duct with air tight fittings with all necessary accessories. (Make shall be as per Airport requirement) |  | 0.00 | 0.00 |  | 0
87407 | E.4.1 | For FCU | Nos | 0.00 | 1.00 |  | 3500
87408 | F | AIR DISTRIBUTION DUCT - THERMAL INSULATIONS ACCOUSTIC LINNINGS |  | 0.00 | 0.00 |  | 0
87409 |  | AIR DISTRIBUTION DUCT - THERMAL INSULATIONS |  | 0.00 | 0.00 |  | 0
87410 | F.1 | Supply, installation of Thermal Insulation of approved make for duct insulation using closed-cell elastomeric nitrile rubber Class O rated as per BS 476 Part 6, Black Colour with silver foil covering with having a density of 50 ± 5 Kg M3. Quote shall be inclusive of necessary Adhesive. (Make Armacell, K-Flex, A-Flex or equivalent with airport approval). |  | 0.00 | 0.00 |  | 0
87411 | F.1.1 | 19 mm thicknesses - (SAD) | Sq.mtr | 0.00 | 78.00 |  | 2430
87412 | F.1.2 | 19 mm thicknesses - (MUAD) | Sq.mtr | 0.00 | 33.00 |  | 2540
87413 | F.2 | Supply, installation of Thermal Insulation of approved make for Kitchen exhaust ducting using rockwool with silver foil covering, density of 50 Kg m3.Quoute shall be inclusive of necessary Adhesive. (Make Armacell, K-Flex, A-Flex or equivalent with airport approval). |  | 0.00 | 0.00 |  | 0
87414 | F.2.1 | 50 mm thicknesses - (KEAD) - For Kitchen Exhaust | Sq.mtr | 0.00 | 42.00 |  | 1250
87415 |  | AIR DISTRIBUTION DUCT - ACCOUSTIC LININGS |  | 0.00 | 0.00 |  | 0
87416 | F.3 | Supply, installation of Acoustic Lining of approved makes for duct insulation using open cell processed elastomeric nitrile rubber, with having a density of 150 ± 10 Kg m3 Quote shall be inclusive of necessary Adhesive. (Make Armacell, K-Flex, A-Flex or equivalent with airport approval). |  | 0.00 | 0.00 |  | 0
87417 | F.3.1 | 15 mm thicknesses - (SAD) | Sq.mtr | 0.00 | 4.00 |  | 14500
87418 | G | AIR DISTRIBUTION DUCT - DAMPERS |  | 0.00 | 0.00 |  | 0
87419 |  | DUCT AIR CONTROL DAMPERS |  | 0.00 | 0.00 |  | 0
87420 | G.1 | Supply, installation, testing and commissioning of aluminum powder coated Opposed Blade Damper Collar Damper of approved make. (Make Greenheck, System Air, JCI, Caryaire or equivalent with airport approval) |  | 0.00 | 0.00 |  | 0
87421 | G.1.1 | Size - 600 x 100 mm | Nos | 0.00 | 7.00 |  | 14300
87422 | G.1.2 | Size - 450 x 450 mm | Nos | 0.00 | 4.00 |  | 12400
87423 | G.2 | Supply, installation, testing and commissioning of Aluminium powder coated Low Leakage Square Rectangular Volume Control Damper of approved make with aero-foil opposed blades and nylon gears system outside air stream with adjustable handle with position arresting bolt. (Make Greenheck, System Air, JCI, Caryaire or equivalent with airport approval) |  | 0.00 | 0.00 |  | 0
87424 | G.2.1 | Size - 600 x 200 mm | Nos | 0.00 | 1.00 |  | 12500
87425 | G.2.2 | Size - 450 x 200 mm | Nos | 0.00 | 1.00 |  | 11450
87426 | G.2.3 | Size - 500 x 300 mm | Nos | 0.00 | 1.00 |  | 10500
87427 | G.2.4 | Size - 500 x 150 mm | Nos | 0.00 | 1.00 |  | 0
87428 | G.3 | Supply, installation, testing and commissioning of MS powder coated Low Leakage Square Rectangular Volume Control Damper of approved make with aero-foil opposed blades and nylon gears system outside air stream with adjustable handle with position arresting bolt.(For Kitchen Exhaust MS duct) (Make Greenheck, System Air, JCI, Caryaire or equivalent with airport approval) |  | 0.00 | 0.00 |  | 0
87429 | G.3.1 | Size - 700 x 400 mm | Nos | 0.00 | 1.00 |  | 14300
87430 | G.3.2 | Size - 500 x 300 mm | Nos | 0.00 | 1.00 |  | 13400
87431 | G.3.3 | Size - 450 x 250 mm | Nos | 0.00 | 1.00 |  | 12400
87432 | G.3.4 | Size - 400 x 200 mm | Nos | 0.00 | 2.00 |  | 10600
87433 | H | AIR TERMINALS - (GRILLES, REGISTERS, DIFFUSERS LOUVERS) |  | 0.00 | 0.00 |  | 0
87434 |  | GRILLES |  | 0.00 | 0.00 |  | 0
87435 | H.1 | Supply, installation, testing and commissioning of Extruded Aluminium Linear Bar Grille of approved make with fixed Aerofoil blades 15° deflection with frame of 20mm flange with all necessary fixing arrangements. powder coated finish with RAL Colour as required by ID Designer Architect. (Make System Air, Caryaire, Dynacraft, Airmaster or equivalent with airport approval). |  | 0.00 | 0.00 |  | 0
87436 | H.1.1 | Neck Size - 100 mm X 600 mm - (1 - Way) | Nos | 0.00 | 2.00 |  | 4500
87437 | H.1.2 | Neck Size - 100 mm X 600 mm - (2 - Way) | Nos | 0.00 | 5.00 |  | 5400
87438 | H.2 | Supply, installation, testing and commissioning of Extruded Aluminium Non Vision Door Transfer Grille of approved make with Inverted V type blade to avoid see through Cision and both side frame which can be adjusted to varying door thickness with all necessary fixing arrangements. Powder coated finish with RAL Colour as required by ID Designer Architect. |  | 0.00 | 0.00 |  | 0
87439 | H.2.1 | 250 mm X 250 mm | Nos | 0.00 | 1.00 |  | 2500
87440 |  | DIFFUSERS |  | 0.00 | 0.00 |  | 0
87441 | H.3 | Supply, installation, testing and commissioning of Extruded Aluminium Square Ceiling Diffuser of approved make with Four way throw with all necessary fixing arrangements. Powder coated finish with RAL Colour as required by ID Designer Architect. (Make System Air, Caryaire, Dynacraft, Airmaster or equivalent with airport approval). |  | 0.00 | 0.00 |  | 0
87442 | H.3.1 | Neck Size - 450 mm X 450 mm (Outer Size - 595 mm X 595 mm) - Tegular | Nos | 0.00 | 7.00 |  | 7500
87443 | J | HVAC SERVICE IDENTIFICATION LABELS, SIGNS TAGS |  | 0.00 | 0.00 |  | 0
87444 | J.1 | All services like Ducts, Pipes need to be clearly labelled or tagged at site with service identification flow direction etc. And all equipment needs to tagged as per Airport requirements. |  | 0.00 | 0.00 |  | 0
87445 | J.1.1 | Labelling Tagging for Services and Equipment s | Lot | 0.00 | 1.00 |  | 35000
87446 | K | TESTING AND BALANCING |  | 0.00 | 0.00 |  | 0
87447 | K.1 | Air balancing of Supply, Fresh air and Exhaust air system to arrive as per design air flow rates | Lumpsum | 0.00 | 0.00 |  | 12500
87448 | K.2 | Water balancing of Entire Chilled Water piping system to arrive the designed flow rates. | Lumpsum | 0.00 | 0.00 |  | 15000
87449 | K.3 | Chilled water pipe Pressure testing at 15kgf cm2 hydrostatics pressure for a minimum 24hrs hold time .Testing should be done in the presence of Airport Concerned Persons. | Lumpsum | 0.00 | 0.00 |  | 23500