## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
41298 |  | Ceiling Suspended AHU Supplying, installing, testing and commissioning of double skin construction draw thru type Ceiling Suspended AIR HANDLING UNITS as per specification, each complete with ESP Filter (94% down to 3 microns), pre-filter section (90% down to 10 microns), min 6 Row Deep Chilled water coil of copper tube aluminium fins construction, squirrel cage induction motor, airfoil centrifugal fan belt drive and vibration isolators, coil size shall be selected for a maximum face velocity of 500 feet minute and static pressure shall be as indicated. The motor selected shall be energy efficient having efficiency (IE2) at full load ranging between 82.5% to 92% in accordance with motor rating as per specification. Motor shall be suitable for 415±10% volts, 50 cycles, 3 phase AC supply. Fan motor assembly (as whole) shall be statically and dynamically balanced to grade G 6.3 as per ISO-1940 AMCA 204-3.All units shall be complete with opposed blade volume control dampers at oulet. Duct flexible connector (fire proof) shall be provided at outlets of AHU. ( Temporary bypass arrangement in Chilled Water Line with related accessories to be considered to facilitate flushing during precommissioning and commissioning of the System). AHU Tag. Description AHU CFM TR ESP Motor HP AHU-01 Sitting area 2500 cfm 5 15 mm 2 | No. | 0.00 | 1.00 |  | 150000