## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
177255 | A | CONNECTING INTEGRATING UNIT MEP SERVICES TO AIRPORT MEP SERVICES BUILDING |  | 0.00 | 0.00 |  | 0
177256 | A.1 | If any termination or connection of the unit services is required outside the site location (i.e., connection termination of the MEP unit to the airport MEP service or airport external façade or roof, etc.), then the contractor has to work in consultation with the airport to plan, design, and detail such connections. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor is to make good on any penetrations after installation, including providing fire seals as required as per airport requirements. |  | 0.00 | 0.00 |  | 0
177257 | C | FIRE SPRINKLER SYSTEM AUTOMATIC FIRE SPRINKLER HEADS ACCESSORIES |  | 0.00 | 0.00 |  | 0
177258 | C.1 | Supply, Installation, Testing Commissioning of Automatic Fire Sprinkler Heads (Bulb-type Sprinklers) of approved make with a standard temperature response with 5mm glass bulb, Temperature rating of 68° C 93° C, Nominal Thread size of 1 2 NPT (15mm) and a Orifice size of 13mm with a Max. Working Pressure of 12 Bar (Factory hydrostatic test pressure of 35 Bar) and to be Manufactured Certified to UL 199. The quote shall also include suspending arrangements with the ceiling, wall etc. |  | 0.00 | 0.00 |  | 0
177259 | C.1.1 | Pendant type of 79° C (Finishing - Chrome Plated) | Nos | 0.00 | 4.00 |  | 2850
177260 | C.2 | Supply, Installation, Testing Commissioning of Automatic Concealed Fire Sprinkler Heads (Bulb-type Sprinklers) of approved make with adjustable Escutcheon plates (Rosette plates). standard temperature response with 5mm glass bulb, Temperature rating of 68° C, Nominal Thread size of 1 2 NPT (15mm) and an Orifice size of 13mm with a Max. Working Pressure of 12 Bar (Factory hydrostatic test pressure of 35 Bar) and to be Manufactured Certified to UL 199. The quote shall also include suspending arrangements with the ceiling, wall etc. |  | 0.00 | 0.00 |  | 0
177261 | C.2.1 | Concealed Pendant type of 68° C (Chrome Finish Plate Cover) | Nos | 0.00 | 25.00 |  | 2650
177262 | C.3 | Supply, Installation, Testing Commissioning of Automatic Fire Sprinkler Heads (Bulb-type Sprinklers) of approved make with a standard temperature response with 5mm glass bulb, Temperature rating of 68° C 93° C, Nominal Thread size of 1 2 NPT (15mm) and a Orifice size of 13mm with a Max. Working Pressure of 12 Bar (Factory hydrostatic test pressure of 35 Bar) and to be Manufactured Certified to UL 199. The quote shall also include suspending arrangements with the ceiling, wall etc. |  | 0.00 | 0.00 |  | 0
177263 | C.3.1 | Upright type of 68° C (Finishing - Chrome Plated) | Nos | 0.00 | 5.00 |  | 2350
177264 |  | FIRE SPRINKLER PIPING |  | 0.00 | 0.00 |  | 0
177265 | C.4 | Supply, Installation, Testing Commissioning of MS C Class Fire Sprinkler Pipe confirming to IS 1239 with all fittings like bends, tees, flanges, nut, bolt and washers etc, and proper pipe supports to not more than 3 meter apart of the pipe length. The pipe work shall be hydrostatically tested for not less than 2 hours at 15 Bar (or 1.5 times the working) pressure without leak. The pipes are to be applied with 2 coats of primer (indicated film thickness, dry 50 microns) and 2 coats of enamel finish paint of approved colour (indicated film thickness, dry 30 microns) |  | 0.00 | 0.00 |  | 0
177266 | C.4.1 | 25 mm Dia | Mtr | 0.00 | 10.00 |  | 1280
177267 | C.4.2 | 32 mm Dia | Mtr | 0.00 | 5.00 |  | 1490
177268 | C.4.3 | 50 mm Dia | Mtr | 0.00 | 8.00 |  | 1860
177269 | C.5 | Supply Fixing of UL Listed Stainless Steal Braided Flexible Sprinkler Hose with a working pressure of 12 Bar, Inlet Nipple(1 (25mm) BSPT NPT connection),Outlet Reducer (1 2 (15mm) BSPT NPT connection), Isolation Ring, Gasket, Snap Clamp, T-bar bracket (TBL or TBS),Stock bar and Nuts etc. |  | 0.00 | 0.00 |  | 0
177270 | C.5.1 | Assembly Length of (1500 mm) | Nos | 0.00 | 29.00 |  | 6500
177271 | F | DISMANTLING OF EXISTING FIRE SPRINKLER PIPES |  | 0.00 | 0.00 |  | 0
177272 | F.1 | Remove and dispose of the existing fire sprinkler pipe branch, fittings and supports etc. and install new fire sprinkler pipe sections to match the new design, including necessary supports. |  | 0.00 | 0.00 |  | 0
177273 | F.1.1 | Dismantling of existing fire sprinkler pipe | Lot | 0.00 | 1.00 |  | 80000
177274 | G | TESTING AND BALANCING |  | 0.00 | 0.00 |  | 0
177275 | G.1 | Checking the functionality of all installed devices, conducting alarm tests, verifying proper communication between control panels and devices, and other systems. Testing should be done in the presence of Airport Concerned Persons. | LS | 0.00 | 1.00 |  | 40000
177276 | G.2 | Sprinkler pipe Pressure testing hydrostatic pressure test of no less than 14 bar (200PSI) for 2 hours with zero loss in pressure at the reference gauge or visual observation of a leak. Testing should be done in the presence of Airport Concerned Persons. | LS | 0.00 | 1.00 |  | 25000
177277 | G.3 | Ensure all extinguishers are properly labelled, mounted, and ready for use. Training for staff on correct usage should be included. Testing should be done in the presence of Airport Concerned Persons. | LS | 0.00 | 1.00 |  | 55000