## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
148530 |  | DISTRIBUTION BOARDS - Supply, erection, testing and commissioning of the following sheet steel clad wall recess mounting dust and vermin proof double door type distribution boards constructed from 16 SWG sheet steel IP 42 construction, finished with rust proof duly powder coated in approved shade with hinged gasketed door and housing the following complete with P.V.C. insulated copper busbars rated 200 amp with interconnections, neutral and earth bar assembly per phase, earthing terminals complete as approved by Architects. Note All MCBs in distribuition board for power circuits shall be of C curve |  | 0.00 | 0.00 |  | 0
148531 |  | Lighting and Power DB with tagging as per drawings - 1-63 amp FP MCB with 3 single phase banks each comprising of 63A DP RCCB(30 mA) and 8 nos. 6 or 16 or 20 or 25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. | Set | 0.00 | 1.00 |  | 45000
148532 |  | Supply, laying, testing and commissioning of following sizes of Al or Cu. conductor 1.1 kV grade, armoured, XLPE insulated FRLS LT Cables or Control Cables including necessary cleats, clamps etc. (Cables shall be partly laid in Pipes, O or H cable tray, on wall as required ) |  | 0.00 | 0.00 |  | 0
148533 |  | 4C – 16.0 (Cu.) FRLS Armoured XLPE Cable | Mtrs | 0.00 | 20.00 |  | 1990
148534 |  | 3C – 4.0 (Cu.) FRLS Armoured XLPE Cable | Mtrs | 0.00 | 25.00 |  | 550
148535 |  | Supply, erection, testing and commissioning of following sizes of cable end terminations with Double compression gland for 1.1 kV grade, XLPE insulated, Al or Cu Conductor cable |  | 0.00 | 0.00 |  | 0
148536 |  | 4C – 16.0 (Cu.) FRLS Armoured XLPE Cable | Nos. | 0.00 | 2.00 |  | 900
148537 |  | 3C – 4.0 (Cu.) FRLS Armoured XLPE Cable | Nos. | 0.00 | 2.00 |  | 680
148538 |  | Wiring for DB Submains with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in surface or concealed MS surface or concealed conduit including cost of providing saddles etc as required for surface conduiting and or or cost of cutting and filling chases as required and making suitable end termination with copper lugs complete as required and as below |  | 0.00 | 0.00 |  | 0
148539 |  | 4 x 6 sq.mm + 2 No. 4.0 Sq. mm in 32 mm dia MS Conduit | Mtrs | 0.00 | 25.00 |  | 480
148540 |  | 2 x 4 sq.mm + 1 No. 2.5 Sq. mm in 25 mm dia MS Conduit | Mtrs | 0.00 | 115.00 |  | 290
148541 |  | Supplying and laying of the following earthing clamped to wall with suitable clamps saddles and fixing bolts or in ground including the cost of digging and back filling as required and complete as required to comply with IS 3043 1987. All copper joints shall be tinned. The rates shall be inclusive of making test joints where ever required |  | 0.00 | 0.00 |  | 0
148542 |  | 25X3 mm GI Strip | Mtrs | 0.00 | 25.00 |  | 160
148543 |  | 8 SWG Copper Wire | Mtrs | 0.00 | 30.00 |  | 400
148544 |  | 8 SWG GI Wire | Mtrs | 0.00 | 20.00 |  | 150
148545 |  | Supply, erection, testing and commissioning of prefabricated GI Perforated type cable trays including Tees or Bends or Crossing or Reducers or Couping to be laid in cable trench, overhead on wall or hanged from ceiling complete with all accessories as required including support at every 1500mm as required |  | 0.00 | 0.00 |  | 0
148546 |  | 150 mm x 40 x 40 x 2 mm thick | Mtrs | 0.00 | 25.00 |  | 1050
148547 |  | Wiring for MCB controlled normal primary light points or Wall Point or Floor Point with 2.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm dia 16 SWG MS conduit in wall or ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq. mm PVC insulated copper conductor wire for loop earthing etc. complete as required. (Cost of MCB included in the item for per DB). | Pt | 0.00 | 1.00 |  | 1500
148548 |  | Wiring for secondary MCB controlled normal light points or Wall Point or Floor Point( Looped from above point) with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm 16 SWG MS conduit in wall or ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq mm PVC insulated copper conductor wire for loop earthing etc. complete as required. | Pt | 0.00 | 2.00 |  | 950
148549 |  | Wiring for MCB controlled Emergency primary light points or Wall Point or Floor Point with 2.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm dia 16 SWG MS conduit in wall or ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq. mm PVC insulated copper conductor wire for loop earthing etc. complete as required. (Cost of MCB included in the item for per DB). | Pt | 0.00 | 1.00 |  | 1500
148550 |  | Wiring for secondary MCB controlled Emergency light points or Wall Point or Floor Point( Looped from above point) with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm 16 SWG MS conduit in wall or ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq mm PVC insulated copper conductor wire for loop earthing etc. complete as required. | Pt | 0.00 | 1.00 |  | 950
148551 |  | Wiring for switch controlled primary light points with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade wires (FRLS) in 25 mm dia 16 SWG MS concealed or surface conduit including cost of cutting and filling chases for recessed conduiting and supports in case of Surface conduit including all bends , saddles , Junction boxes etc. including the cost of running 1.5 sq. mm PVC insulated copper conductor wire for loop earthing etc. and including providing circuit wiring with 2.5 sq mm PVC insulated stranded copper conductor 1100 volt grade FRLS wires and including the cost of providing and fixing a 6 amp 240 Volt grid plate mounted switch with moulded cover plate in GI box and complete as required ( Switch shall be as approved by the architect or Client) | Pt. | 0.00 | 1.00 |  | 1500
148552 |  | Wiring for a 5 pin 240 volt 6 amp single phase and neutral switch socket outlet with 2.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall or ceiling including cost of providing circuit wiring with 2.5 sq mm PVC insulated stranded copper conductor 1100 volt grade wires and including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and providing and fixing of a combined 5 pin 240 volt 6 amp socket outlet with safety shutters and 6 amp 240 volt single pole grid plate mounted switch with moulded cover plate in recessed GI box and including earthing of the 3rd pin with 1.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wires complete as requied( Switch and socket shall be as approved by the architect or Client) | Pt. | 0.00 | 3.00 |  | 1500
148553 |  | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (1 outlet wired on 1 circuit) with 2.5 sq. mm PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall or Ceiling including the cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including providing and fixing 6 pin 240 volt 16 amp socket outlet with safety shutters and 16 amp 240 volt single pole grid plate mounted modular type switch with moulded cover plate in recessed GI box and including earthing of the 3rd pin with 1.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wires and complete as requied( Switch and socket shall be as approved by the architect or Client) | Pt. | 0.00 | 1.00 |  | 2200
148554 |  | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (1 outlet wired on 1 circuit) with 4.0 sq. mm PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall or Ceiling including the cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including providing and fixing 6 pin 240 volt 16 amp socket outlet with safety shutters and 16 amp 240 volt single pole grid plate mounted modular type switch with moulded cover plate in recessed GI box and including earthing of the 3rd pin with 2.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wires and complete as requied( Switch and socket shall be as approved by the architect or Client) | Pt. | 0.00 | 8.00 |  | 2500
148555 |  | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (2 outlets wired on 1 circuit) with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS), 4.0 sq mm upto the first outlet and 2.5 sq mm from first to the second outlet in 25mm dia 16 SWG MS conduit in wall or Ceiling including cost of providing saddles etc as required for surface conduiting and or or cost of cutting and filling chases and including providing and fixing of two sets of 6 pin 240 volt 16 amp socket outlet with safety shutters and 16 amp 240 volt single pole grid plate mounted switches with moulded cover plate in a recessed GI box including earthing of the 3rd pin with 2.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wire complete as required. (Switch or Socket Shall be as per approved sample by Architect) | Pt. | 0.00 | 3.00 |  | 2500
148556 |  | Supply installation testing and fixing 3 pin 16A or 20A , 240V , single Phase metal Clad industrial socket outlet with 16A or 20A DP MCB and complete in all respects( Wiring Excluded from scope of this item) | Nos. | 0.00 | 3.00 |  | 5000
148557 |  | Supply installation testing and fixing 3 pin 25A or 32A , 240V , single Phase metal Clad industrial socket outlet with 25A or 32A DP MCB and complete in all respects( Wiring Excluded from scope of this item) | Nos. | 0.00 | 4.00 |  | 6000
148558 |  | Supply installation testing and fixing 5 pin 32A , 415V , Three Phase metal Clad industrial socket outlet with 32A FP MCB and complete in all respects( Wiring Excluded from scope of this item) | Nos. | 0.00 | 1.00 |  | 7500
148559 |  | Supply and Installation of following in wall mounted MS enclosure - 32A or 25A DP RCBO | Nos | 0.00 | 1.00 |  | 5000
148560 |  | Supply and installation of flush mounted (Enhanced Category 6T 568 A or B) outlets with 2 mm thick GI box complete including cutting, chases, fixing of GI boxes and making good. The plastic shall be high impact, flame-retardant, UL rate thermoplastic. Dust cover or blank shall be provided to protect unused faceplate openings. Termination caps and plastic cover shall be provided to protect jack wiring. Single outlet face plate with RJ-45 Jack with information outlet | Nos. | 0.00 | 1.00 |  | 1200
148561 |  | Supply, installation, testing, commissioning and laying of Category 6A cable in existing conduits or raceways including Numbering-ferruling, bunching, tagging, computerised labeling of utp cable , Input and Output termination or Punching at both the ends , (both side i.e. user and rack) Cable Dressing etc as required . | Mtrs | 0.00 | 30.00 |  | 150
148562 |  | Supplying,installation and commisioning of CAT-6A patch cords 2 mtrs. | Nos | 0.00 | 1.00 |  | 800
148563 |  | Supplying,installation and commisioning of CAT-6A patch cords 1 mtr. | Nos | 0.00 | 1.00 |  | 500
148564 |  | Supply , fixing and Laying 16 SWG MS conduits on surface or concealed complete with PVC junction boxes, cover plates, bends, saddles, base and other accessories all made in PVC with GI screws as required to complete the job. 20 mm dia 16 SWG MS conduit | Mtrs | 0.00 | 30.00 |  | 200
148565 |  | Supply and fixing of air curtain with automatic sensor - 4ft - Euronics or Russell | Nos. | 0.00 | 1.00 |  | 35000
148566 |  | Installation of following light fixtures including connections and complete in all respects - 25 or 15 or 12Watt Recessed Down Lighter | No. | 0.00 | 15.00 |  | 2900