## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
175672 | A | WATER SUPPLY PIPING |  | 0.00 | 0.00 |  | 0
175673 | 1 | CPVC Pipes conforming to ASTM D-2846, SDR-11 grade and CPVC solvent weld fittings like elbows, tees, couplars, brass threaded adaptors, insert ring etc. suitable for (domestic and flushing) cold applications rated, concealed piping within wall floor including jointing with fittings using solvent cement, brass threaded end fittings for making connection to fixtures. The work shall also include chasing the walls with machine wherever required for concealed piping and making good the same after laying of pipes necessary pressure testing Chasing finishing shall be done with 1 1 cement mixed mortar, restore the same original condition for internal and shaft piping, including necessary hot deep galvanised supports vertical horizontal, as per direction of Site incharge direction. [The rate shall include supply of S.S.screws and nut bolts etc.chasing in walls done by machine] (For Domestic and Flushing water-Toilet internal) (Pipe shall be tested with 1.5 times working pressure as covered in specifications) Make (Astral Ashirwad supreme Prince or Approved Equivalent) |  | 0.00 | 0.00 |  | 0
175674 | 1.1 | 20 mm Dia | R.mt | 0.00 | 35.00 |  | 671.0
175675 | 1.2 | 25 mm Dia | R.mt | 0.00 | 30.00 |  | 715.0
175676 | 1.3 | 32mm Dia | R.mt | 0.00 | 6.00 |  | 935.0
175677 | 2 | Copper pipes and tubes shall be hand tempered conforming to requirements of EN 1057 ( formerly BS 2871) Table X , half and the fittings shall confirm the EN-1254-I ( Formerly BS 864 part-02). The fittings shall be end feed capillary fittings within wall ceiling floor including cutting chasing the wall floor, jointing, making connection to fixtures, equipment and piping with purposes made connectors, etc. including insulation of closed cell elastomeric nitrile rubber. thermal conductivity of elastometric nitrile rubber shall not exceed 0.038w m deg K. The insultaion should have fire performance and thickness of nitrile rubber should be 9mm (for hot water piping) |  | 0.00 | 0.00 |  | 0
175678 | 2.1 | 20mm Dia | R.mt | 0.00 | 35.00 |  | 2270.0
175679 | 2.2 | 25mm Dia | R.mt | 0.00 | 15.00 |  | 2570.0
175680 | 2 | Providing Fixing of forged brass lever operated Ball Valves (10Kg Sq.cm). Valve shall have with unions. Make Leader Neta Zolotto or approved Equivalent |  | 0.00 | 0.00 |  | 0
175681 | 2.1 | 20mm Dia | Nos. | 0.00 | 4.00 |  | 2750.0
175682 | 2.3 | 32mm Dia | Nos. | 0.00 | 1.00 |  | 3850.0
175683 | 3 | Providing ,fixing, testing and commissioning Electromagnetic flow meter-flow (12 GPM-0.76 LPS) including providing fixing matching with required accessories 16Kgs Sq.cm). - Contractor to check existing make and provide that. Make - ENH Porsh Marshal or approved Equivalent |  | 0.00 | 0.00 |  | 0
175684 | 3.1 | 25 mm Dia incoming line | Nos. | 0.00 | 1.00 |  | 115000.0
175685 | 4 | Supply, installation,testing commissioning of Storage Type Electric Hot Water Generator of mentioned capacity, suitable for 3 KG cm2 pressure, Wall Mounted Floor standing type, with Auto Shut-off Thermostat, along with isoltion Valves, Air Release valve, SS flexible connections andall other std accessories Make - AO Smith or Approved Equivalent |  | 0.00 | 0.00 |  | 0
175686 | 4.2 | 20 L Capacity | Nos. | 0.00 | 1.00 |  | 25000.0
175687 | 7 | Supply, Installation, Commissioning Testing for Booster pump for Ro water supply WITH FLOW SWITCH GRAVITATIONAL FLOW (top to bottom flow) with both side Sensor operations- A) 3CUM PER HR. B) HEAD 25M, C) PHASE SINGLE PHASE, D) PROTECTION IP55, E) MONOBLOCK TYPE, with sensors cabling Control panel.(Pump shall be Auto fill stop and Auto empty start mechanisam) Make - Grundfoss Kirloskar Bharat Bijli Agasti or Approved Equivalent |  | 0.00 | 0.00 |  | 0
175688 | 7.1 | 0.75 HP | Nos. | 0.00 | 1.00 |  | 21750.0
175689 | 10 | Providing Fixing Brass Non Return Vavles of ISI mark. Rates are for BRASS valves Make - Make – KITZ ZOLOTO AUDCO or Approved Equivalent |  | 0.00 | 0.00 |  | 0
175690 | 12.1 | 20mm | Nos | 0.00 | 2.00 |  | 2790.0
175691 | 12.2 | 25mm | Nos | 0.00 | 2.00 |  | 3250.0
175692 | 15 | Installalation , testing commissioning of S.S. Grease trap nurgreen Make -NGT 20 ( 34.3. lit) | Nos. | 0.00 | 1.00 |  | 15750..0
175693 | 16 | Installalation , testing commissioning of S.S. Grease trap nurgreen Make -NGT 14 ( 25.5. lit) | Nos. | 0.00 | 1.00 |  | 12750.0
175694 | 17 | Installalation , testing commissioning of S.S. Grease trap nurgreen Make -NGT 50 ( 72 lit) | Nos. | 0.00 | 1.00 |  | 19750.0
175695 | B | DRAINAGE |  | 0.00 | 0.00 |  | 0
175696 | 1 | UPVC-SWR pipes (working pressure 10kg cm2) conforming to IS 13592 92 and IS 14735-type-B solvent posted ( for Dia above 50mm) and for ( Dia below 50mm) shall be as per IS 4985 and 7834 Class-05 (10 kg cm2) including cutting the pipes to required lengths, laying in the position to required grade and level, jointing, supporting with PVC cleat,hot deep galvanised bracket supports,hot deep galvanised nut-bolts, anchor fastners, PVC coated U-clamp, testing and rectifying leakages for piping within vertical shafts supported on wall hung below slab etc. with all material labor complete and as directed. [The Rate shall include supply and fixing of nesessary items] Vertical line bracket shall be fixed at every 0.8 mtr to 1.00 mtr.] Make - Supreme Finolex Prince Oriplast or Approved Equivalent |  | 0.00 | 0.00 |  | 0
175697 | 1.2 | 50mm Dia | R.mt | 0.00 | 6.00 |  | 2010.0
175698 | 1.5 | 100 mm Dia | R.mt | 0.00 | 28.00 |  | 2970.0
175699 | 2 | Supply, Install PVC Floor Trap for the following pipes including making all approved quality Solvent cement joints with material labour etc. all complete as per direction of the engineer-in-charge. | Nos. | 0.00 | 1.00 |  | 2700.0
175700 | 3 | Supply, Install PVC Multi Floor Trap for the following pipes including making all approved quality Solvent cement joints with material labour etc. all complete as per direction of the engineer-in-charge. | Nos. | 0.00 | 5.00 |  | 2950.0
175701 | C | SANITARY AND C. P. FITTINGS FIXTURES |  | 0.00 | 0.00 |  | 0
175702 |  | Supply installation, testing and commissioning of sanitary and C.P. fittings( Client Architect to select the model no as required and provide fixtures) |  | 0.00 | 0.00 |  | 0
175703 | 1.12 | Under Counter Sink including waste Coupling | Nos | 0.00 | 3.00 |  | 15750.0
175704 | 1.13 | Sink Pillar Cock - Jaquar continental series | Nos | 0.00 | 3.00 |  | 8750.0
175705 | 1.15 | Angle Cock with PVC pipe connection upto WHB sink Geyser connection Jaquar continental series | Nos | 0.00 | 4.00 |  | 2150.0
175706 |  | SUB TOTAL -C-SANITARY AND C. P. FITTINGS FIXTURES ( ONLY INSTALLATIONS) |  | 0.00 | 0.00 |  | 0
175707 | D | S.S. GRATING |  | 0.00 | 0.00 |  | 0
175708 |  | Supply , installations testing and commissioning of S.S.Gratings |  | 0.00 | 0.00 |  | 0
175709 | 1 | Supply installation of S.S Grating size, 600mm x 600mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS perforated tray (304 SWR). Complete as per architectural detail drawing Site Engineer s instruction. (100 mm Dia S.S 304 grade finish unions reducers coupling or 75mm Dia S.S 304 grade finish unions reducers coupling or 50mm Dia S.S 304 grade finish unions reducers coupling) Entire Chamber will be made in 16 SWG SS 304 , Testing of Chamber as per DIAL Guideline | Nos. | 0.00 | 3.00 |  | 29750.0
175710 | 3 | Supply installation of S.S Grating size, 600mm x 600mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS Closed tray (304 SWR). Complete as per architectural detail drawing Site Engineer s instruction. ( at hook up point)ntire Chamber will be made in 16 SWG SS 304 , Testing of Chamber as per DIAL Guideline | Nos. | 0.00 | 1.00 |  | 29750.0
175711 |  | Water Supply General commentsKindly note our water meter is digital which will be integrated with the BMS, so whatever cable will be installed during the shifting of water meter, will concessionaire scope.Water meter Isolation valve shall have adequate space and access for maintenance of valve water meter and taking reading of water meter and water meter power supply should be on UPS source.General Guidelines (Water Supply) .Water supply pipe laying for FOH, should be laid in niche with openable cover, for BOH it could be exposed. Supply Line installation check leakage testing to be done, before connection with DIAL tapping point.Specification for Supply pipe- 1) CPVC ASTM D-2846 SDR-11 Class-1, CPVC solvent ASTM F-493 for normal waterFor Hot water Copper pipe EN 1057 with thermal insulation. Thermal insulation shall be conforming to BS 476 Part 6 7 FM approved, Fittings BN-1254-1, Pipe installation in walls (except washroom and shower room) shall be through niches with openable SS cover.All materials items to be used at site are subjected to prior inspection and approval from DIAL Engg. Data sheet with respect to all material need to be submitted for prior approval. Test certificate with respect to all material need to be submitted prior to installation during MIR Process.Make– Astral Supreme for Pipe and Fittings.· All pipes should be installed freely from ceiling void area. Water Supply piping from floor is not allowed. Piping drops from ceiling inside BOH areas are recommended to be exposed on walls partitions. In FOH areas, piping drops from ceiling can be installed through niche in walls with openable S.S. covers. Needs to be mentioned in drawing.· Existing Water Meter should be easily accessible.· Hydro-testing of pipe to be done at a pressure of 15Kgf cm² for 24 hrs and get it inspected from DIAL- EnggWater meter Isolation valve shall have adequate space and access for maintenance of valve water meter and taking reading of water meter. Kindly share section drawing of same and water meter power supply should be on UPS source. Data Sheet, material inspection Catalogue needs to be submitted for prior approval from DIAL-Engg.Kindly note our water meter is digital which will be integrated with the BMS, so whatever cable will be installed during the shifting of water meter, will concessionaire scope.General Guidelines (Drainage) . To be followed during execution workGrease trap Make shall be as per TDM and selection and backup calculation shall be as per TDM and have adequate space for opening of top cover for maintenance. Kindly share the details.Cleanout provisioning for maintenance and cleaning purpose to be provided.Water proofing for wet Dry to be done as per TDM Airport guideline.Pipe laying to be done within trench, and trench flooring should have openable cover.Power to be provided for existing Digital Water meter. Drain Line testing to be done, before connection with DIAL tapping point.Required JB Openable trench cover Grating Floor trap IC to be provided.Specification for Drain Pipe- uPVC IS 4985 Class 5 IS 7834 Class 5 for fittings, uPVC solvent- ASTM D-2564, Makes – Astral Supreme for Pipe and Fittings.Pipe installation in raised flooring should be through trench with openable cover.Each and every drain should go through Grease Traps. Only Condensate drain of HVAC Units are allowed to be conned without Grease Trap. Calculations w.r.t drain flow rate with grease capacity need to be submitted w.r.t selection of Grease Traps Capacities. Only S.S. Grease Traps are allowed. Data Sheet Catalogue needs to be submitted for prior approval from DIAL-Engg. Size of IC should not be less than 600MMx600MM. S.S. grating with dia 5mm holes should be permanently welded inside IC at discharge end.Y- Connections to be provided instead of Tee in uPVC waste pipe.Note- Before execution, all Material inspection to be done along with TDS required test certificates.Installation check to be done, before closing of ceiling FlooringPost completion of onsite work, As Built Drawing to be submitted.DIAL Shared Guideline to be followed |  | 0.00 | 0.00 |  | 0