## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
179989 | A | CONNECTING INTEGRATING UNIT M E SERVICES TO AIRPORT M E SERVICES BUILDING |  | 0.00 | 0.00 |  | 0
179990 | A.1 | If any termination connection of the unit services are required outside the site location (i.e. connection of the unit M E to the airport M E or service termination to the airport external façade roof etc.); then the contractor has to work in consultation with the airport to plan, design detail for such connections. The contractor to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor to make good after installation any penetrations including providing fire seals as requried as per airport requirement. |  | 0.00 | 0.00 |  | 0
179991 | B | METER METER PANEL |  | 0.00 | 0.00 |  | 0
179992 | B.1 | Supply, Installation, Testing Commissioning of kWH MFM Energy Meter Panel complete with Enclosure (If required as per site condition Airport TDM). The RYB sequence should be provided. Energy Meter shall be of Digital kVAH Type of approved make or any other make with kVAH option with Approval from TS Department. |  | 0.00 | 0.00 |  | 0
179993 | B.1.1 | 63 5A Energy Meter(Direct)-3 Phase | Nos | 0.00 | 1.00 |  | 18500
179994 | C | LV CABLING |  | 0.00 | 0.00 |  | 0
179995 | C.1 | Supply and Laying of approved make Fire Rated LSZH XLPE insulated PVC sheathed, Copper conductor, Steel Tape Wire Armoured, 1100V grade cable, Number of Cable Core as per SLD Load Calculation Sheet (Main Cable) Unarmoured Single Core Wire (ECC). The cable shall be laid Underground on Cable Tray through Cable Trunking in Pipe on Wall Trench using necessary supporting clamping arrangements.The cable shall be provided with cable identification tags made out of Aluminium strip, engraved with cable size and the routing. |  | 0.00 | 0.00 |  | 0
179996 | C.1.1 | 4C x 25 Sq. mm XLPE Al Armoured Cable + 2 x 8SWG Cu | Mtr | 0.00 | 15.00 |  | 655
179997 | D | CABLE END TERMINATIONS |  | 0.00 | 0.00 |  | 0
179998 | D.1 | Supply and Installation of approved make cable end Termination for the following cables using Single Compression Brass Glands, Solderless Tinned Copper Lugs, Gland earthing of adequate size, etc.complete. |  | 0.00 | 0.00 |  | 0
179999 | D.1.1 | 4C x 25 Sq. mm XLPE Al Armoured Cable | Nos | 0.00 | 4.00 |  | 550
180000 | E | DISTRIBUTION BOARDS |  | 0.00 | 0.00 |  | 0
180001 | E.1 | Supply, Installation, Testing Commissioning of approved make Surface Flush Floor mounting 10kA 25kA Distribution Boards, Devices, Relays and all accessories. The RYB sequence should be provided at the incomer entry, followed by on off and trip indicators. The DB shall be made out of 1.2 mm CRCA sheet steel enclosure and powder coated complete with cable gland plate knock out at the top and bottom. The DB shall have hinged lockable door. The busbar shall be tinned copper, for phases mounted on suitable type Insulator, Independent neutral busbar including inter connecting wiring earth bus on insulation mount, complete with Protective devices (MCCB, MCB, RCCB, RCBO, etc.) The Contractor shall be responsible to supply materials and equipment complying with the green building specification if required. All DB s must named as per the SLD Load Calculation Sheet. Laminated SLD Load Calculation Sheet shall be placed near to DB Locations. The RCCB RCBO shall be Hpi Si series MCB s shall be B C Curve (As per Airport requirement). |  | 0.00 | 0.00 |  | 0
180002 | E.1.1 | LPDB 6 Way TPN DBIncomer 63A 4P 30mA RCCB - 1 No.Outgoings10 16 20 25A SP MCB- 18 Nos | Each | 0.00 | 1.00 |  | 35200
180003 | F | LIGHT POINT WIRING |  | 0.00 | 0.00 |  | 0
180004 | F.1 | Supply, Installation, Testing Commissioning of Point wiring (Light Fixtures to be as approved by Architect Design BOQ) with approved makes Switches Lighting Control Switch Board with FRLSH PVC insulated Flexible Copper Wires 660 1100V grade through suitable size GI Conduit Heavy Duty PVC Conduit GI Trunking (Containment size Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. carrying out Surface Concealed wiring as per site condition maintain aesthetic of the unit.Wiring shall be as per IS 732. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports brackets for conduit and Trunking suspension. |  | 0.00 | 0.00 |  | 0
180005 | F.1.1 | 1 No. light point controlled by 1 No 10A, SP Switch. | Nos | 0.00 | 7.00 |  | 4050
180006 | F.1.2 | Secondary light points. (from the first light point without supply and installation of switches.) | Nos | 0.00 | 63.00 |  | 2240
180007 | G | CIRCUIT WIRING |  | 0.00 | 0.00 |  | 0
180008 | G.1 | Supply, Installation, Testing Commissioning of approved makes FRLSH PVC insulated Flexible Copper Wires 660 1100V grade through suitable size GI Conduit Heavy Duty PVC Conduit GI Trunking (Containment size Type selection as per site requirement) for the following types of wires. For dummy sockets, wiring considered. |  | 0.00 | 0.00 |  | 0
180009 | G.1.1 | Circuit wiring for light points using 2 Runs of 2.5 sq.mm PVC insulated copper wires along with 1 Run of 1.5 sqmm pvc copper wire (Green) for continuous earthing, through suitable GI Conduit Heavy Duty PVC Conduit GI Trunking from DB to Light control switch box Normal Sockets. | Mtr | 0.00 | 200.00 |  | 282
180010 | G.1.2 | Power points using 2x2 Runs of 4 sq.mm PVC insulated copper wires along with 2 Run of 2.5 sqmm pvc copper wire (Green) for continuous earthing, through suitable GI Conduit Heavy Duty PVC Conduit GI Trunking from DB to Power points(Ring circuit). | Mtr | 0.00 | 100.00 |  | 385
180011 | H | POWER POINTS (SWITCHES SOCKETS) |  | 0.00 | 0.00 |  | 0
180012 | H.1 | Supply, Installation, Testing Commissioning of approved makes Devices (Switches Sockets - Face Plate Finish as approved by Architect Matching to Architecture interior Finishes) complete with suitable GI Back boxes, Earthing, accessories, glands, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. on Surface Concealed as per site condition maintain aesthetic of the unit.Type annd IP rating should be as per Airport requirements. The rate shall include wall chasing, chipping of floors, rough plastering. The unit shall be suitable for 400 ± 15 volts 3 phase and 230 ± 10 volts 1 phase, 50 60 Hz, AC supply as per Airport Country power supply. |  | 0.00 | 0.00 |  | 0
180013 | H.1.1 | 13A Single Switched Socket Outlet | Nos | 0.00 | 1.00 |  | 850
180014 | H.1.2 | 13A Dual Switched Socket Outlet | Nos | 0.00 | 4.00 |  | 1450
180015 | H.1.3 | 13A Single Switched Socket with dual USB Outlet | Nos | 0.00 | 8.00 |  | 2430
180016 | H.1.4 | 16A Single Switched Socket Outlet | Nos | 0.00 | 1.00 |  | 950
180017 | H.1.5 | One Gang Blank Plate | Nos | 0.00 | 1.00 |  | 250
180018 | J | CONTAINMENT |  | 0.00 | 0.00 |  | 0
180019 | J.1 | Supply Installation of approved makes GI Conduit Heavy Duty PVC Conduit, through Wall Ceiling Floor as per drawings, complete with ISI standard accessories factory made fittings. |  | 0.00 | 0.00 |  | 0
180020 | J.1.1 | 25mm GI PVC Conduit | Mtr | 0.00 | 50.00 |  | 220
180021 | J.1.2 | Cable Pull Box (Floor box with rempvable cover) | Nos | 0.00 | 14.00 |  | 850
180022 | J.1.3 | 75 X 50 MM PERFORATED CABLE TRAY | Mtr | 0.00 | 40.00 |  | 730
180023 | M | DATA NETWORK SYSTEM |  | 0.00 | 0.00 |  | 0
180024 | M.1 | Supply, Installation, Testing Commissioning of approved makes Data Telephone Network System with required cabling through suitable size GI Conduit Heavy Duty PVC Conduit GI Trunking (Containment size Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with IDF SERVER Rack using patch cordes, etc. carrying out Surface Concealed wiring as per site condition maintain aesthetic of the unit. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports brackets for conduit and Trunking suspension. |  | 0.00 | 0.00 |  | 0
180025 | M.1.1 | Dual Data outlet (RJ45) Jack | Nos | 0.00 | 4.00 |  | 1430
180026 | M.1.4 | SITC of CAT6 cable on surface concealed wall, including suitable conduits, fittings, accessories, etc.(For dummy points cabling considered) | Mtr. | 0.00 | 80.00 |  | 240
180027 | N | ELECTRICAL SERVICE IDENTIFICATION LABELS, SIGNS TAGS |  | 0.00 | 0.00 |  | 0
180028 | N.1 | All services like Panels, Cables, Pipes etc need to be clearly labelled or tagged at site with service identification, direction etc. And all equipment needs to tagged as per Airport requirements. |  | 0.00 | 0.00 |  | 0
180029 | N.1.1 | Labelling Tagging for Services and Equipment s | Lot | 0.00 | 1.00 |  | 5000
180030 | O | MISCELLANEOUS |  | 0.00 | 0.00 |  | 0
180031 | O.1 | The contractor needs to mention any additional items or missing items that are not mentioned in the above BOQ after a detailed site survey or inspection and to be validated by consultants. |  | 0.00 | 0.00 |  | 0
180032 | O.1.1 | Providing and Fixing of Electrical Standard Grade Rubber Mat suitable for LT Volts | Unit | 0.00 | 1.00 |  | 3000
180033 | O.1.2 | Provide and Fixing Shock Treatment Chart | Unit | 0.00 | 1.00 |  | 1500
180034 | O.1.3 | Provide and Fixing of L.T. danger sign boards in Panel side | Unit | 0.00 | 1.00 |  | 550