## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
136239 |  | Main MDB as described above | Set | 0.00 | 1.00 |  | 0
136240 | 1.1 | DISTRIBUTION BOARDS |  | 0.00 | 0.00 |  | 0
136241 |  | Supply, erection, testing and commissioning of the following sheet steel clad wall recess mounting dust and vermin proof double door type distribution boards constructed from 16 SWG sheet steel IP 42 construction, finished with rust proof duly powder coated in approved shade with hinged gasketed door and housing the following complete with P.V.C. insulated copper busbars rated 200 amp with interconnections, neutral and earth bar assembly per phase, earthing terminals complete as approved by Architects. |  | 0.00 | 0.00 |  | 0
136242 |  | Note All MCBs in distribuition board for power circuits shall be of C curve |  | 0.00 | 0.00 |  | 0
136243 | i | Type A |  | 0.00 | 0.00 |  | 0
136244 |  | 1-63 amp FP MCB with 3 single phase banks each comprising of 63A DP RCCB(30 mA) and 6 nos. 6 16 20 25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. | Set | 0.00 | 2.00 |  | 0
136245 | ii | Type B |  | 0.00 | 0.00 |  | 0
136246 |  | 1-32 amp DP MCB + DP RCCB ( 30mA) and 12 nos. 6 16 20 25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. | Set | 0.00 | 1.00 |  | 0
136247 | ii | Type C |  | 0.00 | 0.00 |  | 0
136248 |  | 1-32 amp DP MCB + DP RCCB ( 30mA) and 8 nos. 6 16 20 25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. | Set | 0.00 | 2.00 |  | 0
136249 | iv | Type D |  | 0.00 | 0.00 |  | 0
136250 |  | 1-25 amp DP MCB + DP RCCB ( 30mA) and 6 nos. 6 16 20 25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. | Set | 0.00 | 0.00 | RO | 0
136251 | 2 | Supply installation testing and commisioning 3.0 kVA online ( 1ph input and 1ph output) UPS with 15 Min power back up complete with in buit Static by pass switch , Mannual external maintenance by pass switch , Rectifiers , Sealed MF batteries etc as required | No. | 0.00 | 2.00 |  | 0
136252 | 3 | Supply, laying, testing commissioning of following sizes of Al Cu. conductor 1.1 kV grade, armoured, XLPE insulated FRLS LT Cables Control Cables including necessary cleats, clamps etc. (Cables shall be partly laid in Pipes, O H cable tray, on wall as required ) |  | 0.00 | 0.00 |  | 0
136253 | 3.1 | 3.5C – 120.0 (Al.) FRLS Armoured XLPE Cable | Mtrs | 0.00 | 20.00 |  | 0
136254 | 3.2 | 4C – 4.0 (Cu.) FRLS Armoured XLPE Cable | Mtrs | 0.00 | 135.00 |  | 0
136255 | 3.3 | 3C – 4.0 (Cu.) FRLS Armoured XLPE Cable | Mtrs | 0.00 | 50.00 |  | 0
136256 | 4 | Supply, erection, testing commissioning of following sizes of cable end terminations with Double compression gland for 1.1 kV grade, XLPE insulated, Al Cu Conductor cable |  | 0.00 | 0.00 |  | 0
136257 | 4.1 | 3.5C – 120.0 (Al.) FRLS Armoured XLPE Cable | Nos. | 0.00 | 2.00 |  | 0
136258 | 4.2 | 4C – 4.0 (Cu.) FRLS Armoured XLPE Cable | Nos. | 0.00 | 4.00 |  | 0
136259 | 4.3 | 3C – 4.0 (Cu.) FRLS Armoured XLPE Cable | Nos. | 0.00 | 4.00 |  | 0
136260 | 5 | Wiring for DB Submains with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in surface concealed MS surface concealed conduit including cost of providing saddles etc as required for surface conduiting and or cost of cutting and filling chases as required and making suitable end termination with copper lugs complete as required and as below |  | 0.00 | 0.00 |  | 0
136261 | 5.1 | 4 x 16 sq.mm + 2 No. 6.0 Sq. mm in 40 mm dia MS Conduit | Mtrs | 0.00 | 95.00 |  | 0
136262 | 5.2 | 4 x 6 sq.mm + 2 No. 4.0 Sq. mm in 32 mm dia MS Conduit | Mtrs | 0.00 | 20.00 |  | 0
136263 | 5.3 | 2 x 6 sq.mm + 1 No. 4 Sq. mm in 25 mm dia MS Conduit | Mtrs | 0.00 | 85.00 |  | 0
136264 | 5.4 | 2 x 4 sq.mm + 1 No. 2.5 Sq. mm in 25 mm dia MS Conduit | Mtrs | 0.00 | 270.00 |  | 0
136265 | 6 | Supplying and laying of the following earthing clamped to wall with suitable clamps saddles and fixing bolts in ground including the cost of digging and back filling as required and complete as required to comply with IS 3043 1987. All copper joints shall be tinned. The rates shall be inclusive of making test joints where ever required |  | 0.00 | 0.00 |  | 0
136266 | 6.1 | 50X6 mm GI Strip | Mtrs | 0.00 | 10.00 |  | 0
136267 | 6.2 | 25X6 mm GI Strip | Mtrs | 0.00 | 20.00 |  | 0
136268 | 6.3 | 25X3 mm GI Strip | Mtrs | 0.00 | 140.00 |  | 0
136269 | 6.4 | 8 SWG Copper Wire | Mtrs | 0.00 | 70.00 |  | 0
136270 | 6.5 | 8 SWG GI Wire | Mtrs | 0.00 | 100.00 |  | 0
136271 | 6.6 | 1 Core 6.0 Sq. Mm FRLS Green Wire | Mtrs | 0.00 | 60.00 |  | 0
136272 | 7 | Supply, erection, testing commissioning of prefabricated GI Perforated type cable trays including Tees Bends Crossing Reducers Couping to be laid in cable trench, overhead on wall or hanged from ceiling complete with all accessories as required including support at every 1500mm as required |  | 0.00 | 0.00 |  | 0
136273 | 7.1 | 150 mm x 40 x 40 x 2 mm thick | Mtrs | 0.00 | 75.00 |  | 0
136274 | 7.2 | 300 mm x 40 x 40 x 2 mm thick | Mtrs | 0.00 | 35.00 |  | 0
136275 | 8 | Wiring for MCB controlled normal primary light points Wall Point Floor Point with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm dia 16 SWG MS conduit in wall ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq. mm PVC insulated copper conductor wire for loop earthing etc. complete as required. (Cost of MCB included in the item for per DB). | Pt | 0.00 | 9.00 |  | 0
136276 | 9 | Wiring for secondary MCB controlled normal light points Wall Point Floor Point( Looped from above point) with 2.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm 16 SWG MS conduit in wall ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq mm PVC insulated copper conductor wire for loop earthing etc. complete as required. | Pt | 0.00 | 14.00 |  | 0
136277 | 10 | Wiring for MCB controlled Emergency primary light points Wall Point Floor Point with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm dia 16 SWG MS conduit in wall ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq. mm PVC insulated copper conductor wire for loop earthing etc. complete as required. (Cost of MCB included in the item for per DB). | Pt | 0.00 | 1.00 |  | 0
136278 | 11 | Wiring for secondary MCB controlled Emergency light points Wall Point Floor Point( Looped from above point) with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm 16 SWG MS conduit in wall ceiling including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq mm PVC insulated copper conductor wire for loop earthing etc. complete as required. | Pt | 0.00 | 5.00 |  | 0
136279 | 12 | Wiring for switch controlled primary light points with 2.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade wires (FRLS) in 25 mm dia 16 SWG MS concealed surface conduit including cost of cutting and filling chases for recessed conduiting and supports in case of Surface conduit including all bends , saddles , Junction boxes etc. including the cost of running 1.5 sq. mm PVC insulated copper conductor wire for loop earthing etc. and including providing circuit wiring with 2.5 sq mm PVC insulated stranded copper conductor 1100 volt grade FRLS wires and including the cost of providing and fixing a 6 amp 240 Volt grid plate mounted switch with moulded cover plate in GI box and complete as required ( Switch shall be as approved by the architect Client) | Pt | 0.00 | 3.00 |  | 0
136280 | 13 | Wiring for secondary Switch controlled light points ( Looped from above point) with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm dia 16 SWG MS concealed surface conduit including cost of cutting and filling chases for recessed conduiting and supports in case of Surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq mm PVC insulated copper conductor wire for loop earthing etc. complete as required. | Pt | 0.00 | 1.00 |  | 0
136281 | 14 | Wiring for a 5 pin 240 volt 6 amp single phase and neutral switch socket outlet with 2.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall ceiling including cost of providing circuit wiring with 2.5 sq mm PVC insulated stranded copper conductor 1100 volt grade wires and including cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and providing and fixing of a combined 5 pin 240 volt 6 amp socket outlet with safety shutters and 6 amp 240 volt single pole grid plate mounted switch with moulded cover plate in recessed GI box and including earthing of the 3rd pin with 1.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wires complete as requied( Switch and socket shall be as approved by the architect Client) | Pt | 0.00 | 9.00 |  | 0
136282 | 15 | Wiring same as in Item 14 above looped from an adjacent 6 amp switch socket outlet as required and providing and fixing of a modular type 5 pin 240 Volt 6 amp shuttered socket outlet and a modular type 6 amp 240 Volt single pole switch in a recessed GI boxes with internal wiring and moulded front plates complete as required. ( Switch and socket shall be as approved by the architect Client) | Pt | 0.00 | 16.00 |  | 0
136283 | 15 | Same as above but switch and socket provided at separate location including wiring berween switch and socket and complete as required | Pt | 0.00 | 0.00 | RO | 0
136284 | 17 | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (1 outlet wired on 1 circuit) with 2.5 sq. mm PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall Ceiling including the cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including providing and fixing 6 pin 240 volt 16 amp socket outlet with safety shutters and 16 amp 240 volt single pole grid plate mounted modular type switch with moulded cover plate in recessed GI box and including earthing of the 3rd pin with 1.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wires and complete as requied( Switch and socket shall be as approved by the architect Client) | Pt | 0.00 | 7.00 |  | 0
136285 | 18 | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (1 outlet wired on 1 circuit) with 4.0 sq. mm PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall Ceiling including the cost of cutting and filling chases for recessed conduiting and supports in case of surface conduit including all bends , saddles , Junction boxes etc and including providing and fixing 6 pin 240 volt 16 amp socket outlet with safety shutters and 16 amp 240 volt single pole grid plate mounted modular type switch with moulded cover plate in recessed GI box and including earthing of the 3rd pin with 2.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wires and complete as requied( Switch and socket shall be as approved by the architect Client) | Pt | 0.00 | 5.00 |  | 0
136286 | 19 | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (2 outlets wired on 1 circuit) with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS), 4.0 sq mm upto the first outlet and 2.5 sq mm from first to the second outlet in 25mm dia 16 SWG MS conduit in wall Ceiling including cost of providing saddles etc as required for surface conduiting and or cost of cutting and filling chases and including providing and fixing of two sets of 6 pin 240 volt 16 amp socket outlet with safety shutters and 16 amp 240 volt single pole grid plate mounted switches with moulded cover plate in a recessed GI box including earthing of the 3rd pin with 2.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wire complete as required. (Switch Socket Shall be as per approved sample by Architect) | Pt | 0.00 | 3.00 |  | 0
136287 | 20.1 | Wiring for primary switch board consisting of 3 Nos. 5 pin 240 volt 6 amp single phase and neutral switch socket outlets with 1 Nos.16A switch with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS), 2.5 sq FRLS copper wire mm in 25mm dia 16 SWG MS conduit in wall Ceiling including cost of providing saddles etc as required for surface conduiting and or cost of cutting and filling chases and including providing and fixing prewired switch board each consisting of 3 Nos. 5 pin 240 volt 6 amp single phase and neutral switch socket outlets with 1 Nos. 16A modular switch , safety shutters in a recessed surface GI box including earthing of the 3rd pin with 1.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wire complete as required. (Switch Socket Shall be as per approved sample by Architect) | Pt | 0.00 | 4.00 |  | 0
136288 | 20.2 | Wiring for secondary switch board ( Looped from Above) consisting of 3 Nos. 5 pin 240 volt 6 amp single phase and neutral switch socket outlets with 1 Nos. 16A switch with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS), 2.5 sq FRLS copper wire mm in 25mm dia 16 SWG MS conduit in wall Ceiling including cost of providing saddles etc as required for surface conduiting and or cost of cutting and filling chases and including providing and fixing prewired switch board each consisting of 3 Nos. 5 pin 240 volt 6 amp single phase and neutral switch socket outlets with 1 Nos. 16A modular switch , safety shutters in a recessed surface GI box including earthing of the 3rd pin with 1.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wire complete as required. (Switch Socket Shall be as per approved sample by Architect) | Pt | 0.00 | 1.00 |  | 0
136289 | 21 | Supply installation testing and fixing 3 pin 16A 20A , 240V , single Phase metal Clad industrial socket outlet with 16A 20A DP MCB and complete in all respects( Wiring Excluded from scope of this item) | Nos. | 0.00 | 17.00 |  | 0
136290 | 22 | Supply installation testing and fixing 3 pin 25A 32A , 240V , single Phase metal Clad industrial socket outlet with 25A 32A DP MCB and complete in all respects( Wiring Excluded from scope of this item) | Nos. | 0.00 | 7.00 |  | 0
136291 | 23 | Supply installation testing and fixing 3 pin 40A , 240V , single Phase metal Clad industrial socket outlet with 40A DP MCB and complete in all respects( Wiring Excluded from scope of this item) | Nos. | 0.00 | 0.00 | RO | 0
136292 | 24 | Supply installation testing and fixing 5 pin 32A , 415V , single Phase metal Clad industrial socket outlet with 32A FP MCB and complete in all respects( Wiring Excluded from scope of this item) | Nos. | 0.00 | 1.00 |  | 0
136293 | 25 | Supply installation testing and fixing 5 pin 63A , 415V , single Phase metal Clad industrial socket outlet with 63A FP MCB and complete in all respects( Wiring Excluded from scope of this item) | Nos. | 0.00 | 3.00 |  | 0
136294 | 26.1 | Supply and Installation of following in wall mounted MS enclosure |  | 0.00 | 0.00 |  | 0
136295 | i | 32A 25A DP RCBO | Nos | 0.00 | 5.00 |  | 0
136296 | 26.2 | Supply and Installation of following in IP 67 Rated Poly carbonate Enclosure |  | 0.00 | 0.00 |  | 0
136297 | i | 25A FP MCB + RCCB (300 mA) | Nos | 0.00 | 2.00 |  | 0
136298 | 27 | Supply and installation of flush mounted (Enhanced Category 6T 568 A or B) outlets with 2 mm thick GI box complete including cutting, chases, fixing of GI boxes and making good. The plastic shall be high impact, flame-retardant, UL rate thermoplastic. Dust cover blank shall be provided to protect unused faceplate openings. Termination caps and plastic cover shall be provided to protect jack wiring. |  | 0.00 | 0.00 |  | 0
136299 | i | Single outlet face plate with RJ-45 Jack with information outlet | Nos. | 0.00 | 14.00 |  | 0
136300 | ii | Duplex outlet face plate with RJ-45 Jack with information outlet | Nos. | 0.00 | 4.00 |  | 0
136301 | 28 | Supply, installation, testing, commissioning and laying of Category 6A cable in existing conduits raceways including Numbering-ferruling, bunching, tagging, computerised labeling of utp cable , Input Output termination Punching at both the ends , (both side i.e. user rack) Cable Dressing etc as required . | Mtrs | 0.00 | 225.00 |  | 0
136302 | 29 | Supplying,installation and commisioning of CAT-6A patch cords 2 mtrs. | Nos | 0.00 | 22.00 |  | 0
136303 | 30 | Supplying,installation and commisioning of CAT-6A patch cords 1 mtr. | Nos | 0.00 | 22.00 |  | 0
136304 | 31 | Supply , fixing Laying 16 SWG MS conduits on surface or concealed complete with PVC junction boxes, cover plates, bends, saddles, base and other accessories all made in PVC with GI screws as required to complete the job. . |  | 0.00 | 0.00 |  | 0
136305 | i | 25 mm dia 16 SWG MS conduit | Mtrs | 0.00 | 60.00 |  | 0
136306 | ii | 20 mm dia 16 SWG MS conduit | Mtrs | 0.00 | 105.00 |  | 0
136307 | 32 | Installation of following light fixtures including connections and complete in all respects |  | 0.00 | 0.00 |  | 0
136308 | i | 25 15 12Watt Recessed Down Lighter | No. | 0.00 | 65.00 |  | 0
136309 | ii | Signage | No. | 0.00 | 5.00 |  | 0
136310 | iv | 2 X 26W LED FTL | No. | 0.00 | 3.00 |  | 0
136311 | v | LED Strip Light | Mtrs | 0.00 | 6.00 |  | 0