## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
143061 | 1 | MAIN Panel |  | 0.00 | 0.00 |  | 0
143062 | A | Incoming |  | 0.00 | 0.00 |  | 0
143063 |  | 1 No. 250 amps 16 kA 440 volt TPN MCCB with Thermal Magnetic overcurrent and short circuit and with following |  | 0.00 | 0.00 |  | 0
143064 | B | Metering, Indication Protection |  | 0.00 | 0.00 |  | 0
143065 | a | 1 Nos. 6 Parameter Multi Function Mater with 3 Nos. Cast Resin CTs and MCBs |  | 0.00 | 0.00 |  | 0
143066 | b | Breaker ON OFF indication Lamps |  | 0.00 | 0.00 |  | 0
143067 | c | R-Y-B indication lamps with MCBs |  | 0.00 | 0.00 |  | 0
143068 | d | ELR with CBCT |  | 0.00 | 0.00 |  | 0
143069 | C | Bus Bar |  | 0.00 | 0.00 |  | 0
143070 |  | 300 A, TPN Al. Bus Bar of suitable length having Current density 1Amp sq.mm having high conductivity electrical grade suitable to withstand symmetrical fault level of 25 kA. Neutral busbar shall be of 100% capacity. |  | 0.00 | 0.00 |  | 0
143071 | D | Outgoings |  | 0.00 | 0.00 |  | 0
143072 | a | 7 No. 63 amps 4P MCB ( Type C) |  | 0.00 | 0.00 |  | 0
143073 | b | 5 No. 20 25 32 amps 4P MCB ( Type C) |  | 0.00 | 0.00 |  | 0
143074 | c | 8 No. 32 25 amps 2P MCB ( Type C) |  | 0.00 | 0.00 |  | 0
143075 |  | Main MDB as described above |  | 0.00 | 1.00 |  | 350000
143076 | 1.1 | DISTRIBUTION BOARDS |  | 0.00 | 0.00 |  | 0
143077 |  | Supply, erection, testing and commissioning of the following sheet steel clad wall recess mounting dust and vermin proof double door type distribution boards constructed from 16 SWG sheet steel IP 42 construction, finished with rust proof duly powder coa |  | 0.00 | 0.00 |  | 0
143078 |  | Note All MCBs in distribuition board for power circuits shall be of C curve |  | 0.00 | 0.00 |  | 0
143079 | i | Type A |  | 0.00 | 0.00 |  | 0
143080 |  | 1-63 amp FP MCB with 3 single phase banks each comprising of 63A DP RCCB(30 mA) and 6 nos. 6 16 20 25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. |  | 0.00 | 2.00 |  | 35000
143081 | ii | Type B |  | 0.00 | 0.00 |  | 0
143082 |  | 1-32 amp DP MCB + DP RCCB ( 30mA) and 12 nos. 6 16 20 25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. |  | 0.00 | 1.00 |  | 25000
143083 | ii | Type C |  | 0.00 | 0.00 |  | 0
143084 |  | 1-32 amp DP MCB + DP RCCB ( 30mA) and 8 nos. 6 16 20 25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. |  | 0.00 | 2.00 |  | 25000
143085 | iv | Type D |  | 0.00 | 0.00 |  | 0
143086 |  | 1-25 amp DP MCB + DP RCCB ( 30mA) and 6 nos. 6 16 20 25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. |  | 0.00 | 0.00 | RO | 0
143087 | 2 | Supply installation testing and commisioning 3.0 kVA online ( 1ph input and 1ph output) UPS with 15 Min power back up complete with in buit Static by pass switch , Mannual external maintenance by pass switch , Rectifiers , Sealed MF batteries etc as requ |  | 0.00 | 2.00 |  | 65000
143088 | 3 | Supply, laying, testing commissioning of following sizes of Al Cu. conductor 1.1 kV grade, armoured, XLPE insulated FRLS LT Cables Control Cables including necessary cleats, clamps etc. (Cables shall be partly laid in Pipes, O H cable tray, on wall as |  | 0.00 | 0.00 |  | 0
143089 | 3.1 | 3.5C – 120.0 (Al.) FRLS Armoured XLPE Cable |  | 0.00 | 20.00 |  | 1800
143090 | 3.2 | 4C – 4.0 (Cu.) FRLS Armoured XLPE Cable |  | 0.00 | 130.00 |  | 650
143091 | 3.3 | 3C – 4.0 (Cu.) FRLS Armoured XLPE Cable |  | 0.00 | 50.00 |  | 600
143092 | 4 | Supply, erection, testing commissioning of following sizes of cable end terminations with Double compression gland for 1.1 kV grade, XLPE insulated, Al Cu Conductor cable |  | 0.00 | 0.00 |  | 0
143093 | 4.1 | 3.5C – 120.0 (Al.) FRLS Armoured XLPE Cable |  | 0.00 | 2.00 |  | 1500
143094 | 4.2 | 4C – 4.0 (Cu.) FRLS Armoured XLPE Cable |  | 0.00 | 4.00 |  | 950
143095 | 4.3 | 3C – 4.0 (Cu.) FRLS Armoured XLPE Cable |  | 0.00 | 4.00 |  | 950
143096 | 5 | Wiring for DB Submains with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in surface concealed MS surface concealed conduit including cost of providing saddles etc as required for surface conduiting and or cost of cutting and fillin |  | 0.00 | 0.00 |  | 0
143097 | 5.1 | 4 x 16 sq.mm + 2 No. 6.0 Sq. mm in 40 mm dia MS Conduit |  | 0.00 | 95.00 |  | 1200
143098 | 5.2 | 4 x 6 sq.mm + 2 No. 4.0 Sq. mm in 32 mm dia MS Conduit |  | 0.00 | 22.00 |  | 650
143099 | 5.3 | 2 x 6 sq.mm + 1 No. 4 Sq. mm in 25 mm dia MS Conduit |  | 0.00 | 90.00 |  | 550
143100 | 5.4 | 2 x 4 sq.mm + 1 No. 2.5 Sq. mm in 25 mm dia MS Conduit |  | 0.00 | 290.00 |  | 450
143101 | 6 | Supplying and laying of the following earthing clamped to wall with suitable clamps saddles and fixing bolts in ground including the cost of digging and back filling as required and complete as required to comply with IS 3043 1987. All copper joints shal |  | 0.00 | 0.00 |  | 0
143102 | 6.1 | 50X6 mm GI Strip |  | 0.00 | 10.00 |  | 180
143103 | 6.2 | 25X6 mm GI Strip |  | 0.00 | 20.00 |  | 150
143104 | 6.3 | 25X3 mm GI Strip |  | 0.00 | 140.00 |  | 110
143105 | 6.4 | 8 SWG Copper Wire |  | 0.00 | 70.00 |  | 150
143106 | 6.5 | 8 SWG GI Wire |  | 0.00 | 100.00 |  | 90
143107 | 6.6 | 1 Core 6.0 Sq. Mm FRLS Green Wire |  | 0.00 | 60.00 |  | 250
143108 | 7 | Supply, erection, testing commissioning of prefabricated GI Perforated type cable trays including Tees Bends Crossing Reducers Couping to be laid in cable trench, overhead on wall or hanged from ceiling complete with all accessories as require |  | 0.00 | 0.00 |  | 0
143109 | 7.1 | 150 mm x 40 x 40 x 2 mm thick |  | 0.00 | 85.00 |  | 750
143110 | 7.2 | 300 mm x 40 x 40 x 2 mm thick |  | 0.00 | 35.00 |  | 1200
143111 | 8 | Wiring for MCB controlled normal primary light points Wall Point Floor Point with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm dia 16 SWG MS conduit in wall ceiling including cost of cutting and filling chases |  | 0.00 | 9.00 |  | 3000
143112 | 9 | Wiring for secondary MCB controlled normal light points Wall Point Floor Point( Looped from above point) with 2.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm 16 SWG MS conduit in wall ceiling including cost of c |  | 0.00 | 14.00 |  | 3000
143113 | 10 | Wiring for MCB controlled Emergency primary light points Wall Point Floor Point with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm dia 16 SWG MS conduit in wall ceiling including cost of cutting and filling cha |  | 0.00 | 1.00 |  | 3450
143114 | 11 | Wiring for secondary MCB controlled Emergency light points Wall Point Floor Point( Looped from above point) with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm 16 SWG MS conduit in wall ceiling including cost o |  | 0.00 | 5.00 |  | 3000
143115 | 12 | Wiring for switch controlled primary light points with 2.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade wires (FRLS) in 25 mm dia 16 SWG MS concealed surface conduit including cost of cutting and filling chases for recessed conduiting a |  | 0.00 | 3.00 |  | 3000
143116 | 13 | Wiring for secondary Switch controlled light points ( Looped from above point) with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm dia 16 SWG MS concealed surface conduit including cost of cutting and filling chase |  | 0.00 | 1.00 |  | 3000
143117 | 14 | Wiring for a 5 pin 240 volt 6 amp single phase and neutral switch socket outlet with 2.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall ceiling including cost of providing circuit wirin |  | 0.00 | 9.00 |  | 3000
143118 | 15 | Wiring same as in Item 14 above looped from an adjacent 6 amp switch socket outlet as required and providing and fixing of a modular type 5 pin 240 Volt 6 amp shuttered socket outlet and a modular type 6 amp 240 Volt single pole switch in a recessed GI bo |  | 0.00 | 16.00 |  | 3000
143119 | 15 | Same as above but switch and socket provided at separate location including wiring berween switch and socket and complete as required |  | 0.00 | 0.00 | RO | 0
143120 | 17 | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (1 outlet wired on 1 circuit) with 2.5 sq. mm PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall Ceiling including t |  | 0.00 | 7.00 |  | 3500
143121 | 18 | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (1 outlet wired on 1 circuit) with 4.0 sq. mm PVC insulated stranded copper conductor 1100 volt grade wires (FRLS) in 25mm dia 16 SWG MS conduit in wall Ceiling including t |  | 0.00 | 5.00 |  | 3500
143122 | 19 | Wiring for 6 pin 240 volt 16 amp single phase and neutral switch socket outlets (2 outlets wired on 1 circuit) with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS), 4.0 sq mm upto the first outlet and 2.5 sq mm from first to the secon |  | 0.00 | 3.00 |  | 3500
143123 | 20.1 | Wiring for primary switch board consisting of 3 Nos. 5 pin 240 volt 6 amp single phase and neutral switch socket outlets with 1 Nos.16A switch with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS), 2.5 sq FRLS copper wire mm in 25mm |  | 0.00 | 4.00 |  | 3500
143124 | 20.2 | Wiring for secondary switch board ( Looped from Above) consisting of 3 Nos. 5 pin 240 volt 6 amp single phase and neutral switch socket outlets with 1 Nos. 16A switch with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS), 2.5 sq FRLS |  | 0.00 | 1.00 |  | 3500
143125 | 21 | Supply installation testing and fixing 3 pin 16A 20A , 240V , single Phase metal Clad industrial socket outlet with 16A 20A DP MCB and complete in all respects( Wiring Excluded from scope of this item) |  | 0.00 | 17.00 |  | 5000
143126 | 22 | Supply installation testing and fixing 3 pin 25A 32A , 240V , single Phase metal Clad industrial socket outlet with 25A 32A DP MCB and complete in all respects( Wiring Excluded from scope of this item) |  | 0.00 | 7.00 |  | 5000
143127 | 23 | Supply installation testing and fixing 3 pin 40A , 240V , single Phase metal Clad industrial socket outlet with 40A DP MCB and complete in all respects( Wiring Excluded from scope of this item) |  | 0.00 | 0.00 | RO | 0
143128 | 24 | Supply installation testing and fixing 5 pin 32A , 415V , Three Phase metal Clad industrial socket outlet with 32A FP MCB and complete in all respects( Wiring Excluded from scope of this item) |  | 0.00 | 1.00 |  | 6000
143129 | 25 | Supply installation testing and fixing 5 pin 63A , 415V , three Phase metal Clad industrial socket outlet with 63A FP MCB and complete in all respects( Wiring Excluded from scope of this item) |  | 0.00 | 3.00 |  | 6000
143130 | 26.1 | Supply and Installation of following in wall mounted MS enclosure |  | 0.00 | 0.00 |  | 0
143131 | i | 32A 25A DP RCBO |  | 0.00 | 5.00 |  | 4500
143132 | 26.2 | Supply and Installation of following in IP 67 Rated Poly carbonate Enclosure |  | 0.00 | 0.00 |  | 0
143133 | i | 25A FP MCB + RCCB (300 mA) |  | 0.00 | 2.00 |  | 4500
143134 | 27 | Supply and installation of flush mounted (Enhanced Category 6T 568 A or B) outlets with 2 mm thick GI box complete including cutting, chases, fixing of GI boxes and making good. The plastic shall be high impact, flame-retardant, UL rate thermoplastic. |  | 0.00 | 0.00 |  | 0
143135 | i | Single outlet face plate with RJ-45 Jack with information outlet |  | 0.00 | 14.00 |  | 850
143136 | ii | Duplex outlet face plate with RJ-45 Jack with information outlet |  | 0.00 | 4.00 |  | 850
143137 | 28 | Supply, installation, testing, commissioning and laying of Category 6A cable in existing conduits raceways including Numbering-ferruling, bunching, tagging, computerised labeling of utp cable , Input Output termination Punching at both the ends , ( |  | 0.00 | 225.00 |  | 110
143138 | 29 | Supplying,installation and commisioning of CAT-6A patch cords 2 mtrs. |  | 0.00 | 25.00 |  | 1000
143139 | 30 | Supplying,installation and commisioning of CAT-6A patch cords 1 mtr. |  | 0.00 | 25.00 |  | 1500
143140 | 31 | Supply , fixing Laying 16 SWG MS conduits on surface or concealed complete with PVC junction boxes, cover plates, bends, saddles, base and other accessories all made in PVC with GI screws as required to complete the job. . |  | 0.00 | 0.00 |  | 0
143141 | i | 25 mm dia 16 SWG MS conduit |  | 0.00 | 60.00 |  | 150
143142 | ii | 20 mm dia 16 SWG MS conduit |  | 0.00 | 100.00 |  | 140
143143 | 32 | Installation of following light fixtures including connections and complete in all respects |  | 0.00 | 0.00 |  | 0
143144 | i | 25 15 12Watt Recessed Down Lighter |  | 0.00 | 15.00 |  | 500
143145 | ii | Signage |  | 0.00 | 5.00 |  | 3500
143146 | iii | 600mmX600mm 36-48 W LED Light |  | 0.00 | 12.00 |  | 400
143147 | iv | 2 X 26W LED FTL |  | 0.00 | 3.00 |  | 500
143148 | v | LED Strip Light |  | 0.00 | 10.00 |  | 500