## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
41321 |  | DISTRIBUTION BOARDS 6 WAY V-TPN DB - LPDB Incomer 63A, FP, MCB, 10kA 1 Nos Sub Incomer 32A, DP, RCCB, 100mA 3 Nos Outgoings 6 10 16 A SP MCB C Type - 18 Nos. | Nos. | 0.00 | 1.00 |  | 65000
41322 |  | MV CABLES |  | 0.00 | 0.00 |  | 0
41323 |  | POWER CABLING Supply and laying, effecting proper connections, testing commissioning of the following sizes of 1.1 KV XLPE FRLS armoured unarmoured PVC insulated PVC sheathed aluminium copper conductor cables conforming to IS 1554 and IS 694 for Flexible copper cable Part I - 1976 with latest amendments laid over MS supports in existing RCC ducts laid in ground laid on Cable Trays including clamping the cables to supports in an approved manner as required complete with all accessories.All cables shall have thermo setting insulation XLPE and low emission of smoke and corrosive gas when affected by fire. Necessary Markers shall be provided at the intervals as per the specifications. CU Flexible Cables 4C x 6 Sq.mm. | Mtr. | 0.00 | 30.00 |  | 600
41324 |  | CABLE TERMINATION - Making cable and terminations including brass single compression glands and crimping type copper lugs for cable sizes mentioned below for aluminium or copper. |  | 0.00 | 0.00 |  | 0
41325 |  | 3.5C x 70 Sq.mm. AL | Nos. | 0.00 | 2.00 |  | 500
41326 |  | 4C x 6 Sq.mm. | Nos. | 0.00 | 2.00 |  | 420
41327 |  | POINT WIRING |  | 0.00 | 0.00 |  | 0
41328 |  | Point wiring LENGTH from DB to SB or First Light point control be MCB shall be avg. of 15Mtr. of 3C x 2.5 sq mm FRLS PVC insulated stranded copper conductor wires. For SB to SB the length shall be measured in Mtr. The secondary Loop point length shall be 10Mtr from Light fixture to light fixture. If secondary point shall be operated from MCB then the length shall be 10 Mtr. All sockets to be checked with a Check Plug socket tester for live-neutral reverse, no earth,neutral fault, live earth reverse, neutral earth reverse. The Circuit No. and DB no. label shall be provided on all UPS ,RAW sockets and switchboards with label printer. The Length shall be paid as per the actual measurements as per following manner. Wiring for the following light points with 3 x 2.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in GI conduits in F.ceiling walls ceiling as direc­ted including providing 6 amps flush type switches, 5 sided G.I Boxes for housing switc­hes and earth­ing complete as required from the above switch board. Rates shall exclusive of Switches Switch Box. (FROM SB TO LIGHT) |  | 0.00 | 0.00 |  | 0
41329 |  | First point controlled by one no. 6 amp switch. (upto 10Mtr.) | Nos. | 0.00 | 15.00 |  | 280
41330 |  | First point controlled by one no. 6 amp switch. For Emergency Light (upto 10Mtr.) | Nos. | 0.00 | 6.00 |  | 300
41331 |  | Same as item No. 4.2.1 4.2.2 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS PVC insulated copper conductor wire in concealed exposed GI conduit and earthing | Nos. | 0.00 | 12.00 |  | 800
41332 |  | Same as item No. 4.2.3 4.2.4 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS PVC insulated copper conductor wire in concealed exposed GI conduit and earthing For Emergency Light | Nos. | 0.00 | 8.00 |  | 800
41333 |  | First point controlled by existing MCB in D.B. | Nos. | 0.00 | 10.00 |  | 650
41334 |  | Same as item No.4.5.1 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS. insulated copper conductor wire in concealed exposed GI conduit and earthing | Nos. | 0.00 | 30.00 |  | 800
41335 |  | Wiring for UPS Raw plug outlets points with 3C x 4 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS 694-1990 with latest amendments, in existing Channels conduit in ceiling walls floor including all cable termination accessories) (including body earth for GI boxes) | Mtr. | 0.00 | 200.00 |  | 450
41336 |  | Wiring for UPS Raw plug outlets points with 4C x 4 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS 694-1990 with latest amendments, in existing Channels conduit in ceiling walls floor including all cable termination accessories) (including body earth for GI boxes) | Mtr. | 0.00 | 125.00 |  | 500
41337 |  | 20 mm dia GI Conduit | Mtr. | 0.00 | 100.00 |  | 120
41338 |  | MODULAR SWITCHES Supply, installation, testing commissioning of following types of modular switches, cover plates, 5 sided G.I. Boxes for housing the modular switches earthing complete as required. GI Boxes to have earth pin for body earthing. The Circuit No. and DB no. label shall be provided on all UPS ,RAW sockets and switchboards with label printer.(Make- Legrand Aretor Series) |  | 0.00 | 0.00 |  | 0
41339 |  | 6A One Way Switch | Nos. | 0.00 | 22.00 |  | 200
41340 |  | 6A 5 pin Socket - 1Nos. 6A Switch - 1Nos. | Nos. | 0.00 | 22.00 |  | 330
41341 |  | GENERAL EARTHING Supplying and erecting bare Copper conductor of following sizes 8 SWG | Mtr. | 0.00 | 30.00 |  | 180
41342 |  | LIGHT FIXTURES INSTALLATION Receiving from Store, Installation, testing commissioning of following light fixtures with complete installation hardwares including Anchor fastner, supporting Hook Rods as per final approval from Architect Client Consultant |  | 0.00 | 0.00 |  | 0
41343 |  | DOME LIGHT | Nos. | 0.00 | 13.00 |  | 3000
41344 |  | CYLINRICAL SURFACE MOUNT LIGHT | Mtr. | 0.00 | 36.00 |  | 7000
41345 |  | MISCELLANEOUS WORKS |  | 0.00 | 0.00 |  | 0
41346 |  | Supply fixing in position approved shock treatment chart written in English, Hindi and Local language. These charts shall be framed in wooden frame covered with clear glass. | Nos. | 0.00 | 1.00 |  | 600
41347 |  | Supply fixing in position the best quality danger notice boards of approved shape size as reqd. by the local Electrical Inspecting Authority written in English, Hindi local language. | Nos. | 0.00 | 1.00 |  | 600
41348 |  | CCTV System |  | 0.00 | 0.00 |  | 0
41349 |  | 2 Megapixel Fixed Lens Camera IR Dome Type 1 2.8 Progressive Scan CMOS, 1920 × 1080 at 25fps, 2.8mm Fixed lens, 0.028 Lux at F1.2, ICR, ONVIF, support H.265, H.264, MJPEG, 120db WDR, 3D Digital Noise Reduction, Three individually configurable stream, 12 VDC PoE, IR range 40m, Support on-board storage up to 128 GB (SD card not included), IP67, IK10, Edge Anlalytics- Line crossing detection, Intrusion detection, Motion detection, Scene change detection, video tampering, UL, CE, FCC certified. | Nos. | 0.00 | 4.00 |  | 2500
41350 |  | NVR 16 Channel Connect Up to 16 IP Cameras, Dual OS, Up to 8 Megapixels Resolution, HDMI output with 4k output and VGA output with 2MP Output , Support H.265,H.264, MJPEG, Incoming Bandwidth 160 Mbps, 4 SATA Hard Disks, ANR Technology, 2 SATA interfaces for 2 HDDs and capacity of each HDD upto 6TB, 2 USB at least 1 × USB with 3.0, Serial interface 1 RS-485, 1 RS-232, Alarm I O 16 4, 2 RJ-45 10 100 1000 Mbps self-adaptive Ethernet interface, Multiple network monitoring Web viewer, CE, FCC, UL certified. | Nos. | 0.00 | 1.00 |  | 16000
41351 |  | 16 Port Network Switch Gigabit POE 16 × gigabit PoE ports, 1 × gigabit RJ45 port, and 1 × gigabit SFP fiber optical port, IEEE 802.3at af standard | Nos. | 0.00 | 1.00 |  | 17000
41352 |  | CAT 6 Connector | Nos. | 0.00 | 8.00 |  | 160
41353 |  | Hard Disk 6 TB | Nos. | 0.00 | 2.00 |  | 22000
41354 |  | Suplly installation of Computer system as required | Nos. | 0.00 | 1.00 |  | 120000
41355 |  | Installation labour charges | Job | 0.00 | 1.00 |  | 6000
41356 |  | Supply, Drawing and Testing of 4 pair ,100 Ohm, 24 AWG UTP Cat 6 Cable as per latest amendments of TIA EIA 568 B.2 specifications for Data Telephone points in existing MS PVC conduits including making connections to Information outlets and patch panels with ferruling at both ends for identification with necessary tools for punching ,stripping crimping and testing as required | Mtr | 0.00 | 80.00 |  | 195
41357 |  | Supply and laying of HDMI Cabel | Nos. | 0.00 | 1.00 |  | 500
41358 |  | Supply and Laying of RIGID PVC Medium Duty Conduits ISI marked conduits complete with accessories such as bends, junction boxes, pull boxes etc., in recess or on surface including cutting chases in the walls floors and making good the same complete as required. 25 mm dia | RM | 0.00 | 32.00 |  | 105
41359 |  | Supply , Installation, Testing and Comissioning of Wall mounted Communication rack with glass doors, handles ,lock , Top and Bottom Cable entries, Supports for mounting rack on wall , Cable managers, one Fan, Equipment mounting hardware, power supply box for supplying power to switches, fans etc along with earth continuity kit, Mcb, indicator, moulded power supply cable . 12U(44 mm ) wall mounted | Nos. | 0.00 | 1.00 |  | 5000
41360 |  | UPS System Supply,Installation, testing and commissioning of following type of Online UPS Inverter as per drawings and specifications with all other accessories. Online UPS 1.2.0KVA UPS12V DC 25AH maintenance free batteries for 30 minutes battery backup. Input supply voltage -230-250 Volts Output voltage -220-240V+ -1% Voltage Regulation -Less than or equal to + - 1% Output frequency -50 Hz + - 0.05 Hz Type of cooling -Forced air cooled Invertor Efficiency -Better than 85% Output Power factor -0.8 | Nos. | 0.00 | 1.00 |  | 45000