## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
161124 |  | PNG Gas Daiphram Type Meter Model G-4 , Running Pressure 2-bar, Flow Rate 6 m3 or h with fiting (elbo,tee,Cupler) - honywell or Matrix | Nos. | 0.00 | 1.00 |  | 0
161125 |  | Pressure Control Regulator RJ-4 Inlet 0 to 19 bar, Outlet 0 to 1.5 Bar - United or honywell | Nos. | 0.00 | 1.00 |  | 0
161126 |  | Gas Filter 25mm almuniam Body - Vanaz or Honywell or vel | Nos. | 0.00 | 1.00 |  | 0
161127 |  | Pressure Gauge 4 inch Dail 2.5 Bar - Mahaveer or H-guru | Nos. | 0.00 | 2.00 |  | 0
161128 |  | Low Pressure Gauge 0.500Mbar ( for used Low pressure Equipment) - Mahaveer or H-guru | Nos. | 0.00 | 2.00 |  | 0
161129 |  | Low Presssure Regulator RJ-4 Blue ( For Used Point Deck Oven) - united or Vanaz | Nos. | 0.00 | 2.00 |  | 0
161130 |  | MS Pipe 40 mm NB IS-1239 ,, MS Fitting (Elbow. Tee, Reducer ANSI B16.5 , 11 ) MS Support , U-Clamp , M clamp , Sleeve and ancher Fastner . - Tata or Jindal or MSL | Nos. | 0.00 | 30.00 |  | 0
161131 |  | CS Ball Valve 40 NB Srew end 150 # single pc design ASME-B16.10 - L T | Nos. | 0.00 | 2.00 |  | 0
161132 |  | Ball Valve 15 NB Screwed , NPTTF end, 3 pcs design ASME B16.10 (for Used Point) - L T | Nos. | 0.00 | 5.00 |  | 0
161133 |  | Painting of pipes. 2 coats of red oxide and 2 coats of Golden Yellow final paint. Total 120 microns thickness - Acian or Burger | Nos. | 0.00 | 30.00 |  | 0
161134 |  | Hose Pipe 3 or 4 inch , Dia ,1.5 mtr Lent Havy Duty Black Used Point - Hyflex or suraksha | Nos. | 0.00 | 4.00 |  | 0
161135 |  | Testing commissioning of Pipe with Nitrogen gas for Testing with pressure of 6 Bar to test all joints with soap test for the leakage , then it will be time holded for 4 hrs then 6 hrs finally 24 hrs to check wheather the leakage is there or not. After | Nos. | 0.00 | 1.00 |  | 0
161136 |  | LPG Leak Detector Alarm System - | Nos. | 0.00 | 0.00 |  | 0
161137 |  | Gas Leakage Detector Display Type - Ambetronic or Crimcent | Nos. | 0.00 | 4.00 |  | 0
161138 |  | Control alarm Panel 4 zone - Ambetronics or N.G | Nos. | 0.00 | 1.00 |  | 0
161139 |  | Solenoid valve with Fittings(65MM) 24V DC - Uflow or Falocon | Nos. | 0.00 | 1.00 |  | 0
161140 |  | Siren Flash or Hooter 24V DC - agni | Nos. | 0.00 | 1.00 |  | 0
161141 |  | Armoured cable 3C x 1.5mm - Polycabe | Nos. | 0.00 | 50.00 |  | 0