## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
137769 |  | CHILLED WATER TYPE CSU AHU UNITS 11.0TR - (4400CFM) static-50mm - Supply, installation, testing commissioning of Double skin construction draw thru type AIR HANDELING UNIT. Direct Driven Backward Curved Plug Fans with VFD, with Squirrel cage IE2 induction motor, GSS frame supporting frame work, Plug type fan, vibration isolators, base frame, Motor shall be suitable for operation of Variable Frequency Drive operation with 415±10% volts, 3 phase AC supply.cost included for VFD. Coils shall have 12.5 to 15 mm dia (O.D )tubes minimum 0.35 mm thick with sine wave aluminium fins firmly bonded to copper tubes assembled in zinc coated steel frame. Face and surface areas shall be such as to ensure rated capacity from each unit and such that the air velocity across the coil shall not exceed 150 meters per minute. The coil shall be pitched in the unit casing for proper drainage. The coil shall have suitable size header with Chilled water COIL supply return connections protruding out of AHU casing by minimum 150 mm. Each coil shall be factory-tested at 21 kg per sq. m air pressure under water. Tube shall be mechanically expanded for minimum thermal contact resistance with fins. Fin spacing shall be 8 - 12 fins per cm. Water pressure drop in coil shall not exceed 10 PSIG. (Including THERMOSTAT WITH REMOTE CONTROL cable) | Nos | 0.00 | 2.00 |  | 0
137770 |  | 65 mm dia - CHILLED WATER PIPING - Supply, delivery, installation, testing of MS C class piping complete with fittings (bends, Tees, reducers, flanges etc.)of class O elastomeric 13mm Nitrile Rubber with 2 coats – one on the insulated surface along with Glass Cloth | Rmt | 0.00 | 18.00 |  | 0
137771 |  | 40 mm dia - CHILLED WATER PIPING - Supply, delivery, installation, testing of MS C class piping complete with fittings (bends, Tees, reducers, flanges etc.)of class O elastomeric 13mm Nitrile Rubber with 2 coats – one on the insulated surface along with Glass Cloth | Rmt | 0.00 | 10.00 |  | 0
137772 |  | 65 mm dia - Butterfly Valves with steel shaft and cast iron body (PN 10) - Supply, delivery, Installation testing of Valves with insulation as per specifications.Approved Make - Zoloto | Nos | 0.00 | 2.00 |  | 0
137773 |  | 40 mm dia - Butterfly Valves with steel shaft and cast iron body (PN 10) - Supply, delivery, Installation testing of Valves with insulation as per specifications.Approved Make - Zoloto | Nos | 0.00 | 4.00 |  | 0
137774 |  | 40 mm dia - Y Strainers with cast iron fabricated steel body (PN 10) - Butterfly Valves with steel shaft and cast iron body (PN 10) - Supply, delivery, Installation testing of Valves with insulation as per specifications.Approved Make - Zoloto | Nos | 0.00 | 2.00 |  | 0
137775 |  | 40 mm dia 2 way Control valve - Supply, installation, testing and commissioning of complete set of control valve kit comprising of Two Way Control Valve of C.I body of PN16 ratings, motorized modulating actuators with linear stroke of minimum 15 mm, AHU room,one thermowell,one power supply unit of 230Vac 24Vac.Tranparent IP55 Control box for mounting Digital controller and power supply unit.The valve size shall be suitable for pipe size coil capacity | Nos | 0.00 | 4.00 |  | 0
137776 |  | Supply and Installation of Auto Air Vents with ball valve - 25 mm dia. | Nos | 0.00 | 4.00 |  | 0
137777 |  | Supply and Installation of Purge valve - 25 mm dia. | Nos | 0.00 | 4.00 |  | 0
137778 |  | Pressure gauges as per specification for mounting on chilled water pipe (Range 0 - 10 kg cm2) with cock and U pipe with ball valve. | Nos | 0.00 | 4.00 |  | 0
137779 |  | Temperature gauges as per specification for mounting on pipe. (Range 0 - 50°C) with brass thermowells for mounting temperature gauges on chilled water line. | Nos | 0.00 | 4.00 |  | 0
137780 |  | drain pipe PVC complete with fitting, U trap, Support, receiving funnel preformed 3mm insulation. 32 mm | Rmt | 0.00 | 20.00 |  | 0
137781 |  | 0.63 mm (24 SWG) GSS ducting (601mm-750mm) - OVAL Ducting in Galvanised Steel - Supply, fabrication, installation and testing of GSS metal ducts as per IS-277 (120 GSM both sides, LFQ confirming to Class VIII) for GS Sheets and IS-655 for fabrication of following thicknesses including necessary G.I. hangers supports, volume control duct dampers, accessories, vanes, 3 mm neoprene rubber gasket etc. complete as per specifications in accordance with the approved shop drawings. No slip joints shall be allowed. Flanges shall be Rolamate or equivalent and ducts upto 1500 mm width shall be with rigid support (Gripple support to be provided wherever required) as per technical specifications. | Sqmt | 0.00 | 45.00 |  | 0
137782 |  | 13 mm thick - Insulation of Duct - Supplying and fixing of following thickness under deck Nitrie Rubber (Class O type of fire retadancy). (Make - Hira Technologies) | Sqmt | 0.00 | 50.00 |  | 0
137783 |  | 1.09 mm (18 MSG) MS ducting (PLENUM) - Rectangular Ducting in Galvanised Steel Supply, fabrication, installation and testing of MS SS metal ducts as per IS-277 (120 GSM both sides, LFQ confirming to Class VIII) for MS SS Sheets and IS-655 for fabrication of following thicknesses including necessary G.I. hangers supports, volume control duct dampers, accessories, vanes, 3 mm neoprene rubber gasket etc. complete as per specifications in accordance with the approved shop drawings. No slip joints shall be allowed. Flanges shall be Rolamate or equivalent and ducts upto 1500 mm width shall be with rigid support (Gripple support to be provided wherever required) as per technical specifications. | Sqm | 0.00 | 17.00 |  | 0
137784 |  | 13 mm thick - Insulation of Duct - Supplying and fixing of following thickness under deck Nitrie Rubber (Class O type of fire retadancy). (Make - Hira Technologies) | Sqmt | 0.00 | 20.00 |  | 0
137785 |  | VOLUME CONTROL DAMPER IN DUCTING -= Supply, installation and testing of GI construction louver dampers within ducts to be provided with suitable links, levers and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system | Sqm | 0.00 | 1.50 |  | 0
137786 |  | 450 x 150mm - Extruded Aluminum Powder Coated Grilles Of Required Airflow Angles With Coller Damper- EP -00 15 30 with four side flanges as following sizes. | Nos. | 0.00 | 24.00 |  | 0
137787 |  | 150mm Width - Extruded Aluminum Powder Coated Continuous Linear Grilles Of Required Airflow Angles Without V.C.D- EP -00 15 30 with four side flanges as per requirements. | Rmt | 0.00 | 20.00 |  | 0