## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
107149 |  | 0 | 0 | 0.00 | 0.00 |  | 0
107150 |  | SPLIT UNITS0 DUCTABLE UNITS HIWALL UNITS | 0 | 0.00 | 0.00 |  | 0
107151 |  | Removal of existing 8.5TR Ductable Indoor Units storing them in a good condition | 0 | 0.00 | 0.00 |  | 0
107152 |  | 8.5TR Ductable Unit | Nos | 0.00 | 8.00 |  | 0
107153 |  | 0 | 0 | 0.00 | 0.00 |  | 0
107154 |  | Re-Installation of existing 8.5TR Ductable Units. Vaccumizing, pressure testing, gas charging commissioning of the same | 0 | 0.00 | 0.00 |  | 0
107155 |  | 8.5TR Ductable Unit | Nos | 0.00 | 8.00 |  | 0
107156 |  | 0 | 0 | 0.00 | 0.00 |  | 0
107157 |  | Gas Required for commissioning | Kgs | 0.00 | 50.00 |  | 0
107158 |  | 0 | 0 | 0.00 | 0.00 |  | 0
107159 |  | Indoor Stands for 8.5TR Ductable Unit | Nos | 0.00 | 8.00 |  | 0
107160 |  | 0 | 0 | 0.00 | 0.00 |  | 0
107161 |  | Epoxy paint, Enamel paint modification if required for existing outdoor unit stand | Nos | 0.00 | 8.00 |  | 0
107162 |  | 0 | 0 | 0.00 | 0.00 |  | 0
107163 |  | 1.5TR Hiwall Split Unit ( 3 Star ) | Nos | 0.00 | 0.00 |  | 0
107164 |  | 0 | 0 | 0.00 | 0.00 |  | 0
107165 |  | REFRIGERANT COPPER PIPING FOR DUCTABLE UNITS | 0 | 0.00 | 0.00 |  | 0
107166 |  | Supply, installation, testing commissioning of refrigerant copper piping connected between odu unit IDU units covered with19 mm thick XLPE insulation. | 0 | 0.00 | 0.00 |  | 0
107167 |  | Liquid Gas Cu Piping with 19mm Al Faced XLPE insulation for Ductable Unit | Rmt | 0.00 | 10.00 |  | 0
107168 |  | Liquid Gas Cu Piping with 19mm Al Faced XLPE insulation for Hiwall Unit | Rmt | 0.00 | 2.00 |  | 0
107169 |  | 0 | 0 | 0.00 | 0.00 |  | 0
107170 |  | Communication Cable if required. Existing cable will be used. 3 Core x 2.5 Sqm Shielded Copper Cable in PVC Conduits(ODU TO IDU) | Rmt | 0.00 | 0.00 |  | 0
107171 |  | 0 | 0 | 0.00 | 0.00 |  | 0
107172 |  | 0 | 0 | 0.00 | 0.00 |  | 0
107173 |  | FAN | 0 | 0.00 | 0.00 |  | 0
107174 |  | Supply, installation, commissioning testing of Inline fans (Exhaust Fresh Air Fan) | 0 | 0.00 | 0.00 |  | 0
107175 |  | Capacity 400 cfm @ 15 mm WC static pressure- Fresh Air Fan | Nos | 0.00 | 0.00 |  | 0
107176 |  | Capacity 500 cfm @ 15 mm WC static pressure0 Fresh Air Fan | Nos | 0.00 | 0.00 |  | 0
107177 |  | Capacity 500 cfm @ 15 mm WC static pressure- Exhaust Air Fan | Nos | 0.00 | 0.00 |  | 0
107178 |  | Capacity 700 cfm @ 15 mm WC static pressure- Exhaust Air Fan | Nos | 0.00 | 0.00 |  | 0
107179 |  | 0 | 0 | 0.00 | 0.00 |  | 0
107180 |  | CONDENSATE DRAIN PIPING | 0 | 0.00 | 0.00 |  | 0
107181 |  | Supply, installation, testing Commissioning of PVC drain pipe of following sizes with 9mm thick XLPE insulation. | 0 | 0.00 | 0.00 |  | 0
107182 |  | 50mm dia With 9mm XLP insulation | Rmt | 0.00 | 35.00 |  | 0
107183 |  | 40mm dia With 9mm XLP insulation | Rmt | 0.00 | 12.00 |  | 0
107184 |  | 32mm dia With 9mm XLP insulation | Rmt | 0.00 | 15.00 |  | 0
107185 |  | 25mm dia With 9mm XLP insulation | Rmt | 0.00 | 0.00 |  | 0
107186 |  | 0 | 0 | 0.00 | 0.00 |  | 0
107187 |  | DUCTWORK ACCESSORIES | 0 | 0.00 | 0.00 |  | 0
107188 |  | Rectangular Ducting | 0 | 0.00 | 0.00 |  | 0
107189 |  | 24G0Ducting Factory Fabricated as per IS standards with angle Iron Flanges. (Supply and Installation of GI sheet metal duct, heavy duty GI angle rod wire supports, adjustable volume control Splitter dampers, guide vanes with necessary flexible conne | Sq.m | 0.00 | 265.00 |  | 0
107190 |  | 22G0 Ducting Factory Fabricated as per IS standards with angle Iron Flanges. (Supply and Installation of GI sheet metal duct, heavy duty GI angle rod wire supports, adjustable volume control Splitter dampers, guide vanes with necessary flexible conn | Sq.m | 0.00 | 125.00 |  | 0
107191 |  | 0 | 0 | 0.00 | 0.00 |  | 0
107192 |  | Supply, Installation, testing commissioning of factory built Manual Volume Control Dampers | Sq.m | 0.00 | 2.00 |  | 0
107193 |  | 0 | 0 | 0.00 | 0.00 |  | 0
107194 |  | Supply, Installation, testing commissioning of factory built Collar Volume Control Dampers | Sq.m | 0.00 | 11.00 |  | 0
107195 |  | 0 | 0 | 0.00 | 0.00 |  | 0
107196 |  | Supply, Installation, testing commissioning of factory built Fire Control Dampers | Sq.m | 0.00 | 0.00 |  | 0
107197 |  | 0 | 0 | 0.00 | 0.00 |  | 0
107198 |  | Fusible Link for Fire Control Dampers | Nos | 0.00 | 0.00 |  | 0
107199 |  | 0 | 0 | 0.00 | 0.00 |  | 0
107200 |  | Supply, Installation, testing commissioning of factory built AL Birdscreen with louvers | Sq.m | 0.00 | 1.00 |  | 0
107201 |  | 0 | 0 | 0.00 | 0.00 |  | 0
107202 |  | Insulated Plenum boxes 200 x 300 x 650 | Nos | 0.00 | 80.00 |  | 0
107203 |  | 0 | 0 | 0.00 | 0.00 |  | 0
107204 |  | SITC and balancing of grills and deffusers | 0 | 0.00 | 0.00 |  | 0
107205 |  | 3 slot grills for supply air with hit and miss dampers complete with air patern controller. | RM | 0.00 | 70.00 |  | 0
107206 |  | 3 slot grills for return air without dampers complete with air patern controller. | RM | 0.00 | 0.00 |  | 0
107207 |  | Linear Air Grilles with Al. VCD0 Linear Fixed Bar Grilles, Horizontal Fixed with removable cores, core styles 1 2 3 way with opposed Blade aluminium Bars, Normal Blade (5 mm nominal thickness) Grille height 16 mm, blade pitch 12.5 mm. 150mm wide linear g | Sq.m | 0.00 | 0.00 |  | 0
107208 |  | Linear Air Grilles without VCD0 Linear Fixed Bar Grilles for Return Air 150mm wide linear grilles without dampers | Sq.m | 0.00 | 12.00 |  | 0
107209 |  | 0 | 0 | 0.00 | 0.00 |  | 0
107210 |  | DIFFUSER | 0 | 0.00 | 0.00 |  | 0
107211 |  | Supply Air Diffusers with Al. VCD - Multicone Ceiling Rectangular Diffusers with removable cores, core styles 1 2 3 way with opposed Blade aluminium extruded construction VCD Black Anodized | Nos | 0.00 | 0.00 |  | 0
107212 |  | Return Air Diffusers without Al. VCD - Multicone Ceiling Rectangular Diffusers with removable cores, core styles 1 2 3 way with opposed Blade aluminium extruded construction. | Nos | 0.00 | 0.00 |  | 0
107213 |  | 0 | 0 | 0.00 | 0.00 |  | 0
107214 |  | Supply and installation of return air Disc valve (TOILET EXHAUST FRESH AIR) | 0 | 0.00 | 0.00 |  | 0
107215 |  | 150dia | Nos | 0.00 | 0.00 |  | 0
107216 |  | 0 | 0 | 0.00 | 0.00 |  | 0
107217 |  | Supply Installation testing and comissioning of insulated flexible duct of given sizes. Make Twiga or equal | 0 | 0.00 | 0.00 |  | 0
107218 |  | 0 | 0 | 0.00 | 0.00 |  | 0
107219 |  | Dia 200 | Rmt | 0.00 | 60.00 |  | 0
107220 |  | 0 | 0 | 0.00 | 0.00 |  | 0
107221 |  | GI Rings for Flexible Connections | 0 | 0.00 | 0.00 |  | 0
107222 |  | 200 Dia | Nos | 0.00 | 160.00 |  | 0
107223 |  | 300 Dia | Nos | 0.00 | 0.00 |  | 0
107224 |  | 0 | 0 | 0.00 | 0.00 |  | 0
107225 |  | Return air Z Piece ( 300 x 300 x 900 ) with Insulation | Nos | 0.00 | 0.00 |  | 0
107226 |  | 0 | 0 | 0.00 | 0.00 |  | 0
107227 |  | INSULATIONS-HVAC | 0 | 0.00 | 0.00 |  | 0
107228 |  | Thermal duct insulation | 0 | 0.00 | 0.00 |  | 0
107229 |  | 13mm thick Al.Faced XLPE insulation ( Aerofoam or approved equivalent) | Sq.m | 0.00 | 350.00 |  | 0
107230 |  | 0 | 0 | 0.00 | 0.00 |  | 0
107231 |  | Duct Accoustic Insulation | 0 | 0.00 | 0.00 |  | 0
107232 |  | Acoustic insulation of Ducts0 Physically crosslinked Open cell polyolefin foam with factory applied reinforced aluminium foil having density of 25kg m3 and meeting the Class 0 requirements of Fire safety as per BS 476 Part 6 7.The material shall be an | Sq.m | 0.00 | 125.00 |  | 0
107233 |  | 0 | 0 | 0.00 | 0.00 |  | 0
107234 |  | Under deck Insulastion | 0 | 0.00 | 0.00 |  | 0
107235 |  | Insulation material shall be Closed Cell Elastomeric Armaflex Nitrile Rubber, Density of Material shall be between 45 + 5 kg m3, Thermal conductivity of elastomeric nitrile rubber shall not exceed 0.035 W m?K at mean temperature of 0?C,• The insulation sh | Sq.m. | 0.00 | 330.00 |  | 0
107236 |  | 0 | 0 | 0.00 | 0.00 |  | 0
107237 |  | Scaffolding for Ducting work at Double height area. | Lot | 0.00 | 1.00 |  | 0