## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
88832 | A | FIRE SPRINKLER SYSTEM |  | 0.00 | 0.00 |  | 0
88833 |  | AUTOMATIC FIRE SPRINKLER HEADS ACCESSORIES |  | 0.00 | 0.00 |  | 0
88834 | A.1 | Supply, Installation, Testing Commissioning of Automatic Concealed Fire Sprinkler Heads (Quick Response) (Bulb type Sprinklers) with adjustable Escutcheon plates (Rosette plates). Standard Temperature Response with 5mm glass bulb, Temperature rating of 68° C, K-factor of 80, Nominal Thread size of 1 2 NPT (15mm) and an Orifice size of 13mm with a Max. Working Pressure of 12 Bar (Factory hydrostatic test pressure of 35 Bar) and to be Manufactured Certified to UL 199. Shall also include suspending arrangements with ceiling wall etc. |  | 0.00 | 0.00 |  | 0
88835 | A.1.1 | Concealed Pendant type of 68° C (Chrome Finish Plate Cover) | Nos | 0.00 | 9.00 |  | 0
88836 | A.1.2 | Concealed Pendant type of 79° C (Chrome Finish Plate Cover) | Nos | 0.00 | 3.00 |  | 0
88837 | A.2 | Supply, Installation, Testing Commissioning of Automatic Fire Sprinkler Heads (Quick Response) (Bulb type Sprinklers) with Standard Temperature Response with 5mm glass bulb, Temperature rating of 68° C 93° C, K-factor of 80, Nominal Thread size of 1 2 NPT (15mm) and a Orifice size of 13mm with a Max. Working Pressure of 12 Bar (Factory hydrostatic test pressure of 35 Bar) and to be Manufactured Certified to UL 199. It shall also include suspending arrangements with ceiling wall etc. |  | 0.00 | 0.00 |  | 0
88838 |  | FIRE SPRINKLER PIPE VALVES ACCESSORIES |  | 0.00 | 0.00 |  | 0
88839 | A.3 | Supply, Installation, Testing Commissioning of Cast Iron Butterfly Valve slimseal PN16 (working pressure of 16 Bar), standard flow control lever operated with stainless steel shaft disc, seat material with Black Nitrile EPDM, flanges nuts and bots etc. |  | 0.00 | 0.00 |  | 0
88840 | A.3.1 | 65 mm Dia | Nos | 0.00 | 1.00 |  | 0
88841 | A.4 | Supply, Installation, Testing Commissioning of Brass body Test And Drain Valve with Sight Glass, working pressure of 20 Bar (300 PSI), standard lever operated with stainless steel stem lever, with necessary weldable fittings in position as per drawings site conditions. |  | 0.00 | 0.00 |  | 0
88842 | A.4.1 | 25 mm Dia | Nos | 0.00 | 1.00 |  | 0
88843 | A.5 | Supply, Installation, Testing Commissioning of Flow Switch on Sprinkler distribution header pipe with a working pressure of 31 Bar (450 PSI) and a flow sensitivity range of 4-10 GPM (15 - 38 LPM) on each floor zone inside proposed demise area tap of point, shall be connected to fire alarm panel through cable. |  | 0.00 | 0.00 |  | 0
88844 | A.5.1 | 65 mm Dia | Nos | 0.00 | 1.00 |  | 0
88845 |  | FIRE SPRINKLER PIPING |  | 0.00 | 0.00 |  | 0
88846 | A.6 | Supply, Installation, Testing Commissioning of GI C Class Fire Sprinkler Pipe confirming to IS 1239 with all fittings like bends, tees, flanges, nut, bolt and washers etc, and proper pipe supports to not more than 3 meter apart of the pipe length. The pipe work shall be hydrostatically tested for not less than 2 hours at 15 Bar (or 1.5 times the working) pressure without leak. The pipes are to be applied with 2 coats of primer (indicated film thickness, dry 50 microns) and 2 coats of enamel finish paint of approved colour (indicated film thickness, dry 30 microns) |  | 0.00 | 0.00 |  | 0
88847 | A.6.1 | 25 mm Dia | Mtr | 0.00 | 30.00 |  | 0
88848 | A.6.2 | 40 mm Dia | Mtr | 0.00 | 15.00 |  | 0
88849 | A.6.3 | 50 mm Dia | Mtr | 0.00 | 10.00 |  | 0
88850 | A.6.4 | 65 mm Dia | Mtr | 0.00 | 2.00 |  | 0
88851 |  | SPRINKLERS BRAIDED FLEXIBLE PIPE |  | 0.00 | 0.00 |  | 0
88852 | A.7 | Providing fixing testing and commissioning of UL Rated Braded SS Flexible pipe ( Assumed required at site) 1500 MM LONG | No. | 0.00 | 12.00 |  | 0