## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
177190 | C | AC PIPING AND ACCESSORIES |  | 0.00 | 0.00 |  | 0
177191 |  | AC CONDENSATE DRAIN PIPE |  | 0.00 | 0.00 |  | 0
177192 | C.1 | Supply, installation and testing of Rigid uPVC drain water piping of approved make with necessary supports and fittings like, U-traps, elbows, tees and reducers. |  | 0.00 | 0.00 |  | 0
177193 | C.1.1 | 32 mm Ø | Mtr | 0.00 | 8.00 |  | 350
177194 | D | AIR DISTRIBUTION DUCTS |  | 0.00 | 0.00 |  | 0
177195 |  | RECTANGULAR DUCTS |  | 0.00 | 0.00 |  | 0
177196 | D.1 | Supply, installation and testing of Galvanized Iron (GI) Galvanized Steel (GS) 120GSM Zinc coated factory fabricated Square Rectangular Ducts of approved make with all necessary fittings, connections, vanes, flanges, bracings, gaskets, duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, slotted rails, threaded rods, anchor bolts, nuts, bolts, structural beam clamps as applicable. The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport local regulatory or approval body having jurisdiction. |  | 0.00 | 0.00 |  | 0
177197 | D.1.1 | 24 Gauge - (0.70 mm Thick) - Supply Air Duct | Sq.mtr | 0.00 | 55.00 |  | 2850
177198 | D.1.2 | 24 Gauge - (0.70 mm Thick) - Return Air Duct | Sq.mtr | 0.00 | 6.00 |  | 2850
177199 | D.1.3 | 24 Gauge - (0.70 mm Thick) - Fresh Air Duct | Sq.mtr | 0.00 | 45.00 |  | 2950
177200 | D.1.4 | 22 Gauge - (0.85 mm Thick) - Fresh Air Duct | Sq.mtr | 0.00 | 4.00 |  | 3850
177201 | D.2 | Supply, installation and testing of Mild Steel (MS) Ducts fabricated with hot rolled or cold rolled black steel sheets Square Rectangular Ducts of approved make with fully welded leak proof construction with Fire rated spay coat conforming to NFPA 96 Standards. with all necessary fittings, connections, vanes, flanges, bracings, gaskets, duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, threaded rods, anchor bolts, nuts, bolts, structural beam clamps as applicable. Duct and all other accessories shall be fire resistant, The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport local regulatory or approval body having jurisdiction. |  | 0.00 | 0.00 |  | 0
177202 | D.2.1 | 18 Gauge - (1.21 mm Thick) - Kitchen Exhaust Air Duct | Sq.mtr | 0.00 | 39.00 |  | 3950
177203 |  | ROUND DUCTS |  | 0.00 | 0.00 |  | 0
177204 | D.3 | Supply, installation, and testing of Galvanized Iron (GI) Galvanized Steel (GS) 120GSM Zinc coated factory fabricated Round Ducts of approved makes with all necessary fittings, round connectors, duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, slotted rails, threaded rods, anchor bolts, nuts, bolts, structural beam clamps as applicable. The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport local regulatory or approval body having jurisdiction. |  | 0.00 | 0.00 |  | 0
177205 | D.3.1 | 24 Gauge - (0.70 mm Thick) - Supply Air Duct | Sq.mtr | 0.00 | 7.00 |  | 3950
177206 |  | DUCT ACCESS DOORS |  | 0.00 | 0.00 |  | 0
177207 | D.4 | Supply, installation, and testing of Hinged type Duct Access Doors as per drawings and to allow easy and convenient access to equipment or any other component within ductwork with all necessary fittings, accessories and airtight gaskets etc. |  | 0.00 | 0.00 |  | 0
177208 | D.4.1 | 300 mm X 300 mm - (MS) | Nos | 0.00 | 5.00 |  | 9500
177209 |  | FLEXIBLE DUCTS |  | 0.00 | 0.00 |  | 0
177210 | D.5 | Supply, installation, and testing of aluminum-polyester casing Round Insulated Flexible Duct of approved make reinforced with spiral wound steel wire, Temperature range -20° C to +140° C, with a standard Insulation with a 25mm thick mineral wool, covered with aluminum-polyester film casing and with all necessary connections, fixing and support arrangements. |  | 0.00 | 0.00 |  | 0
177211 | D.5.1 | 250 mm Ø | Mtr | 0.00 | 5.00 |  | 3000
177212 | D.6 | Supply, installation, and testing of Flexible Duct Connectors (Canvas connection) of approved make to isolate vibrations and noises caused by fans or any other equipment s connected to the duct with air tight fittings with all necessary accessories. |  | 0.00 | 0.00 |  | 0
177213 | D.6.1 | For Air Washer Unit | Nos | 0.00 | 2.00 |  | 15500
177214 | D.6.2 | For Kitchen Exhaust air Fan | Nos | 0.00 | 2.00 |  | 18500
177215 | E | AIR DISTRIBUTION DUCT - THERMAL INSULATIONS ACCOUSTIC LINNINGS |  | 0.00 | 0.00 |  | 0
177216 |  | AIR DISTRIBUTION DUCT - THERMAL INSULATIONS |  | 0.00 | 0.00 |  | 0
177217 | E.1 | Supply, installation of Thermal Insulation of approved make for duct insulation using closed-cell elastomeric nitrile rubber Class O rated as per BS 476 Part 6 1989 for fire propagation test and for Class 1 as per BS 476 Part 7, 1987 for surface spread of flame test. Water vapour permeability shall be not less than 0.024 per inch (2.48 x 10-13 Kg m.s.Pa i.e. µ>7000 Water Vapor diffusion resistance) as per DIN 53122 part 2, DIN 52615 EN 12086 EN13469. Insulaton shall be black Colour with having a density of 50 ± 10 Kg M3. Quote shall be inclusive of necessary Adhesive. |  | 0.00 | 0.00 |  | 0
177218 | E.1.1 | 25 mm thicknesses | Sq.mtr | 0.00 | 117.00 |  | 2550
177219 | E.2 | Supply, installation of Thermal Insulation of approved make for Kitchen exhaust ducting using Resin Bonded Fibre Glass Wool (Asbestos Free) with Aluminum Foil covering, density of not less than 48 Kg m3. Quoute shall be inclusive of necessary Adhesive. |  | 0.00 | 0.00 |  | 0
177220 | E.2.1 | 80 mm thicknesses - For Kitchen Exhaust | Sq.mtr | 0.00 | 39.00 |  | 3000
177221 | F | AIR DISTRIBUTION DUCT - DAMPERS |  | 0.00 | 0.00 |  | 0
177222 |  | DUCT AIR CONTROL DAMPERS |  | 0.00 | 0.00 |  | 0
177223 | F.1 | Supply, installation, testing and commissioning of aluminum powder coated Opposed Blade Damper Collar Damper of approved make. |  | 0.00 | 0.00 |  | 0
177224 | F.1.1 | Size - 300 x 300 mm | Nos | 0.00 | 9.00 |  | 7500
177225 | F.1.2 | Size - 375 x 375 mm | Nos | 0.00 | 4.00 |  | 8500
177226 | F.2 | Supply, installation, testing and commissioning of Aluminium powder coated Low Leakage Square Rectangular Volume Control Damper of approved make with aero-foil opposed blades and nylon gears system outside air stream with adjustable handle with position arresting bolt. |  | 0.00 | 0.00 |  | 0
177227 | F.2.1 | Size - 350 x 200 mm | Nos | 0.00 | 2.00 |  | 7500
177228 | F.2.2 | Size - 550 x 250 mm | Nos | 0.00 | 2.00 |  | 8500
177229 | F.2.3 | Size - 300 x 200 mm | Nos | 0.00 | 2.00 |  | 7000
177230 | F.3 | Supply, installation, testing and commissioning of MS powder coated Low Leakage Square Rectangular Volume Control Damper of approved make with aero-foil opposed blades and nylon gears system outside air stream with adjustable handle with position arresting bolt. (For Kitchen Exhaust MS duct) |  | 0.00 | 0.00 |  | 0
177231 | F.3.1 | Size - 500 x 400 mm | Nos | 0.00 | 1.00 |  | 8500
177232 | F.3.2 | Size - 450 x 250 mm | Nos | 0.00 | 4.00 |  | 9500
177233 | F.4 | Supply, installation, testing and commissioning of Circular Volume Control Damper of approved make with high quality Galvanized steel and Flap Blade fixed with nylon bushes, with hand locking quadrant. |  | 0.00 | 0.00 |  | 0
177234 | F.4.1 | Size - 250 mm Ø | Nos | 0.00 | 2.00 |  | 6500
177235 | G | AIR TERMINALS - (GRILLES, REGISTERS, DIFFUSERS LOUVERS) |  | 0.00 | 0.00 |  | 0
177236 |  | DIFFUSERS |  | 0.00 | 0.00 |  | 0
177237 | G.1 | Supply, installation, testing and commissioning of Extruded Aluminium Square Ceiling Diffuser of approved make with Four way throw with all necessary fixing arrangements. Powder coated finish with RAL Colour as required by ID Designer Architect. |  | 0.00 | 0.00 |  | 0
177238 | G.1.1 | Neck Size - 300 mm X 300 mm (Outer Size - 440 mm X 440 mm) | Nos | 0.00 | 17.00 |  | 5500
177239 | G.1.2 | Neck Size - 375 mm X 375 mm (Outer Size - 600 mm X 600 mm) | Nos | 0.00 | 4.00 |  | 5500
177240 | H | DISMANTLING OF EXISTING DUCTS |  | 0.00 | 0.00 |  | 0
177241 | H.1 | Remove and dispose of the existing supply air duct branch, fittings, insulation, and supports etc. and install new duct sections to match the new design, including necessary supports and hangers. |  | 0.00 | 0.00 |  | 0
177242 | H.1.1 | Dismantling of existing ducts | Lot | 0.00 | 1.00 |  | 100000
177243 | J | HVAC SERVICE IDENTIFICATION LABELS, SIGNS TAGS |  | 0.00 | 0.00 |  | 0
177244 | J.1 | All services like Ducts, Pipes need to be clearly labelled or tagged at site with service identification flow direction etc. And all equipment needs to tagged as per Airport requirements. |  | 0.00 | 0.00 |  | 0
177245 | J.1.1 | Labelling Tagging for Services and Equipment s | Lot | 0.00 | 1.00 |  | 125000
177246 | K | TESTING AND BALANCING |  | 0.00 | 0.00 |  | 0
177247 | K.1 | Air balancing of Supply, Return, Fresh air and Exhaust air system to arrive as per design air flow rates |  | 0.00 | 0.00 |  | 0
177248 | L | SHOP DRAWINGS APPROVALS |  | 0.00 | 0.00 |  | 0
177249 | L.1 | Preparation and submission of a detailed shop drawing for the HVAC system after a thorough study of design drawings, site surveys, and relevant airport standards with correct routing, size, and elevations. The drawings also need to be coordinated with other MEP services like Electrical, Plumbing, and fire services, with the latest Architectural and Interior design drawings, before construction. Necessary amendments to the drawings are to be made and resubmitted in case of any variations on site while at the construction stage of the project. Also prepare relevant detailed connection drawings as per selected manufacturer details and Airport standards, with necessary approval to be obtained from consultants and authority regulatory bodies having jurisdiction, along with material submission approval with airport authorities. |  | 0.00 | 0.00 |  | 0
177250 | M | MISCELLANEOUS OR ANY ADDITIONAL ITEMS |  | 0.00 | 0.00 |  | 0
177251 | M.1 | The contractor needs to mention any additional items or missing items that are not mentioned in the above BOQ after a detailed site survey or inspection and to be validated by consultants. |  | 0.00 | 0.00 |  | 0
177252 | M.1.1 | Item 1 - (Contractor to describe only if there are any) | Unit | 0.00 | 1.00 |  | 0
177253 | M.1.2 | Item 2 - (Contractor to describe only if there are any) | Unit | 0.00 | 1.00 |  | 0
177254 | M.1.3 | Item 3 - (Contractor to describe only if there are any) | Unit | 0.00 | 1.00 |  | 0