## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
141453 | 1 | Ducting (Factory Fabricated) |  | 0.00 | 0.00 |  | 0
141454 | 1.1 | Supplying, installing, testing and balancing of Galvanised Steel Sheet (Completely Factory Fabricated with TDF Slip ON Flanges) 120 GSM seamed ducting of following thickness including necessary supports, hangers, nuts, bolts, gaskets, splitter dampers, turning vanes, canvas connections etc. complete as per technical specifications. All archs shall have baffles inside. The bidder shall quote his rates considering elbows, reducers, tees, baffles etc. The thickness of ducting shall be according to IS 655- 1963. Support Gaskets shall be provided striclty as per the technical specifications, drawings. Support shall be considered at an interval of 2.5 mtrs and on all branches. For all main ducts engraved labels shall be provided as per reqmt of EIC. Measurement shall be made based upon effective duct area, Contractor to bid accordingly.- Rectifcation of Exisiting |  | 0.00 | 0.00 |  | 0
141455 |  | Rectangular seamed galvanised steel sheet ducting |  | 0.00 | 0.00 |  | 0
141456 | 1.1.2 | 24 Gauge | Sqm. | 0.00 | 10.00 |  | 0
141457 |  | (Up to 20% can be manual fabricated based on site conditions) |  | 0.00 | 0.00 |  | 0
141458 | 2 | Ducting built-in components |  | 0.00 | 0.00 |  | 0
141459 | 2.1 | Rectangular Manually Operated Duct Collar Dampers |  | 0.00 | 0.00 |  | 0
141460 |  | Supplying, installing, testing and balancing of rectangular volume control damper made of 18 G GI casing 120 mm wide and 20 G GI sheet blade 100 mm wide, chrome plated spindles, self lubricating bushes blade linkage fully enclosed, handle operation with status indicator suitable for rectangular ducting connection. | Sqm. | 0.00 | 2.00 |  | 0
141461 | 2.2 | Supplying, Fixing, Testing and Commissioning of supply air Grills of powder coated aluminium with all accessories.Supplying, installing, testing and balancing of alumnimium powder coated linear rectangular single louvered grill for supply return air(sample shall be approved before the execution). |  | 0.00 | 0.00 |  | 0
141462 | 2.2.1 | Supply air grilles with GI damper | Sqm. | 0.00 | 1.50 |  | 0
141463 | 2.2.2 | Return Exhaust air Grilles without GI damper | Sqm. | 0.00 | 2.00 |  | 0
141464 | 2.2.3 | Supply air squire diffuser with GI damper | Sqm. | 0.00 | 5.00 |  | 0
141465 | 2.2.5 | Fresh Exhaust air Louvers with VCD, Bird screen wire mesh etc. | Sqm. | 0.00 | 1.00 |  | 0
141466 | 4 | Duct Insulation |  | 0.00 | 0.00 |  | 0
141467 | 4.1 | Supplying, installing of external thermal insulation on ducts with approved sample of Al faced closed cell nitrile rubber duct insulation with density 50 Kg Cum complete as per specifications. |  | 0.00 | 0.00 |  | 0
141468 | 4.1.1 | 9mm thick insulation | Sqm. | 0.00 | 20.00 |  | 0
141469 | 4.1.2 | 12mm thick insulation | Sqm. | 0.00 | 0.00 | RO | 0
141470 | 5 | Duct Acoustic Lining |  | 0.00 | 0.00 |  | 0
141471 |  | All rates to be inclusive of all cutting, chasing etc in brickwork partitions civil works, its repairRates to be all inclusive of disposal of debris to be dumped carted away from the site to approved dumping ground as per local statutory norms. All rates to be inclusive of any core cutting required in civil worksRates to be all inclusive of scaffolding, labour, material, tools, tackles etc. Rates to be all inclusive of preparation of shop drawings wherever required and its approvalTenants need to provide booster exhaust fan to suit their ventilation, if required. |  | 0.00 | 0.00 |  | 0