## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
7705 | 1 | Providing, laying, jointing, testing and commissioning of G.I. `C Class pipes (IS 1239 (Part-I)-1979) including cutting,threading welding etc providing all malleable galvanized iron fittings conforming to IS 1879, viz. Flanges, bends, tees, elbows,reducers, unions, supporting with G. I. clamps, hangers, M.S. brackets etc. including cutting holes and chases in brick or RCC wall slabs and making good the same to the Approval of Architect consultant,complete including painting with one coat of primer and two or more coats of synthetic enamel paint of approved make and shade. ( Note- Rigid flexible pipe extension from existing line is considered) |  | 0.00 | 0.00 |  | 0
7706 | i) | 25 mm dia. | RMT | 0.00 | 25.00 |  | 620
7707 | ii) | 32 mm dia. | RMT | 0.00 | 5.00 |  | 700
7708 | iii) | 40 mm dia. | RMT | 0.00 | 10.00 |  | 850
7709 | iv) | 50 mm dia. | RMT | 0.00 | 10.00 |  | 1050
7710 | v) | 65 mm dia. | RMT | 0.00 | 10.00 |  | 1250
7711 | vi) | 80 mm dia. | RMT | 0.00 | 0.00 |  | 1850
7712 | vii) | 100 mm dia. | RMT | 0.00 | 0.00 |  | 2150
7713 | 2 | Providing , fixing testing and commissioning of pendant type sprinkler heads 68 deg. Temp.(Quick response type)-UL listed FM approved | No. | 0.00 | 0.00 |  | 950
7714 | 3 | Providing , fixing testing and commissioning of concealed type sprinkler heads 68 deg. Temp.(Quick response type)-UL listed FM approved | No. | 0.00 | 14.00 |  | 2020
7715 | 4 | Providing , fixing testing and commissioning of upright type sprinkler heads 68 deg. temp(Quick response type)- Optional Subject to liasion team requirements | No. | 0.00 | 14.00 |  | 650
7716 | 5 | Providing , fixing testing and commissioning of upright type sprinkler heads 79 deg. Temp (Quick response type)-UL listed FM approved | No. | 0.00 | 0.00 |  | 1150
7717 | 6 | Providing fixing testing and commissioning of braided UL listed FM approved SS Flexible pipe |  | 0.00 | 0.00 |  | 0
7718 | i) | 1 MT Long | No. | 0.00 | 7.00 |  | 2000
7719 | ii) | 1.6 MT Long | No. | 0.00 | 7.00 |  | 2420
7720 | 7 | Gun metal chrome finished Ball valves (PN 16) with fittings of screwedend type. |  | 0.00 | 0.00 |  | 0
7721 | I) | 40 mm dia. | No. | 0.00 | 1.00 |  | 2400
7722 | I) | 32 mm dia. (Sprinkler drain-OPTIONAL) | Nos. | 0.00 | 1.00 |  | 2150
7723 | 8 | Wheel operated Butterfly Valves (PN 16) with inbuilt supervisory switch (UL listed and FM approved) with CI Body, Black Nitrile Body Liner and Nylon Coated SG Iron Disc with material and labour including hydraulic testing etc. complete as per drawing, specification to the level of satisfaction of Site- Incharge. |  | 0.00 | 0.00 |  | 0
7724 | I) | 150 mm dia. | No. | 0.00 | 0.00 |  | 0
7725 | I) | 100 mm dia. (OPTIONAL) | No. | 0.00 | 0.00 |  | 0
7726 | I) | 65 mm dia. | No. | 0.00 | 1.00 |  | 18500
7727 | 9 | 6kg capacity ABC type dry chemical powder fire Extinguishers with wall mounting brackets | Nos. | 0.00 | 0.00 |  | 0
7728 | 10 | 6kg capacity K type fire Extinguishers with wall mounting brackets | No. | 0.00 | 0.00 |  | 0
7729 | 11 | 5kg capacity CO2 type fire Extinguishers with wall mounting brackets | No. | 0.00 | 0.00 |  | 0
7730 | 12 | 9Lit AR-AFFF type fire Extinguishers with wall mounting brackets | Nos. | 0.00 | 0.00 |  | 0
7731 | 13 | Flow switch on sprinkler distribution header on floor with 2 SPDT contacts suitably rated, capable of the high pressure system and connected to fire alarm panel through cable. (OPTIONAL IF REQUIRED BY CLIENT) |  | 0.00 | 0.00 |  | 0
7732 | i) | 65 mm dia. | No. | 0.00 | 1.00 |  | 3500
7733 | 14 | Ceasefire 5 Kg Ceiling Mounted Fire Extinguisher Clean Agent FE-36, Zero ODP, Stored Pressure Type, Pressure Gauge, Gross Weight 7.7 Kg, empty Weight 2.7 Kg, Can Height 264MM, Diameter 240MM,Discharge Time less than 8 Secs, Auto discharge mechanism on temperature rise, applicable on Class A,B,C and electrically started Fire, Can Construction Deep drawn Co2 Mig welded, Valve Construction Forging Machining, Internal Coating of Can Epoxy Powder coating, External Coating of Can Epoxy Polyster Powder coating, Sheet metal thickness 2.0MM, Helium Leak Detection Test, 5 Years Warranty-model no 1CH21CF | No. | 0.00 | 0.00 |  | 0