## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
167686 | B | GAS SYSTEMS GAS SUPPLY EQUIPMENTS METERING |  | 0.00 | 0.00 |  | 0
167687 | B.1 | Supply, Installation, Testing, and Commissioning of Gas Meter with a maximum pressure range of 0.5 Bar or as per Airport guidelines or standards, operating temperature range of -20°C to +60°C, of approved make and with all necessary fittings and connectors, etc. |  | 0.00 | 0.00 |  | 0
167688 | B.1.1 | Max flow rate - 10 m3 h | Nos | 0.00 | 1.00 |  | 18990
167689 |  | GAS SUPPLY PIPE VALVES ACCESSORIES |  | 0.00 | 0.00 |  | 0
167690 | B.2 | Supply, Installation, Testing, and Commissioning of Chrome Plated Brass Ball Valve with double O-ring stem, nut with anti-corrosion coating, and steel lever handle with anti-corrosion treatment and PVC coating, suitable for Gas pipe service of approved make and with all necessary fittings and connectors, etc. |  | 0.00 | 0.00 |  | 0
167691 | B.2.1 | 32 mm Dia | Nos | 0.00 | 3.00 |  | 4110
167692 | B.3 | Supply, Installation, Testing, and Commissioning of Gas Solenoid Valve with manual reset, operating pressure 6 Bar, operating temperature range -15°C to +60°C with a protection class of IP65 of approved make with integration to Gas leak detection, Kitchen Fire suppression systems, and Fire alarm systems as per Airport guidelines or standards requirement and with all necessary fitting and connectors, etc. |  | 0.00 | 0.00 |  | 0
167693 | B.3.1 | 20 mm Dia | Nos | 0.00 | 2.00 |  | 9430
167694 | B.4 | Supply, Installation, Testing, and Commissioning of Automatic Gas Shutt-off Valve of approved make and with all necessary fitting and connectors |  | 0.00 | 0.00 |  | 0
167695 | B.4.1 | 25 mm Dia | Nos | 0.00 | 1.00 |  | 9880
167696 | B.5 | Supply, Installation, Testing, and Commissioning of Second Stage Regulator with adjustable pressure control, inlet pressure of 0.5 Bar, and outlet pressure to suit the kitchen equipment of approved make and with all necessary fittings and connectors, etc. |  | 0.00 | 0.00 |  | 0
167697 | B.5.1 | AS PER EQUIPMENT REQUIREMENTS | Nos | 0.00 | 3.00 |  | 3670
167698 | B.6 | Supply, Installation, Testing, and Commissioning of Pressure Guage with a range of 0 - 30 PSI (0 - 2 Bar) and 63 mm dial size of approved make and with all necessary fittings, isolation valves and connectors, etc. |  | 0.00 | 0.00 |  | 0
167699 | B.6.1 | 1 4 - inch NPT on bottom Connection | Nos | 0.00 | 2.00 |  | 1880
167700 |  | GAS SUPPLY PIPING |  | 0.00 | 0.00 |  | 0
167701 | B.7 | Supply, Installation, Testing, and commissioning of Schedule 40 Carbon Steel Pipe with all necessary fittings such as bends, elbows, tees, reducers, unions, threading, cutting and welding etc. The pipes are to be applied with 2 coats of primer and 2 coats of enamel finish paint of approved color and with proper pipe supports necessary as per standards and site condition requirements. Complete pipeline to be flushed with Nitrogen before commissioning of the system. |  | 0.00 | 0.00 |  | 0
167702 | B.7.4 | 20 mm Dia | Mtr | 0.00 | 10.00 |  | 980
167703 | B.7.5 | 25 mm Dia | Mtr | 0.00 | 7.00 |  | 1090
167704 | B.7.6 | 32 mm Dia | Mtr | 0.00 | 8.00 |  | 1210
167705 | B.8 | Supply, Installation, Testing, and commissioning of Corrugated Stainless Steel Flexible Gas Pipe (CSST) conforming to BS EN 15266 with an operating pressure of 0.5 Bar, UV resistant PVC jacket, and all necessary fittings such as adapters, couplers, tees, nipples, reducers, nuts, washers, gasket, and necessary connections, etc. Proper pipe supports are necessary as per standards and site conditions requirements. |  | 0.00 | 0.00 |  | 0
167706 | B.8.1 | 15 mm Dia | Mtr | 0.00 | 3.00 |  | 510
167707 | C | GAS SERVICE IDENTIFICATION LABELS, SIGNS TAGS |  | 0.00 | 0.00 |  | 0
167708 | C.1 | All services for pipes Like Type of Gas, pipe size, Flow direction need to be clearly labelled or tagged at site with service identification flow direction etc. And all equipment needs to tagged as per Airport requirements. |  | 0.00 | 0.00 |  | 0
167709 | C.1.1 | Labelling Tagging for Services and Equipment s | Lot | 0.00 | 1.00 |  | 2000
167710 | D | TESTING COMMISSIONING |  | 0.00 | 0.00 |  | 0
167711 | D.1 | Pressure test for Gas supply piping system for leak detection |  | 0.00 | 0.00 |  | 0
167712 | D.1.1 | Gas piping systems are to be tested at the site with a test pressure three times the working or operating pressure recommended as per airport design guidelines for a holding time period of at least 30 minutes. The test is to be conducted after the complete installation of all gas supply pipes, including all valves and accessories, as per the proposed design. | Set | 0.00 | 1.00 |  | 12300