## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
154698 |  | Low Side Works |  | 0.00 | 0.00 |  | 0
154699 |  | Chilled Water Piping with Nitrile Rubber Insulation - Supplying, laying or fixing, testing and commissioning of MS C class chilled water piping (cut of required length and installed with welded joints. The necessary fittings such as elboues, tees etc. shall all to included in this item). The Insulation shall be Class O nitrile Rubber pre-slit, pipe sleeve upto 100 mm dia and sheet for bigger dia with factory Laminated 7 mill woven glass cloth of thicknesses as specified, with approved adhesive. Manufactured supplied, suitable sized nitrile rubber pipe supports with PUF or PIR inserts shall be used. Thermal conductivity should not exceed 0.035 W or MK at 0 degree celsius and water vaper resisitance > 7000. Manufactures tapes and adhesive to used only. The pipe supports should also be of nitrile rubber with PUF or PIR inserts and are to be installed as per manufacturer s recomendation. The pipe fittings shall be MS. class for pipes upto 150 mm and for 200mm and above, same material of the pipe shall be usee all bends or Reducess or Tee upto 150 mm shall be factory fabricated ready made MS C class. Note Use proper template for marking block colour Arrows pipe. for supply or return. |  | 0.00 | 0.00 |  | 0
154700 |  | 40mm dia with 38mm (25 mm + 13 mm) dia thick insulation | Mtrs. | 0.00 | 15.00 |  | 1425
154701 |  | 32mm dia with 38mm (25 mm + 13mm) dia thick insulation | Mtrs. | 0.00 | 50.00 |  | 1330
154702 |  | Insulated Valves |  | 0.00 | 0.00 |  | 0
154703 |  | Dynamic Balancing Valve-PID type |  | 0.00 | 0.00 |  | 0
154704 |  | Supply and installation, testing and commissioning of BMS Compatible electronic self balancing valve with integrated two way modulating control valves in a single body. The actuator shall be capable of accepting 230V or 24V or 2-10VDC or 4-20 mA electrical signed and shall provided similar transduced feed back output singed to control system. The minimum close off pressure of actuator must be 1.5 times shut of head of pump as per Specification of following size. The actuator shall be microprocessor based with self calibration feature. All the valve shall be complete with step down transformers, thermostat, control wiring and probe. 0-20 USGPM (32 mm dia) Insulation as per pipes | Nos. | 0.00 | 1.00 |  | 23270
154705 |  | Ball valves with Strainer Providing and Fixing of the following insulated ball valve having a heavy duty forged body as per approved make. The ball shall be of bronze construction duty chrome plated. 32 mm dia - PN-16 with insulation same a Chilled water piping | Nos | 0.00 | 4.00 |  | 7125
154706 |  | Providing and Fixing digital type thermometers with copper well, valve and probe suitable for binder test point application. 6 INCH long (Insulated) | Nos. | 0.00 | 2.00 |  | 16150
154707 |  | Dial Presure Guages (glycerine filled Type) with SS Encasing with isolating valve and piping etc.The gauge should be with appropriate range and valve and fitted with probe suitable for binder test point application as well. 4 inch Dial (Insulated) | Nos. | 0.00 | 2.00 |  | 2850
154708 |  | Providing and Fixing of automatic air vent of approved make with insulation valves as per specifications or drawings - 20mm dia | Nos. | 0.00 | 4.00 |  | 2330
154709 |  | Drain Piping Supply, Installation, testing and commissioning of UPVC condensate drain pipe along with necessary clamps, fittings sich as bends, tees, etc. it shall be insulated with 9 mm thick nitrile foam insulation in tubular form as per specifications. 25 mm dia | Mtrs. | 0.00 | 15.00 |  | 570
154710 |  | BTU Meter Supply, Installation, testing and commissioning of BTU Meter as per specifications given or approved from airport authorities. 40 mm dia | Nos | 0.00 | 1.00 |  | 62700
154711 |  | DUCTING |  | 0.00 | 0.00 |  | 0
154712 |  | G.I. Sheet Metal Ducting - Factory Fabricated - Supply, Installation, Testing and Commissioning of factory fabricated GSS sheet metal rectangular ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required. |  | 0.00 | 0.00 |  | 0
154713 |  | 0.50 MM (26 Gauge) | Sqm. | 0.00 | 65.00 |  | 2330
154714 |  | 0.63 MM (24 Gauge) | Sqm. | 0.00 | 80.00 |  | 2375
154715 |  | 0.80 MM (22 Gauge) | Sqm. | 0.00 | 15.00 |  | 2520
154716 |  | 1.00 MM (20 Gauge) | Sqm. | 0.00 | 10.00 |  | 2615
154717 |  | 1.25 MM (18 Gauge) | Sqm. | 0.00 | 5.00 |  | 2755
154718 |  | G.I. Sheet Metal Ducting - Site Fabricated - Supply,Installation, Testing and Commissioning of site fabricated GSS sheet metal rectangular ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required. |  | 0.00 | 0.00 |  | 0
154719 |  | 0.63 MM (24 Gauge) | Sqm. | 0.00 | 20.00 |  | 2375
154720 |  | 0.80 MM (22 Gauge) | Sqm. | 0.00 | 20.00 |  | 2520
154721 |  | INSULATION |  | 0.00 | 0.00 |  | 0
154722 |  | Nitrile Rubber Insulation- Class O - Supplying and fixing of closed cell elastomeric insulation of following thickness and density 55 kg or cu.m.and K valueof not less than 0.037W or mk at 20 deg C as per specifications and drawings (For indoor applications) with factory Laminated 7 mill woven glass cloth |  | 0.00 | 0.00 |  | 0
154723 |  | 19 mm thick (AC and Fresh Air Duct) | Sqm. | 0.00 | 100.00 |  | 380
154724 |  | 25 mm thick (Exhaust Duct) | Sqm. | 0.00 | 80.00 |  | 430
154725 |  | Acoustic Lining Supplying and Application of Acoustic lining within the Supply Air duct with 10 mm thick class O open cell nitrile Rubber of density 140-160 kg. or Cubm. as per spefications. 15 MM Thick | Sqm | 0.00 | 10.00 |  | 1150
154726 |  | DUCT ACCESSORIES |  | 0.00 | 0.00 |  | 0
154727 |  | Supply,Installation, Testing and Commissioning of GI multiblade volume control duct damper complete with neoprene rubber gaskets, nuts, bolts, screws linkages, flanges etc., as per specifications. | Sqm. | 0.00 | 2.00 |  | 10925
154728 |  | Supply,Installation, Testing and Commissioning of multiblade Al volume control Collar or Grille or exhaust Air Opening damper complete with suitable links, lever and quadrants for manual control of airflow and with suitable links , lever and quadrants for manual control of airflow and neoprene rubber gaskets, nuts, bolts, screws, flanges etc., as per specifications. | Sqm. | 0.00 | 1.00 |  | 10925
154729 |  | Supply,Installation, Testing and Commissioning and fixing of powder coated extruded aluminium Supply or Exhaust Air Grills as per specifications | Sqm. | 0.00 | 2.00 |  | 7125
154730 |  | Supply,Installation, Testing and Commissioning and fixing of powder coated extruded aluminium Continuos Grills as per specifications - 200 MM Wide | RM | 0.00 | 12.00 |  | 1809
154731 |  | Electrical Works |  | 0.00 | 0.00 |  | 0
154732 |  | Electrical Control Panel Supply, installation, testing and commissioning of panel boards made of 2.0 mm thick steel sheet duly powder coated with voltmeter, ammeter, electronic energy meter, indicating lights, Stop or manual or Auto selector switch in each, outgoing current operated single phase preventer. The starters should have potential free contacts for connection to Building Automation System. The panel shall include contactors or over load relay with built in single phase protection or Time delay relay for delayed automatic start of the motor. All panels should have spare NO or NC Contacts for BMS applications as required. Panel-P01 (1 X 1.1 KW) OUTGOING 1 Nos. 32 Amps TP MCB ( for AHU) and each with following - Spare NO or NC Contacts for BMS Integration, Looping with Fire Alarm Panel to trip the Fan in case of Fire. - Fully automatic 1.1 KW Motor DOL starter each 20A TP Contactor , ON or OFF push buttons and on or off or Trip indicating lights , A or M selector switch for local or remote operations, CT operated Digital Ammeter, suitable NO and NC Potential free contacts for Interlocking with Fire alarm panel , 9.0 A -15 A O or L relay with inbuilt single phase preventor , selector switches etc as required. Panel P-01 as described above | Set | 0.00 | 1.00 |  | 31000
154733 |  | Cables (FRLS) - Supplying, laying, testing and commissioning of XLPE insulated copper conductor armored FRLS cables of 1.1 KV grade of following sizes directly on wall or structural frame or cable trays or racks using approved type of clamps,End terminations with Double Compression type glands on both ends, double earthing with GI strip or wire of suitable size and hardware as per specifications. |  | 0.00 | 0.00 |  | 0
154734 |  | 3 C x 4 Sq. mm | Mtrs | 0.00 | 35.00 |  | 525
154735 |  | 2C x 1.5 sqmm | Mtrs | 0.00 | 25.00 |  | 380
154736 |  | Earthing - Supplying and laying of the following earthing clamped to wall with suitable clamps saddles and fixing bolts or in ground including the cost of digging and back filling as required and complete as required to comply with IS 3043 1987. All copper joints shall be tinned. The rates shall be inclusive of making test joints where ever required |  | 0.00 | 0.00 |  | 0
154737 |  | 25 mm x 3 mm GI strip | RM | 0.00 | 24.00 |  | 380
154738 |  | 8 SWG GI Wire | RM | 0.00 | 24.00 |  | 170