## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
146348 | Part A | VRF EQUIPMENTS (Hi Side Works) |  | 0.00 | 0.00 |  | 0
146349 | 1 | VRV VRF UNITS (Supply Part) |  | 0.00 | 0.00 |  | 0
146350 |  | Outdoor Unit (Heat Pump) |  | 0.00 | 0.00 |  | 0
146351 | 1.1 | Supply of Variable refrigerant volume flow modular type air-conditioning system suitable to operate from 415±10% volt, 50 Hz,single three phase AC power supply for Heating Cooling by using inverter driven capa`city control compressors (Hermetically sealed scroll DC Twin Rotary type) complete with individual controller and fittings with necessary wiring, connection, including suitable isolator for each selected module, termination etc. M.S. frame duly painted to locate Outdoor Unit etc. as per quantity given below including full charging of R-410A refrigerant gas complete as per specifications. |  | 0.00 | 0.00 |  | 0
146352 | 1.1.1 | 20 HP (Three Phase) | Nos | 0.00 | 1.00 |  | 360000
146353 | 1.1.2 | 18 HP (Three Phase) | Nos | 0.00 | 1.00 |  | 350000
146354 | 1.2 | Indoor Units |  | 0.00 | 0.00 |  | 0
146355 |  | Supply of following Indoor units equipped with pre-filter, fan section with low noise fan, multispeed motor, coil section with DX coil, outer cabinet, drain pan, insulation, pipe connections, corded cordless remote control etc. of various capacities as per specifications and drawings. |  | 0.00 | 0.00 |  | 0
146356 | a) | Ceiling Mounted Duct Type |  | 0.00 | 0.00 |  | 0
146357 | 1.2.1 | 1377 CFM (4.0 TR 5.0 HP) | Nos | 0.00 | 1.00 |  | 40055
146358 | 1.2.2 | 2047 CFM (5.5 TR 6.9 HP) | Nos | 0.00 | 2.00 |  | 73000
146359 | b) | 4 Way Cassette Type |  | 0.00 | 0.00 |  | 0
146360 | 1.2.3 | 4.0 TR (5.0 HP) 1218 CFM | Nos | 0.00 | 3.00 |  | 41319
146361 | c) | 1 Way Cassette Type |  | 0.00 | 0.00 |  | 0
146362 | 1.2.4 | 1.3 TR (1.6 HP) 346 CFM | Nos | 0.00 | 1.00 |  | 39245
146363 | 1.2.5 | 1.6 TR (2.0 HP) 441 CFM | Nos | 0.00 | 1.00 |  | 40096
146364 | d) | Hi Wall |  | 0.00 | 0.00 |  | 0
146365 | 1.2.6 | 530 CFM Hi Wall Type (1.6TR) | Nos | 0.00 | 1.00 |  | 24739
146366 |  | Sub-Total Part- A Rs. |  | 0.00 | 0.00 |  | 0
146367 | Part B | VRF EQUIPMENTS (Low Side Works) |  | 0.00 | 0.00 |  | 0
146368 | 1 | VRV VRF UNITS |  | 0.00 | 0.00 |  | 0
146369 |  | Outdoor Unit (Heat Pump) |  | 0.00 | 0.00 |  | 0
146370 | 1.1 | Installation, testing commissioning of Variable refrigerant volume flow modular type air-conditioning system suitable to operate from 415±10% volt, 50 Hz,single three phase AC power supply for Heating Cooling by using inverter driven capa`city control compressors (Hermetically sealed scroll DC Twin Rotary type) complete with individual controller and fittings with necessary wiring, connection, including suitable isolator for each selected module, termination etc. M.S. frame duly painted to locate Outdoor Unit etc. as per quantity given below including full charging of R-410A refrigerant gas complete as per specifications. |  | 0.00 | 0.00 |  | 0
146371 | 1.1.1 | 20 HP (Three Phase) | Nos | 0.00 | 1.00 |  | 40000
146372 | 1.1.2 | 18 HP (Three Phase) | Nos | 0.00 | 1.00 |  | 35000
146373 | 1.2 | Indoor Units |  | 0.00 | 0.00 |  | 0
146374 |  | Installation , Testing and Commissioning of following Indoor units equipped with pre-filter, fan section with low noise fan, multispeed motor, coil section with DX coil, outer cabinet, drain pan, insulation, pipe connections, corded remote control etc. of various capacities as per specifications and drawings. |  | 0.00 | 0.00 |  | 0
146375 | a) | Ceiling Mounted Duct Type |  | 0.00 | 0.00 |  | 0
146376 | 1.2.1 | 1377 CFM (4.0 TR 5.0 HP) | Nos | 0.00 | 1.00 |  | 4500
146377 | 1.2.2 | 2047 CFM (5.5 TR 6.9 HP) | Nos | 0.00 | 2.00 |  | 6000
146378 | b) | 4 Way Cassette Type |  | 0.00 | 0.00 |  | 0
146379 | 1.2.3 | 4.0 TR (5.0 HP) 1218 CFM | Nos | 0.00 | 3.00 |  | 4000
146380 | c) | 1 Way Cassette Type |  | 0.00 | 0.00 |  | 0
146381 | 1.2.4 | 1.3 TR (1.6 HP) 346 CFM | Nos | 0.00 | 1.00 |  | 2550
146382 | 1.2.5 | 1.6 TR (2.0 HP) 441 CFM | Nos | 0.00 | 1.00 |  | 2550
146383 | b) | Hi Wall |  | 0.00 | 0.00 |  | 0
146384 | 1.2.6 | 530 CFM Hi Wall Type (1.6TR) | Nos | 0.00 | 1.00 |  | 2000
146385 | 1.3.1 | Corded Remote Control (SITC) | Nos. | 0.00 | 5.00 |  | 5000
146386 | 1.3.2 | Cordless Remote Control (SITC) | Nos. | 0.00 | 4.00 |  | 4000
146387 |  | Sub-Total Part- B Rs. |  | 0.00 | 0.00 |  | 0
146388 | Part C | VENTILATION EQUIPMENTS |  | 0.00 | 0.00 |  | 0
146389 | 1.0 | Kitchen Scrubber (Dry Type)-With Fan Section |  | 0.00 | 0.00 |  | 0
146390 | 1.1 | Supply , Installation, Testing and Commissioning of Dry Type Scrubber each comprising of extract air intake section, electrostatic precipitation technology, dry type air cleaner to remove oil, smoke and fumes from exhaust air, as per the Specifications. Electrostatic section shall be made of 16 gauge galvanised sheet, high bake epoxy powder coated, washable type aluminium mesh filters, stainless steel spiked ionizers to create high voltage DC field, aluminum collector plates which should be alternatively charged positive and negative with large collecting area with 14 deep cell, to work as magnet for charged smoke and oil particles. Average efficiency of 90-95% in single pass as per ASHRAE test method. Electrostatic Precipitator should be able to charge particles from 0.01 micron to 10 microns through solid state power supply. Collector cell should be of permanent type and incorporate slide out facility for easy removal for cleaning. Power supplies shall be 100% solid state UL Listed, Module of capacity above 3000 CFM shall be equipped with Pulse width modulating (PWM) |  | 0.00 | 0.00 |  | 0
146391 |  | The system should be fitted with interlock switch for safety . The system should allow connection to a fan section to achieve 500 FPM velocity across the air |  | 0.00 | 0.00 |  | 0
146392 |  | Operating Voltage 220V, 50 Hz |  | 0.00 | 0.00 |  | 0
146393 |  | Ionizing Voltage 12.5 to 13 KVDC |  | 0.00 | 0.00 |  | 0
146394 |  | Collector Cell Voltage 6 to 6.5 KVDC |  | 0.00 | 0.00 |  | 0
146395 |  | Power Consumption Not more than 50W per cell. |  | 0.00 | 0.00 |  | 0
146396 | 1.2 | DIDW Blower |  | 0.00 | 0.00 |  | 0
146397 |  | DIDW Blower, motor, V belt drive, A.V mounting, supports etc. as per Specifications Drawings |  | 0.00 | 0.00 |  | 0
146398 | 1.3 | Casing |  | 0.00 | 0.00 |  | 0
146399 |  | Factory fabricated Double Skin construction shall have 25 mm thick PUF injected Panels having density 42Kg Cum with 0.6 mm pre-plasticized pre-coated Galvanised steel sheet outside 0.6 mm plain Galvanised steel sheet inside and fixed on 30x30 mm hollow extruded aluminium section. Casing shall be appropriately housed both Electrostatic Modules and Fan with Drive. |  | 0.00 | 0.00 |  | 0
146400 | 1.4 | Accessories |  | 0.00 | 0.00 |  | 0
146401 |  | The cost shall include all accessories like Adjusting motor brackets,base,vee drive belt pulleys, vibration isolators, internal frame works ,canvas connection, Inlet Outlet flange connection etc |  | 0.00 | 0.00 |  | 0
146402 |  | 17000 CMH (10000 CFM) DIDW Blower Capacity at 65 MM ESP 7.5 KW (3 Phase) motor | Nos | 0.00 | 1.00 |  | 548000
146403 | 2.0 | Package Type Air Washers (Floor Mounted) |  | 0.00 | 0.00 |  | 0
146404 |  | Supply , Installation , testing commissioning Of Double Skin Floor Mounted Type Packaged Air Washer with extruded aluminium section with 0.6 mm preplasticized precoated GI sheet outside and 0.6 mm plain Galvanized sheet inside, minimum of 25 mm thick PUF insulation of 38KG m3 , Backward Curved DIDW Blowers , base , drive arrangement ,Filter, 200 mm thick cooling pad section, SS-304 sump tank and housing, motor drive, water circulation pump,4 Bend PVC Eliminators, piping, valves fittings etc. suitable for Outdoor Application as per specifications and drawings . |  | 0.00 | 0.00 |  | 0
146405 | 2.1 | 14450 CMH(8500 CFM) ,55 mm ESP , 5.5 KW Motor | Nos. | 0.00 | 1.00 |  | 275000
146406 |  | Sub-Total Part- C Rs. |  | 0.00 | 0.00 |  | 0
146407 | Part D | LOW SIDE WORKS |  | 0.00 | 0.00 |  | 0
146408 | 1 | Piping |  | 0.00 | 0.00 |  | 0
146409 | 1.1 | Refrigerant Piping |  | 0.00 | 0.00 |  | 0
146410 | 1.1.1 | VRF VRV SYSTEM |  | 0.00 | 0.00 |  | 0
146411 |  | Interconnecting refrigerant copper pipe work suitable for R-410A refrigerant with (19mm 13mm thick) closed cell elastomeric nitrile rubber tubular insulation between each set of indoor outdoor units as per specifications, all piping inside the room shall be properly supported with MS slotted covered cable trays(on building exterior) and suitably suspended from ceiling inside the area. |  | 0.00 | 0.00 |  | 0
146412 | a. | 6.4 mm O.D.(insulation 13 mm) | RM | 0.00 | 4.00 |  | 675
146413 | b. | 9.5 mm O.D.(insulation 13 mm) | RM | 0.00 | 36.00 |  | 750
146414 | c. | 12.7 mm O.D (insulation 19 mm). | RM | 0.00 | 18.00 |  | 950
146415 | d. | 15.9 mm O.D.(insulation 19 mm) | RM | 0.00 | 148.00 |  | 1050
146416 | e. | 19.1 mm O.D.(insulation 19 mm) | RM | 0.00 | 8.00 |  | 2250
146417 | f. | 22.2 mm O.D.(insulation 19 mm) | RM | 0.00 | 10.00 |  | 1500
146418 | g. | 28.6 mm O.D.(insulation 19 mm) | RM | 0.00 | 144.00 |  | 2650
146419 | 1.2 | Drain Piping |  | 0.00 | 0.00 |  | 0
146420 | 1.2.1 | 32 mm PVC Pipe with 9 mm insulation | RM | 0.00 | 40.00 |  | 185
146421 | 1.2.2 | 25 mm PVC Pipe with 9 mm insulation | RM | 0.00 | 25.00 |  | 155
146422 | 1.2.3 | 20 mm PVC Pipe with 9 mm insulation | RM | 0.00 | 15.00 |  | 150
146423 | 1.3 | Providing Fixing of Imported fittings Y-joints and headers etc. (9 IDU s and 2 ODU s) | Lot | 0.00 | 1.00 |  | 30000
146424 | 1.4 | Supplying, fixing, testing and commissioning of Main centralized controller Push Button Type suitable for groups of indoor outdoor units to be installed for control. (BMS Compatible). | Nos | 0.00 | 0.00 | R.O | 0
146425 | 5.0 | DUCTING |  | 0.00 | 0.00 |  | 0
146426 | 5.1 | G.I. Sheet Metal Ducting - Factory Fabricated |  | 0.00 | 0.00 |  | 0
146427 |  | Supply, Installation, Testing and Commissioning of factory fabricated GSS sheet metal rectangular ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required. |  | 0.00 | 0.00 |  | 0
146428 | 5.1.1 | 0.50 MM (26 Gauge) | Sqm. | 0.00 | 80.00 |  | 1050
146429 | 5.1.2 | 0.63 MM (24 Gauge) | Sqm. | 0.00 | 260.00 |  | 1250
146430 | 5.1.3 | 0.80 MM (22 Gauge) | Sqm. | 0.00 | 250.00 |  | 1450
146431 | 5.1.4 | 1.00 MM (20 Gauge) | Sqm. | 0.00 | 30.00 |  | 1700
146432 | 5.1.5 | 1.25 MM (18 Gauge) | Sqm. | 0.00 | 15.00 |  | 1900
146433 | 5.2 | G.I. Sheet Metal Ducting - Site Fabricated |  | 0.00 | 0.00 |  | 0
146434 |  | Supply,Installation, Testing and Commissioning of site fabricated GSS sheet metal rectangular ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required. |  | 0.00 | 0.00 |  | 0
146435 | 5.2.1 | 0.63 MM (24 Gauge) | Sqm. | 0.00 | 60.00 |  | 1250
146436 | 5.2.2 | 0.80 MM (22 Gauge) | Sqm. | 0.00 | 5.00 |  | 1350
146437 | 5.2.3 | 1.00 MM (20 Gauge) | Sqm. | 0.00 | 0.00 | R.O. | 0
146438 | 5.2.4 | 1.25 MM (18 Gauge) | Sqm. | 0.00 | 0.00 | R.O. | 0
146439 | 5.4 | Flexible Duct |  | 0.00 | 0.00 |  | 0
146440 | 5.4.1 | 200 MM Dia | RM | 0.00 | 0.00 | RO | 0
146441 | 6.0 | INSULATION |  | 0.00 | 0.00 |  | 0
146442 | 6.1 | Nitrile Rubber Insulation- Class O |  | 0.00 | 0.00 |  | 0
146443 |  | Supplying and fixing of closed cell elastomeric insulation of following thickness and density 55 kg cu.m.and K valueof not less than 0.037W mk at 20 deg C as per specifications and drawings (For indoor applications) with factory Laminated 7 mill woven glass cloth |  | 0.00 | 0.00 |  | 0
146444 | 6.1.1 | 19 mm thick (AC Fresh Air Duct ) | Sqm. | 0.00 | 340.00 |  | 1100
146445 | 6.1.2 | 25 mm thick (Exhaust Air Duct ) | Sqm. | 0.00 | 320.00 |  | 1250
146446 | 6.2 | Acoustic Lining |  | 0.00 | 0.00 |  | 0
146447 |  | Supplying and Application of Acoustic lining within the Supply Air duct with 10 mm thick class O open cell nitrile Rubber of density 140-160 kg. Cubm. as per spefications. |  | 0.00 | 0.00 |  | 0
146448 | 6.2.1 | 15 MM Thick | Sqm | 0.00 | 30.00 |  | 1450
146449 | 7.0 | DUCT ACCESSORIES |  | 0.00 | 0.00 |  | 0
146450 | 7.1 | Supply,Installation, Testing and Commissioning of GI multiblade volume control duct damper complete with neoprene rubber gaskets, nuts, bolts, screws linkages, flanges etc., as per specifications. | Sqm. | 0.00 | 2.00 |  | 7500
146451 | 7.2 | Supply,Installation, Testing and Commissioning of multiblade Al volume control Collar Grille exhaust Air Opening damper complete with suitable links, lever and quadrants for manual control of airflow and with suitable links , lever and quadrants for manual control of airflow and neoprene rubber gaskets, nuts, bolts, screws, flanges etc., as per specifications. | Sqm. | 0.00 | 2.00 |  | 9500
146452 | 7.3 | Supply,Installation, Testing and Commissioning fixing of powder coated extruded aluminium Supply Exhaust Air Grills as per specifications (zero degree deflection) | Sqm. | 0.00 | 2.00 |  | 7500
146453 | 7.8 | Supply,Installation, Testing and Commissioning fixing of powder coated extruded aluminium Continuos Grills as per specifications |  | 0.00 | 0.00 |  | 0
146454 | 7.8.1 | 150 MM Wide | RM | 0.00 | 20.00 |  | 1450
146455 | 7.8.2 | 200 MM Wide | RM | 0.00 | 15.00 |  | 1750
146456 | 7.8.3 | Scaffolding for ducting work | Job | 0.00 | 1.00 |  | 2500
146457 |  | Sub-Total Part D Rs. |  | 0.00 | 0.00 |  | 0
146458 | Part E | ELECTRICAL WORKS |  | 0.00 | 0.00 |  | 0
146459 | 1 | Electrical Work |  | 0.00 | 0.00 |  | 0
146460 | 1.0 | Electrical Control Panel |  | 0.00 | 0.00 |  | 0
146461 |  | Supply, installation, testing and commissioning of panel boards made of 2.0 mm thick steel sheet duly powder coated with voltmeter, ammeter, electronic energy meter, indicating lights, Stop manual Auto selector switch in each, outgoing current operated single phase preventer. The starters should have potential free contacts for connection to Building Automation System. The panel shall include contactors over load relay with built in single phase protection Time delay relay for delayed automatic start of the motor. All panels should have spare NO NC Contacts for BMS applications as required. |  | 0.00 | 0.00 |  | 0
146462 | 1.1.1 | Panel-P01 (Kitchen Ventilation) |  | 0.00 | 0.00 |  | 0
146463 |  | (1 x 7.5 KW + 1 x 5.5 KW ) |  | 0.00 | 0.00 |  | 0
146464 |  | INCOMER |  | 0.00 | 0.00 |  | 0
146465 | -- | 1 No. incoming 40 Amps TP+N MCB |  | 0.00 | 0.00 |  | 0
146466 | -- | 1 No. Digital Type voltmeter with selector switch with control MCB |  | 0.00 | 0.00 |  | 0
146467 | -- | 1 No. Digital Type Ammeter 0-80 A with C.T. s and selector switch. |  | 0.00 | 0.00 |  | 0
146468 | -- | 1 Set of RYB indication lamps with control MCB |  | 0.00 | 0.00 |  | 0
146469 | -- | 1 No. of 80 Amps Aluminium conductor 25kA bus bar duly sleeved as required. |  | 0.00 | 0.00 |  | 0
146470 |  | OUTGOING |  | 0.00 | 0.00 |  | 0
146471 |  | 1 Nos. 32 Amps TPN MCB |  | 0.00 | 0.00 |  | 0
146472 |  | 1 Nos. 40 Amps TPN MCB |  | 0.00 | 0.00 |  | 0
146473 |  | 1 No. DOL starter for 5.5 KW Motor |  | 0.00 | 0.00 |  | 0
146474 |  | 1 No. star delta starter for 7.5 KW Motor |  | 0.00 | 0.00 |  | 0
146475 |  | 2 Nos. of single phase preventor (current based-MPRD2) |  | 0.00 | 0.00 |  | 0
146476 |  | 2 Nos. Digital Type Ammeter |  | 0.00 | 0.00 |  | 0
146477 |  | Each star-delta DOL starter consists of current operated MN type over load relay, contactor, push button, ON OFF indication light | Set | 0.00 | 1.00 |  | 45000
146478 | 2.0 | Cables |  | 0.00 | 0.00 |  | 0
146479 | 2.1 | Supplying, laying, testing and commissioning of XLPE insulated aluminium conductor armored cables of 1.1 KV grade of following sizes directly on wall structural frame cable trays or racks using approved type of clamps,End terminations with Double Compression type glands on both ends, double earthing with GI strip wire of suitable size and hardware as per specifications. |  | 0.00 | 0.00 |  | 0
146480 | i. | 3 C x 10 Sq. mm | Mtrs | 0.00 | 0.00 | R.O. | 270
146481 | ii. | 3 C x 6 Sq. mm | Mtrs | 0.00 | 0.00 | R.O. | 0
146482 | iii. | 3 C x 4 Sq. mm | Mtrs | 0.00 | 50.00 |  | 270
146483 | 3.0 | Control Transmission Wiring |  | 0.00 | 0.00 |  | 0
146484 | 3.1 | Providing fixing control cum transmission wiring of 2 core x 1.5 sqmm copper in MS conduits between indoor and out door unit and between indoor units and their remote sensor controller. | RM | 0.00 | 190.00 |  | 150
146485 | 4.0 | Power Cabling |  | 0.00 | 0.00 |  | 0
146486 | 4.1 | Indoor Units |  | 0.00 | 0.00 |  | 0
146487 | 4.1.1 | Providing and fixing flexible power cable of 3 core x 1.5 sqmm copper between Indoor units and their power points | RM | 0.00 | 50.00 |  | 175
146488 | 4.1.2 | Providing and fixing flexible power cable of 3 core x 2.5 sqmm copper between Indoor units and their power points | RM | 0.00 | 10.00 |  | 175
146489 | 5.0 | Outdoor Units |  | 0.00 | 0.00 |  | 0
146490 | 5.1.1 | Providing and fixing flexible power cable of 4 core x 10 sqmm copper between Outdoor units and their MCB | RM | 0.00 | 0.00 | R.O. | 0
146491 | 5.1.2 | Providing and fixing flexible power cable of 4 core x 6 sqmm copper between Outdoor units and their MCB | RM | 0.00 | 80.00 |  | 475
146492 | 5.1.3 | Providing and fixing flexible power cable of 4 core x 4 sqmm copper between Outdoor units and their MCB | RM | 0.00 | 0.00 | R.O. | 0
146493 | 6.0 | Isolator (Weather Proof) |  | 0.00 | 0.00 |  | 0
146494 | 6.1 | Providing fixing weather proof isolator near each outdoor unit kitchen ventilation units as per specific control drawup. |  | 0.00 | 0.00 |  | 0
146495 | 6.1.1 | 63 Amp MCCB | Nos | 0.00 | 2.00 |  | 5200
146496 | 6.1.2 | 32 Amp MCB | Nos | 0.00 | 1.00 |  | 4200
146497 | 6.1.3 | 16 Amp MCB | Nos | 0.00 | 1.00 |  | 1500
146498 | 7.0 | GI perforated Cable tray |  | 0.00 | 0.00 |  | 0
146499 |  | Supply,Installation, Testing and Commissioning following size of perforated painted with powder coating M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts nuts, painting suspenders etc. as required. |  | 0.00 | 0.00 |  | 0
146500 | 7.1 | 150 mm width X 50 mm depth X 1.6 mm thickness | RM | 0.00 | 15.00 |  | 350
146501 | 7.2 | 300 mm width X 50 mm depth X 1.6 mm thickness | RM | 0.00 | 15.00 |  | 475
146502 | 7.3 | 450 mm width X 50 mm depth X 2.0 mm thickness | RM | 0.00 | 10.00 |  | 525
146503 | 8.0 | Earthing |  | 0.00 | 0.00 |  | 0
146504 |  | Supply,Installation, Testing and Commissioning of the following earthing clamped to wall with suitable clamps saddles and fixing bolts in ground including the cost of digging and back filling as required and complete as required to comply with IS 3043 1987. All copper joints shall be tinned. The rates shall be inclusive of making test joints where ever required |  | 0.00 | 0.00 |  | 0
146505 | 8.1 | 25 mm x 6 mm GI strip | RM | 0.00 | 25.00 |  | 275
146506 | 8.2 | 8 SWG GI Wire | RM | 0.00 | 25.00 |  | 135