## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
180777 |  | Fire Sprinkler System |  | 0.00 | 0.00 |  | 0
180778 |  | Supply, installation, testing and commissioning of G.I Heavy grade piping as per IS 1239 or 3589 GI Forged Threaded GI forged socket welded and 65mm and above Seamless schedule 40) with necessary fittings such as tees, elbows,union,flanges, bends, rubber gaskets, reducers, GI nut bolt, washer etc. The pipes being suspended from ceilings by using support with clamps, hangers using anchor fastners upto 65 mm and above 80 mm pipe should be support with galvanized channel supports complete Rate quoted shall include painting with one coat of zinc cromet primer and 2 coats of synthetic enamel PO red paint and for painting of pipe and brackets and clamps as per IS-5 for above ground piping as per the NBC or IS standards and local fire service department requirement complete including supply and installation of G.I. Rods, clamps and , fasteners etc. All supports shall be hot dip galvanized in the range of DFT of micron 80 to 90 micron with 7 tank process, hot dip galvanizing shall be confirming to IS 2629 or 2633 or 4759 or 6745. Anchor fastners to be used of chemical type only where pipe supports to be taken from brick or block work. |  | 0.00 | 0.00 |  | 0
180779 |  | 80mm nominal dia | Rmtrs | 0.00 | 10.00 |  | 0
180780 |  | 65mm nominal dia | Rmtrs | 0.00 | 10.00 |  | 0
180781 |  | 40mm nominal dia | Rmtrs | 0.00 | 5.00 |  | 0
180782 |  | 32mm nominal dia | Rmtrs | 0.00 | 15.00 |  | 0
180783 |  | 25mm nominal dia | Rmtrs | 0.00 | 45.00 |  | 0
180784 |  | Supplying, installing, testing and commissioning conventional Standard Response Sprinkler quartzoid bulb type with 15mm screwed end connection of 68 deg. C. temperature rating, K-Factor =5.6 GPM or psi½ (80.6 LPM or bar½) and orifice shall not be less than 6mm. Sprinklers shall be UL Listed or BIS approved with Chrome finished. Pendent Sprinkler | Nos | 0.00 | 22.00 |  | 0
180785 |  | Stainless steel corrugated flexible pipe(hose) for dropping sprinklers below false ceiling, pipe shall be 16 bar pressure rating and 1500 mm long, 25 mm dia with union or reducer collar, clamps etc. as required. | Nos | 0.00 | 22.00 |  | 0
180786 |  | Supply and fixing of approved type rosette plates (Recessed type, in two piece) for Sprinklers below false ceiling area. | Nos | 0.00 | 22.00 |  | 0