## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
105130 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105131 |  | MAIN PANEL SWITCHGEAR ( MAKE DB ELECTRICALS PVT LTD ) | 0 | 0.00 | 0.00 |  | 0
105132 |  | Supply, Installation, Testing Commissioning of free standing, floor mounting compartmentalized panels fabricated out of CRCA sheet steel sections after carrying out 7 tank cleaning process duly powder coated using Siemens Grey shade no. RAL- 7032. The | 0 | 0.00 | 0.00 |  | 0
105133 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105134 |  | Supply, Installation, Testing Commissioning of MAIN LT PANEL as per SLD | Nos | 0.00 | 1.00 | Technical specification and single line diagram required for quotation | 545218
105135 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105136 |  | Supply, Installation, Testing Commissioning of KITCHEN PANEL as per SLD | Nos | 0.00 | 1.00 | Technical specification and single line diagram required for quotation | 71492
105137 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105138 |  | Supply, Installation, Testing Commissioning of APFC PANEL as per SLD | Nos | 0.00 | 1.00 | Technical specification and single line diagram required for quotation | 163480
105139 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105140 |  | Supply, Installation, Testing Commissioning of switchgear with enclosure which shall be dust vermin proof with blank plates if required as per the final approval of Consultant. | 0 | 0.00 | 0.00 |  | 0
105141 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105142 |  | 250 A TPN MCCB Thermal magnetic type (25KA) in MS powdercoated enclosure complete with all mounting accessories like cable end box etc. as per site requirement. | Nos. | 0.00 | 0.00 |  | 0
105143 |  | 100 A TPN MCCB Thermal magnetic type (16KA) in MS powdercoated enclosure complete with all mounting accessories like cable end box etc. as per site requirement. | Nos. | 0.00 | 0.00 |  | 0
105144 |  | 63 A 4P RCCB 300mA type In Enclosure Outdoor Type (IP–65-Model No.601994) for AC Outdoor Unit. | Nos. | 0.00 | 8.00 |  | 4667
105145 |  | 40 A 4P RCCB 300mA type In Enclosure Outdoor Type (IP–65-Model No.601994) for AC Outdoor Unit. | Nos. | 0.00 | 0.00 |  | 0
105146 |  | 25 A 4P RCCB 300mA type In Enclosure Outdoor Type (IP–65-Model No.601994) for AC Outdoor Unit. | Nos. | 0.00 | 3.00 |  | 4132
105147 |  | SCAME ominia series switched socket outlets with interlock, flush mounting back box, frame complete with gasket. IP 67 Rating 32 A 2 pin Earth Socket outlet plug. | Nos. | 0.00 | 12.00 |  | 8825
105148 |  | SCAME ominia series switched socket outlets with interlock, flush mounting back box, frame complete with gasket. IP 67 Rating 32 A 3 phase + Neutral Earth Socket outlet plug. | Nos. | 0.00 | 12.00 |  | 10720
105149 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105150 |  | TOTAL FOR MAIN PANEL SWITCHGEAR | 0 | 0.00 | 0.00 |  | 0
105151 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105152 |  | DISTRIBUTION BOARDS | 0 | 0.00 | 0.00 |  | 0
105153 |  | Supply, Installation, Testing Commissioning of Distribution boards surface flush mounted with Double Door containing MCB ELMCB as incomer and SP MCB as outgoing. All MCB s are of 10KA breaking capacity ELMCB RCCB should be of 30mA 100mA sensitivity. | 0 | 0.00 | 0.00 |  | 0
105154 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105155 |  | Normal Power Light DB | Nos | 0.00 | 5.00 |  | 15730
105156 |  | 6 way TPN DB - Model NO. 507671 | 0 | 0.00 | 0.00 |  | 0
105157 |  | Incomer 1 X 63A 4 POLE MCB | 0 | 0.00 | 0.00 |  | 0
105158 |  | Sub Incomer 3 X 40A 2P RCCB-100mA | 0 | 0.00 | 0.00 |  | 0
105159 |  | Outgoing 12 # 10 16 20 A SP MCB C Type | 0 | 0.00 | 0.00 |  | 0
105160 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105161 |  | TOTAL FOR DISTRIBUTION BOARDS | 0 | 0.00 | 0.00 |  | 0
105162 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105163 |  | CABLES AND ACCESSORIES | 0 | 0.00 | 0.00 |  | 0
105164 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105165 |  | Supply and installation of following LT cables rated for 600 1100 volt AC as per IS standard1554 part-I with necessary M.S. clamps. All cables shall be properly clamped or tied when run on cable trays. All such cables shall be provided with temporary labe | 0 | 0.00 | 0.00 |  | 0
105166 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105167 |  | 31 2C x 240 Sq. mm Al. conductor armoured cable | Mtr | 0.00 | 0.00 |  | 0
105168 |  | 3.5C x 95 Sq. mm Al. conductor armoured cable | Mtr | 0.00 | 0.00 |  | 0
105169 |  | 4C x 50 Sq. mm Al. conductor armoured cable | Mtr | 0.00 | 0.00 |  | 0
105170 |  | 4C x 25 sq.mm. Al. conductor armoured cable | Mtr. | 0.00 | 0.00 |  | 0
105171 |  | 4C x 10 sq.mm. Copper conductor armoured cable - AC Unit, DB etc. | Mtr. | 0.00 | 500.00 |  | 651
105172 |  | 4C x 6 sq.mm. Copper conductor armoured cable - AC Unit, DB etc | Mtr. | 0.00 | 220.00 |  | 417
105173 |  | 3C x 6 sq.mm. Copper conductor armoured cable | Mtr. | 0.00 | 0.00 |  | 0
105174 |  | 4C x 4 sq.mm. Copper conductor armoured cable. | Mtr. | 0.00 | 140.00 |  | 306
105175 |  | 3C x 4 sq.mm. Copper conductor armoured cable. (AC, Power socket) | Mtr. | 0.00 | 0.00 |  | 0
105176 |  | 3C x 2.5 sq.mm. Copper conductor armoured cable (AC, Power socket) | Mtr. | 0.00 | 140.00 |  | 172
105177 |  | 3C x 1.5 sq.mm. Copper conductor armoured cable (AC, Power socket) | Mtr. | 0.00 | 275.00 |  | 122
105178 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105179 |  | Terminations for following sizes of cables | 0 | 0.00 | 0.00 |  | 0
105180 |  | Termination of the below sizes of cables with Heavy duty double compression Brass cable glands Alluminium or copper heavy duty lugs as per requirements. (4c 3.5c 3c) | 0 | 0.00 | 0.00 |  | 0
105181 |  | 31 2C x 240 Sq. mm Al. conductor armoured cable | Nos. | 0.00 | 2.00 |  | 2640
105182 |  | 3.5C x 95 Sq. mm Al. conductor armoured cable | Nos. | 0.00 | 1.00 |  | 1275
105183 |  | 3.5 4C x 50 Sq. mm Al. conductor armoured cable | Nos. | 0.00 | 1.00 |  | 892
105184 |  | 4C x 25 16 sq.mm. Al.conductor armoured cable. | Nos. | 0.00 | 24.00 |  | 520
105185 |  | 3c 4C x 10 16 sq.mm. Copper conductor armoured cable - AC Unit, DB etc. | Nos. | 0.00 | 24.00 |  | 632
105186 |  | 3c 4C x 6 4 sq.mm. Copper conductor armoured cable. | Nos. | 0.00 | 10.00 |  | 482
105187 |  | 4c 3C x 2.5 1.5 sq.mm. Copper conductor armoured cable (AC, Power socket) | Nos. | 0.00 | 20.00 |  | 482
105188 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105189 |  | TOTAL FOR CABLES AND ACCESSORIES | 0 | 0.00 | 0.00 |  | 0
105190 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105191 |  | WIRING ACCESSORIES – | 0 | 0.00 | 0.00 |  | 0
105192 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105193 |  | Supply, installation, testing commissioning of wiring for light points, power points including Circuit wiring from Distribution Board upto switch board or first light point for circuits controlled directly by MCB and shall be measured on per point basi | 0 | 0.00 | 0.00 |  | 0
105194 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105195 |  | PRIMARY POINT WIRING from switch board to first light point in 25 mm dia. PVC conduit using 2 x 1.5 sq. mm PVC insulated copper wires and 1.5 sq. mm green color PVC insulated copper wire for earthing. Conduits to be surface mounted on ceiling, concealed | Nos | 0.00 | 55.00 |  | 1700
105196 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105197 |  | Providing point wiring for Secondary light points using 2 x 1.0 sq. mm copper conductor PVC insulated wires and 1.0 sq. mm PVC insulated green color copper earth wire for continuous earthing up to fixture in PVC conduits of 20 mm dia, surface mounted on c | Nos | 0.00 | 350.00 |  | 900
105198 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105199 |  | Providing Automation light points wiring using 2 runs x 2.5 sq. mm copper conductor PVC insulated wires and 1 run of 2.5 sq. mm PVC insulated green colour copper earth wire for continuous earthing upto fixture switch board in PVC conduits of 20 mm dia, | Mtr | 0.00 | 2000.00 |  | 130
105200 |  | Providing Automation Light light points using 2 core x 1 sq. mm copper conductor PVC insulated flexible cable upto fixture from automation DB in PVC conduits of 20 mm dia, surface mounted on ceiling, concealed in wall and or through partitions with necess | Mtr | 0.00 | 500.00 |  | 72
105201 |  | Providing wiring in existing conduits 3 runs of 2.5 sq.mm. PVC insulated wires FRLS grade for Power socket outlets. | mtr | 0.00 | 1000.00 |  | 110
105202 |  | Providing wiring in existing conduits 2 runs of 4 sq.mm. 1 runs of 2.5 sq.mm.PVC insulated wires FRLS grade for Power socket outlets. | mtr | 0.00 | 500.00 |  | 170
105203 |  | Providing 3 core x 2.5 sq.mm. PVC insulated flexible cables for Power socket outlets through existing conduits trays raceways. | mtr | 0.00 | 1500.00 |  | 130
105204 |  | Providing 3 core x 4 sq.mm. PVC insulated flexible cables for Power socket outlets through existing conduits trays raceways. | mtr | 0.00 | 1000.00 |  | 180
105205 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105206 |  | Supply Installation of Hot dipped Cable Tray complete with necessary fixing arrangements like threaded rod,or angle supports, Anchor Fastner and all other accessories, as per the final approval of the Consultant Architect. | 0 | 0.00 | 0.00 |  | 0
105207 |  | 150 x 50 x1.6 mm Ladder type Cable tray. | Mtr | 0.00 | 20.00 |  | 900
105208 |  | 300 x 50 x1.6 mm Ladder type Cable tray. | Mtr | 0.00 | 100.00 |  | 1300
105209 |  | 150 x 50 x1.6 mm Perforated type Cable tray. | Mtr | 0.00 | 30.00 |  | 925
105210 |  | 300 x 50 x1.6 mm Perforated type Cable tray. | Mtr | 0.00 | 50.00 |  | 1400
105211 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105212 |  | Supply installation of AL raceway with 1.6 mm thickness having fixed with clamps at appropriate intervals as per the route approved by Architect Consultant. (Cost of cutting the floor for laying of raceways to be included wherever required) DATA | 0 | 0.00 | 0.00 |  | 0
105213 |  | a) 1 Runs of underfloor Electrical Al. raceways of size 63x38 mm | Mtr | 0.00 | 100.00 |  | 460
105214 |  | b) 1 Runs of underfloor Data Al. raceways of size 100x40 mm | Mtr | 0.00 | 100.00 |  | 690
105215 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105216 |  | Supply installation of GI junction boxes with 2mm thickness, openable cover on top having screw-fixed plates on all four sides with knock-out holes for conduits. The plates shall be retained on the sides having no conduit or raceway so as to avoid the | 0 | 0.00 | 0.00 |  | 0
105217 |  | a) suitable for 550 x 550 x 50 65 | Nos | 0.00 | 1.00 |  | 2970
105218 |  | b) suitable for 450 x 450 x 50 65 | Nos | 0.00 | 1.00 |  | 2230
105219 |  | c) suitable for 350 x 350 x 50 65 | Nos | 0.00 | 1.00 |  | 1630
105220 |  | d) suitable for 300 X 300 x 50 65 | Nos | 0.00 | 5.00 |  | 840
105221 |  | e) suitable for 150 X 150 x 50 65 | Nos | 0.00 | 5.00 |  | 450
105222 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105223 |  | Supply Installation of 25mm.dia. Medium gauge (MMS) PVC conduit with pull box junction box all accessories for Voice Data Power wiring as per the requirement. | Mtr | 0.00 | 500.00 |  | 60
105224 |  | Supply Installation of 25mm.dia. PVC flexible conduit pipe | Mtr | 0.00 | 50.00 |  | 35
105225 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105226 |  | Supply, Installation, Testing Commissioning of flush mounted plate type switch switch + sockets with hot dipped GI box complete as per the final approval of Architect Consultant. | 0 | 0.00 | 0.00 |  | 0
105227 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105228 |  | 6A One way plate type switch - SWITCH Myris NG Black color finish. | Nos | 0.00 | 30.00 |  | 90
105229 |  | 3M Plate for above Switch - Myris NG Plate Pearl Chapagne or black color finish. | Nos | 0.00 | 10.00 |  | 210
105230 |  | 3M Box for above Switch - Myris NG. | Nos | 0.00 | 10.00 |  | 90
105231 |  | 6A switch controlling 1 no. 3 pin 6A socket outlet complete with Modular plate metal back box. Myris or equivalent Plate Pearl Chapagne cover plate or black color finish | Nos | 0.00 | 5.00 |  | 500
105232 |  | 2 nos. x 16A switch controlling 2 nos. 6 pin 6 16A socket outlet complete with Modular plate metal back box. Myris or equivalent Plate Pearl Chapagne or black finish cover plate | Sets | 0.00 | 20.00 |  | 1290
105233 |  | 2 nos. 16A switch controlling 2 nos. 6 pin 6 16 A socket outlet complete with Modular plate metal back box. Myris or equivalent WHITE | Nos | 0.00 | 20.00 |  | 1130
105234 |  | 1 x 16A switch controlling 1 no. 6 pin 6 16 A socket outlet complete with Modular plate metal back box. Myris or equivalent WHITE | Nos | 0.00 | 5.00 |  | 565
105235 |  | 6A switch controlling 1 no. 3 pin 6A socket, 1no. C Power outlet, 1 no. USB outlet,1 no. Blank plate complete with Modular plate metal back box. Myris NG Plate Pearl Chapagne or black color finish. | Nos | 0.00 | 5.00 |  | 2400
105236 |  | Back box suitable for mounting Network Outlets. | Nos | 0.00 | 5.00 |  | 100
105237 |  | Arranging temporary Power Lighting for all agencies to work including suitable protection through MCBs ELCBs MCCBs wiring cabling. The temporary switch Boards should have minimum 4 Nos of 6A 16A Switch sockets plus two nos of Metal Clad sockets (Sin | Lumpsum | 0.00 | 1.00 |  | 75000
105238 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105239 |  | TOTAL FOR WIRING ACCESSORIES | 0 | 0.00 | 0.00 |  | 0
105240 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105241 |  | EARTHING | 0 | 0.00 | 0.00 |  | 0
105242 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105243 |  | Supplying and erecting GI strip of 25 x 6 mm used for earthing on wall with necessary MS clamps fixed on wall painted with bituminous paint in an approved manner (Joints are to be Bolted Welded ) | Mtr. | 0.00 | 100.00 |  | 190
105244 |  | Supplying and erecting Earth tap off box with Cu strip of 30 x 6 mm of 300mm length in 350X200X85 box with acralic facia used for earthing on wall with necessary clamps fixed on wall painted with bituminous paint in an approved manner (Joints are to be ti | Nos. | 0.00 | 2.00 |  | 6500
105245 |  | Supplying and erecting bare copper conductor of 14 SWG for earthing purpose of DBs AC machine | Mtr | 0.00 | 300.00 |  | 50
105246 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105247 |  | TOTAL FOR EARTHING | 0 | 0.00 | 0.00 |  | 0
105248 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105249 |  | LOW VOLTAGE SYSTEM | 0 | 0.00 | 0.00 |  | 0
105250 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105251 |  | ADDRESSABLE FIRE ALARM SYSTEM( RAVEL MAKE - UL APPROVED) | 0 | 0.00 | 0.00 |  | 0
105252 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105253 |  | 2 Loop Addressable Fire Alarm Panel Intelligent Fire Alarm Control Panel - Addressable Devices, Bell Circuit, Integrated PSU with Battery Charger Batteries, (Certificated by LPCB or UL) | Nos. | 0.00 | 1.00 |  | 85000
105254 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105255 |  | Addressable Manual Call Point Semi FlushMounting Re-settable, Supplied with Special Reset Tool | Nos. | 0.00 | 3.00 |  | 4500
105256 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105257 |  | Addressable Combined Sounder and Strobe, Loop Powered and 24VDC. | Nos. | 0.00 | 3.00 |  | 4500
105258 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105259 |  | Addressable Smoke Detector Intelligent Optical Detector, Above False Below Ceiling | Nos. | 0.00 | 70.00 |  | 2650
105260 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105261 |  | Addressable hEAT Detector, Above False Below Ceiling | Nos. | 0.00 | 5.00 |  | 2650
105262 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105263 |  | Response Indicator for AFC Detectors | Nos. | 0.00 | 20.00 |  | 300
105264 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105265 |  | AUTO DIALLYING System | Nos. | 0.00 | 0.00 |  | 0
105266 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105267 |  | Short Circuit Isolator Module | Nos. | 0.00 | 3.00 |  | 3500
105268 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105269 |  | Addressable Relay Module. | Nos. | 0.00 | 3.00 |  | 3500
105270 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105271 |  | MS Junction Box with GI Glands for AFC True Ceiling Detectors Modules | Nos. | 0.00 | 40.00 |  | 2500
105272 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105273 |  | Supply, installation of 2C x 1.0 sq. mm FRLS armoured cable RED in color for Fire Alarm Works System. The cost is inclusive of termination as per standard practice or as advised by Consultant. MAKE -CENTURY CABLE | Mtr | 0.00 | 1050.00 |  | 150
105274 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105275 |  | SUB TOTAL FOR FIRE ALARM SYSTEM | 0 | 0.00 | 0.00 |  | 0
105276 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105277 |  | CCTV SYSTEM cabling | 0 | 0.00 | 0.00 |  | 0
105278 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105279 |  | SITC of CAT 6 - 4 Pair UTP Cable (1 Box = 305 Mtrs ) ( Make COMMSCOPE ), including termination, connection, testing etc | Mtr | 0.00 | 610.00 |  | 45
105280 |  | Co-ordination charges for CCTV equipments. | LS | 0.00 | 1.00 |  | 10000
105281 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105282 |  | SUB TOTAL FOR CCTV EQUIPMENTS | 0 | 0.00 | 0.00 |  | 0
105283 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105284 |  | DJ CONSOLE PROJECTOR TV CABLING | 0 | 0.00 | 0.00 |  | 0
105285 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105286 |  | Removing relaying speaker MIC cables as directed by Architect Consultants.(Labour charges only) | Mtr | 0.00 | 100.00 |  | 75
105287 |  | Removing relaying HDMI cables as directed by Architect Consultants.(Labour charges only) | Mtr | 0.00 | 100.00 |  | 75
105288 |  | Removing relaying Power cables as directed by Architect Consultants.(Labour charges only) | Mtr | 0.00 | 100.00 |  | 75
105289 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105290 |  | TOTAL FOR PA SYSTEM | 0 | 0.00 | 0.00 |  | 0
105291 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105292 |  | TELEPHONE SYSTEM – MAIN WIRING | 0 | 0.00 | 0.00 |  | 0
105293 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105294 |  | Supply Installation of 25mm.dia. Medium gauge (MMS) PVC conduit with pull box junction box all accessories for Voice Data Power wiring as per the requirement. | Mtr | 0.00 | 500.00 |  | 60
105295 |  | 25 dia flexible conduit | Mtr. | 0.00 | 75.00 |  | 45
105296 |  | Supply, installation of CAT 6 - 4 Pair UTP Cable ( 1 Box = 305 Mtrs ) ( Make COMMSCOPE ) | Mtr. | 0.00 | 305.00 |  | 45
105297 |  | Testing of all Terminations using Fluke Cable Analyser. The cost quoted is including Information outlet. | Nos | 0.00 | 8.00 |  | 100
105298 |  | Supply Installation of Dual I O Face Plate ( Make COMMSCOPE ) | Nos | 0.00 | 8.00 |  | 200
105299 |  | Supply Installation of CAT 6 I O ( Make COMMSCOPE ) | Nos | 0.00 | 8.00 |  | 450
105300 |  | Telephone patch cord | Nos. | 0.00 | 8.00 |  | 200
105301 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105302 |  | TOTAL FOR TELEPHONE DISTRIBUTION | 0 | 0.00 | 0.00 |  | 0
105303 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105304 |  | DATA (NETWORK SYSTEM) | 0 | 0.00 | 0.00 |  | 0
105305 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105306 |  | Supply, installation of CAT 6 - 4 Pair UTP Cable ( 1 Box = 305 Mtrs ) ( Make COMMSCOPE ) | Mtr. | 0.00 | 610.00 |  | 45
105307 |  | Testing of all Terminations using Fluke Cable Analyser. The cost quoted is including Information outlet. | Nos | 0.00 | 8.00 |  | 350
105308 |  | Supply Installation of Dual I O Face Plate ( Make COMMSCOPE ) | Nos | 0.00 | 8.00 |  | 195
105309 |  | Supply Installation of CAT 6 I O ( Make COMMSCOPE ) | Nos | 0.00 | 8.00 |  | 450
105310 |  | Supply, Installation, testing commissioning of 48 port patch panel ( Make COMMSCOPE ) | Nos. | 0.00 | 0.00 |  | 0
105311 |  | Supply, installation of 1 Mtr UTP Patch Cord CAT 6 ( Make COMMSCOPE ) | Nos | 0.00 | 8.00 |  | 230
105312 |  | Supply, installation of 2 Mtr UTP Patch Cord CAT 6 ( Make COMMSCOPE ) | Nos | 0.00 | 8.00 |  | 270
105313 |  | Supply, installation of 5 Mtr UTP Patch Cord CAT 6 ( Make COMMSCOPE ) | Nos | 0.00 | 0.00 |  | 0
105314 |  | PVC Horizontal Cable Manager | Nos | 0.00 | 0.00 |  | 0
105315 |  | Jack panel 24 Port (Voice Data) | Nos | 0.00 | 1.00 |  | 10000
105316 |  | Supply, Installation of 6 core multimode armoured OFC cable on existing cable tray (Make COMMSCOPE) | Mtr. | 0.00 | 0.00 |  | 0
105317 |  | OFC Termination of Fiber Cores using Fusion Splicing Method | Nos. | 0.00 | 0.00 |  | 0
105318 |  | OFC Testing of Fiber Cores After Termination | Nos. | 0.00 | 0.00 |  | 0
105319 |  | Documentation Includes Updation of Drawing Specifying Data, Voice Points on Floor Plan, Soft Copy Hard Copy of all Test Reports Certification 20 year performance guarantee Certificate by Schneider ensuring installation is done as per TIA EIA or | LS | 0.00 | 0.00 |  | 0
105320 |  | HEAT MAP ANALYSIS TEST FOR WIFI NETWORK Test to plan and create Wi-Fi networks according to client performance and capacity requirements and simulating real-life application usage such as VoIP, HD video streaming and web browsing. | LS | 0.00 | 0.00 |  | 0
105321 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105322 |  | TOTAL FOR NETWORKING | 0 | 0.00 | 0.00 |  | 0
105323 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105324 |  | LIGHTING FIXTURES Labour charges towards Installation Only | 0 | 0.00 | 0.00 | We are quoting labour charges only towards installation of all types of lights supplied by you on site | 0
105325 |  | 0 | 0 | 0.00 | 0.00 |  | 0
105326 |  | Linear profile light for ceiling Cove light | mtr. | 0.00 | 165.00 |  | 250
105327 |  | Flexible profile light for Cove light for wall paneling skirting etc. | mtr. | 0.00 | 100.00 |  | 150
105328 |  | Wall mounted light Ceiling mounted decorative indoor lights. | Nos. | 0.00 | 20.00 |  | 400
105329 |  | Decorative table lamps | Nos. | 0.00 | 10.00 |  | 400
105330 |  | Spot light upto 24 Watts | Nos. | 0.00 | 66.00 |  | 400
105331 |  | Spot light upto 12 15 Watts | Nos. | 0.00 | 100.00 |  | 400
105332 |  | Decorative outdoor 3 watt uplighter | Nos. | 0.00 | 200.00 |  | 400
105333 |  | 6w grazer spot light | Nos. | 0.00 | 20.00 |  | 400
105334 |  | Submersible light for waterbody | Nos. | 0.00 | 15.00 |  | 400
105335 |  | Occupancy sensor for Washroom | Nos. | 0.00 | 4.00 |  | 400
105336 |  | LIGHTING AUTOMATION PROVISIONAL BUDGET. | LS | 0.00 | 0.00 | Light Automation scope cannot be quoted as labour charges only as detailed scope of work to be understood from lighting fixture, automation agency and any other agencies involved in finalizing the work.