## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
125893 |  | Supply and Installation of all materials, accessories and labour for point wiring for power or light or equipment circuit main using PVC insulated stranded copper conductor FRLS wires of 650V grade drawn th0ugh Rigit Metal MS Conduit along with switch boards.Flex conduit to be used for turning.(The cost of the conduit will be taken with point wiring) using necessary conduit accessories,junction boxes, etc. The rate shall include the cost of p0viding PVC insulated stranded copper conductor earth wire in each conduit alongwith other circuit main wires. Lugs to be use at both the ends. FRLS wiresType only.Primary point of power point should be considered upto 20 Mtr Light point should be considered upto 15MTR wire all secondary points upto 5 Mtr.Above rate should include all wires,conduits,support,hardwate other required all accessories,scaffolding etc. Work to be completed in all respect. NO ADDITIONAL CIRCUIT LENGTH WOULD BE P0VIDED FOR ANY POWER OR LIGHTING POINT. MEASUREMENT WILL BE TAKEN ON THE PURE COUNT OF NOS OF POWER LIGHT POINTS |  | 0.00 | 0.00 |  | 0
125894 |  | Primary Point wiring 2x2.5 + 1x1.5 sq. mm CU. FRLS wire. Power point cost to be included with back box,Switches,Socket,Modulat plate all inclusive. FOH area plates to be black Kitchen SB to have white color switch board. (For EquipmentsorComputersorConvenience points) | Nos. | 0.00 | 53.00 |  | 0
125895 |  | Secondary Point wiring 2x2.5 + 1x1.5 sq. mm CU. FRLS wire.Power point cost to be included with back box,Switches,Socket,Modulat plate all inclusive. FOH area plates to be black Kitchen SB to have white color switch board. (For EquipmentsorComputersorConvenience points) | Nos. | 0.00 | 35.00 |  | 0
125896 |  | Primary Point wiring 2x2.5 + 1x1.5 sq. mm CU. FRLS wire. Lighting wiring min conduit size to be 20mm. 20mm conduit should not have maximum 2 or 3 circuit. All conduits should not be full with 3 circuit. Future p0vision space to be left in some conduits. Juction boxes,Ceiling 0se,connector for light fixture to be installed. (Lights directly cont0lled f0m distribution board) | Nos. | 0.00 | 25.00 |  | 0
125897 |  | Secondary Point wiring 2x2.5 + 1x1.5 sq. mm CU. FRLS wire. Lighting wiring min conduit size to be 20mm. 20mm conduit should not have maximum 2 or 3 circuit. All conduits should not be full with 3 circuit. Future p0vision space to be left in some conduits.Juction boxes,Ceiling 0se,connector for light fixture to be installed. (Lights directly cont0lled f0m distribution board) | Nos. | 0.00 | 105.00 |  | 0
125898 |  | Primary Point wiring 2x2.5 + 1x1.5 sq. mm CU. FRLS wire. Lighting wiring min conduit size to be 20mm. 20mm conduit should not have maximum 2 or 3 circuit. All conduits should not be full with 3 circuit. Future p0vision space to be left in some conduits.Juction boxes,Ceiling 0se,connector for light fixture to be installed.Avg circuit 15 Mtr (Lights cont0lled f0m individual switch board) | Nos. | 0.00 | 5.00 |  | 0
125899 |  | Secondary Point wiring 2x2.5 + 1x1.5 sq. mm CU. FRLS wire. Lighting wiring min conduit size to be 20mm. 20mm conduit should not have maximum 2 or 3 circuit. All conduits should not be full with 3 circuit. Future p0vision space to be left in some conduits.Juction boxes,Ceiling 0se,connector for light fixture to be installed.Avg Length 7 Mtr (Lights cont0lled f0m individual switch board) | Nos. | 0.00 | 3.00 |  | 0
125900 |  | Supplying and installing all materials, accessories and labour for conduiting the accessories for lightor Equipment circuit main.The conduit should be Medium gauge rigid 1.6 mm thick GI conduits conforming to IS-2509 of 1973 . The conduits shall be clamped by GI saddles . The clampsorsupports shall be fixed to the underside of the ceiling or floor by means of nylon rawl plugs and brass screws of 3 mm size. Anchor fasteners of suitable sizes shall be p0vided if necessary. The conduits shall be supported at regular intervals of 500 mm. Additional supports shall be p0vided on either side of bends, JB s terminations. The conduits shall be bent with bending springs to p0vide smooth bends. Use of ready made bends shall be kept to a minimum. The jointing of GI conduits shall be done with couplers. Conduits to be terminated in GI Boxes shall be terminated with female adaptors with bushes. End portion of the conduit to be p0vided with end caps where ever necessary. The cost should include the cost of heavy gauge rigid GI conduit with necessary conduit accessories, GI pullorjunction boxes, GI fish wire etc laying of the same. FRLS Only |  | 0.00 | 0.00 |  | 0
125901 |  | 25mm PVC Conduit | Rmt | 0.00 | 60.00 |  | 0
125902 |  | 32mm PVC Conduit | Rmt | 0.00 | 0.00 |  | 0
125903 |  | 75X45mm Aluminium Rectangle tube Raceway | Rmt | 0.00 | 0.00 |  | 0
125904 |  | 80X60mm Aluminium Rectangle tube Raceway | Rmt | 0.00 | 0.00 |  | 0
125905 |  | Supply installations of GI Powder coated, Junction Boxes made of 2.0 mm thkor1.6mm thk, with removal GI Powder coated Top Cover 2.0mm thk, all side entries for raceways, complete with all accessories. The rate to include fixing the juncrtion box on the floor Trenches or floor described above. Sample junction box to be app0ved first. |  | 0.00 | 0.00 |  | 0
125906 |  | 150mm x 150mm GI Junction Box | Nos. | 0.00 | 0.00 |  | 0
125907 |  | 200mm x 200mm GI Junction Box | Nos. | 0.00 | 0.00 |  | 0
125908 |  | 300mm x 300mm GI Junction Box | Nos. | 0.00 | 0.00 |  | 0
125909 |  | SECTION-II-SUPPLY INSTALLATION OF WHETHER P0OF SWITCH SOCKET OUTLETS |  | 0.00 | 0.00 |  | 0
125910 |  | Supply Installation of switches, sockets, complete with MS boxes f0nt plate inter - connections, box earthing its complete accessories.Wiring to be included switch board. Avg length of Primaty point upto 20 Mtr Secondary point upto 8 Mtr. All wiring to be complete with all accessories. Conduit to be used as Rigid Metal. |  | 0.00 | 0.00 |  | 0
125911 |  | Primary Point - 6or16A Switch Socket Outlet (RAW Power) - Whether P0of for outside | Nos. | 0.00 | 0.00 |  | 0
125912 |  | Secondary Point - 6or16A Switch Socket Outlet (RAW Power) - Whether P0of for outside | Nos. | 0.00 | 0.00 |  | 0
125913 |  | SECTION III-TELEPHONE or DATA SYSTEM AND TV |  | 0.00 | 0.00 |  | 0
125914 |  | Supply Installation of the Cat6 information outlet with face plate. (For data). | Nos. | 0.00 | 30.00 |  | 0
125915 |  | Supply Installation of Cat. 6 Data cable via 20or25mm Metal Conduits with tagging ferruling crimping at both the ends. | Rmt | 0.00 | 1450.00 |  | 0
125916 |  | Supply Installation of RJ11 telephone outlet with plate and box | Nos | 0.00 | 0.00 |  | 0
125917 |  | Supply Installation of CAT5 cable in 20or25mm dia GI conduit for telephone | Rmt | 0.00 | 0.00 |  | 0
125918 |  | Supply Installation of 20 pair telephone tag block with enclosure | Nos | 0.00 | 0.00 |  | 0
125919 |  | TV out let socket with white face plate Metal back box | Nos | 0.00 | 0.00 |  | 0
125920 |  | 4W or 6W Splitter fot TV cables | Nos | 0.00 | 0.00 |  | 0
125921 |  | Supply, installation of RG59orRG6 Co-axial cable for TV with PVC Conduits 25mmor32 mm fixed to wallsorCeiling with Spacers saddles or taken th0ugh false ceiling or raceways | Rmt | 0.00 | 0.00 |  | 0
125922 |  | SECTION IV-LIGHTING |  | 0.00 | 0.00 |  | 0
125923 |  | Installation of the following light fittings (Light Fixtures will be supplied by Client) |  | 0.00 | 0.00 |  | 0
125924 |  | Suspended Linear | Nos | 0.00 | 0.00 |  | 0
125925 |  | Suspended Chandelier | Nos | 0.00 | 37.00 |  | 0
125926 |  | Surface Mounted or Concealed DownlightorDownlight | Nos | 0.00 | 65.00 |  | 0
125927 |  | Covelight | Rmt | 0.00 | 25.00 |  | 0
125928 |  | Supplying, installing, testing and commissioning of suitable size of dimmer panel for 10 Nos. circuit with 6 to 8 Nos light fixture on each circuit 2000W light load, complete as required . (Make-Wip0orABB) | Nos | 0.00 | 1.00 |  | 0
125929 |  | SECTION-V PANELS, DISTRIBUTION BOARDS |  | 0.00 | 0.00 |  | 0
125930 |  | Supply,Installation, Testing Commissioning of FloororWall mounted cubicle type LT panelorDB of CRCA sheet steel (2mm Thickness) construction with total f0nt access for switchgear and top entry for all incoming and outgoing cables. Totally compartmentalized including p0per AlorCopper bus bar chambers, cable alley, etc. as per SLD. 160A - MCCB Incomer ELR - 300 MA OorV Voltage Relay Single Phase Preventor Al Bus Bar - 200A Earthing strip - 2 Nos Cooling Fan - APFC Section APFC - 28 to 30 KVAR Out going feeder as per SLD with RCBO Inbuit 14WAY SPN LDB 1 Inbuit - 12WAY TPN RPDB Phase Lamp Emergency Stop Botton All AHU Starter panel with VFD Floor Standing Panel Tube type Fire Suppression system | Nos | 0.00 | 1.00 |  | 0
125931 |  | 8 Way ETPN (LDB-2) with 1 no 40A FP RCBO 100mA as incomer and 24 nos of 6or10or16A MCB as Outgoings (RAW DB) | Nos. | 0.00 | 1.00 |  | 0
125932 |  | 12 Way ETPN (LPDB) with 1 no 63A FP RCBO 100mA as incomer and 24 nos of 16A MCB as Outgoings (Raw Power) | Nos. | 0.00 | 0.00 |  | 0
125933 |  | 16 Way SPN (UPSDB1) with 1 no 63A DP RCBO 100mA as incomer and 14 nos of 6or10or16A MCB as Outgoings | Nos. | 0.00 | 1.00 |  | 0
125934 |  | 12 Way SPN (UPSDB2) with 1 no 25A DP RCBO 100mA as incomer and 8 nos of 6or10or16A MCB as Outgoings | Nos. | 0.00 | 1.00 |  | 0
125935 |  | SECTION-VI -CABLING EARTHING |  | 0.00 | 0.00 |  | 0
125936 |  | Supply of Installation of Following cables 1.1 KV grade PVCorXLPE insulated Armoured AluminiumorCopper conductor cables. The cables shall be laid as per dwgs or on cable trays laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an app0ved manner as required complete with earthing as specified for continuous earthing along with cable . (The cost of the cable trays or ladders, excavation and back filling of trenches will be measured separate. The unit cost of the cable shall include clamps, fasteners etc. as required for p0per installation. Earthing will be measured separately and need not be quoted under this item). All complete as required and as per final instruction as given by consultantorsite engineer. The cables should be p0perly dressed and to be tied to the cable trays using app0priate cable ties. |  | 0.00 | 0.00 |  | 0
125937 |  | 2 C X 2.5 sq. mm. CU ARMOURED | Rmt | 0.00 | 0.00 |  | 0
125938 |  | 3.5 C X 50 sq. mm. CU ARMOURED | Rmt | 0.00 | 0.00 |  | 0
125939 |  | 3.5 C X 70 sq. mm. CU ARMOURED | Rmt | 0.00 | 0.00 |  | 0
125940 |  | 3.5 C X 95 sq. mm. CU ARMOURED | Rmt | 0.00 | 0.00 |  | 0
125941 |  | 3 C X 2.5 sq. mm. CU PVC ARMOURED | Rmt | 0.00 | 25.00 |  | 0
125942 |  | 3 C X 4 sq. mm. CU PVC ARMOURED | Rmt | 0.00 | 15.00 |  | 0
125943 |  | 3 C X 6 sq. mm. CU PVC ARMOURED | Rmt | 0.00 | 60.00 |  | 0
125944 |  | 3 C X 10 sq. mm. CU PVC ARMOURED | Rmt | 0.00 | 0.00 |  | 0
125945 |  | 3 C X 16 sq. mm. CU PVC ARMOURED | Rmt | 0.00 | 0.00 |  | 0
125946 |  | 4 C X 16 sq. mm. CU PVC ARMOURED | Rmt | 0.00 | 0.00 |  | 0
125947 |  | 4 C X 2.5 sq. mm. CU PVC ARMOURED | Rmt | 0.00 | 0.00 |  | 0
125948 |  | 4 C X 4 sq. mm. CU PVC ARMOURED | Rmt | 0.00 | 210.00 |  | 0
125949 |  | 4 C X 6 sq. mm. CU PVC ARMOURED | Rmt | 0.00 | 80.00 |  | 0
125950 |  | 4 C X 10 sq. mm. CU PVC ARMOURED | Rmt | 0.00 | 50.00 |  | 0
125951 |  | 4 C X 16 sq. mm. AL. PVC ARMOURED | Rmt | 0.00 | 40.00 |  | 0
125952 |  | 4 C X 25 sq. mm. AL. PVC ARMOURED | Rmt | 0.00 | 0.00 |  | 0
125953 |  | 4 C X 35 sq. mm. AL. PVC ARMOURED | Rmt | 0.00 | 0.00 |  | 0
125954 |  | 3.5 C X 50 sq. mm. AL. XLPE ARMOURED | Rmt | 0.00 | 0.00 |  | 0
125955 |  | 3.5 C X 70 sq. mm. AL. XLPE ARMOURED | Rmt | 0.00 | 0.00 |  | 0
125956 |  | 3.5 C X 95 sq. mm. AL. XLPE ARMOURED | Rmt | 0.00 | 0.00 |  | 0
125957 |  | 3.5 C X120 sq. mm. AL. XLPE CABLE ARMOURED | Rmt | 0.00 | 0.00 |  | 0
125958 |  | 3.5 C X185 sq. mm. AL. XLPE CABLE ARMOURED | Rmt | 0.00 | 0.00 |  | 0
125959 |  | Supply of Installation of Following cable Terminations including SingleorDouble compression type ch0me plated brass glands and lugs(crimping type), PVC taping as required and all accessories complete. |  | 0.00 | 0.00 |  | 0
125960 |  | 2 C X 2.5 sq. mm. CU ARMOURED | Nos | 0.00 | 0.00 |  | 0
125961 |  | 3.5 C X 50 sq. mm. CU ARMOURED | Nos | 0.00 | 0.00 |  | 0
125962 |  | 3.5 C X 70 sq. mm. CU ARMOURED | Nos | 0.00 | 0.00 |  | 0
125963 |  | 3.5 C X 95 sq. mm. CU ARMOURED | Nos | 0.00 | 0.00 |  | 0
125964 |  | 3 C X 2.5 sq. mm. CU PVC ARMOURED | Nos | 0.00 | 2.00 |  | 0
125965 |  | 3 C X 4 sq. mm. CU PVC ARMOURED | Nos | 0.00 | 2.00 |  | 0
125966 |  | 3 C X 6 sq. mm. CU PVC ARMOURED | Nos | 0.00 | 4.00 |  | 0
125967 |  | 3 C X 10 sq. mm. CU PVC ARMOURED | Nos | 0.00 | 0.00 |  | 0
125968 |  | 3 C X 16 sq. mm. CU PVC ARMOURED | Nos | 0.00 | 0.00 |  | 0
125969 |  | 4 C X 16 sq. mm. CU PVC ARMOURED | Nos | 0.00 | 0.00 |  | 0
125970 |  | 4 C X 2.5 sq. mm. CU PVC ARMOURED | Nos | 0.00 | 0.00 |  | 0
125971 |  | 4 C X 4 sq. mm. CU PVC ARMOURED | Nos | 0.00 | 12.00 |  | 0
125972 |  | 4 C X 6 sq. mm. CU PVC ARMOURED | Nos | 0.00 | 4.00 |  | 0
125973 |  | 4 C X 10 sq. mm. CU PVC ARMOURED | Nos | 0.00 | 2.00 |  | 0
125974 |  | 4 C X 16 sq. mm. AL. XLPE ARMOURED | Nos | 0.00 | 2.00 |  | 0
125975 |  | 4 C X 25 sq. mm. AL. XLPE ARMOURED | Nos | 0.00 | 0.00 |  | 0
125976 |  | 4 C X 35 sq. mm. AL. XLPE ARMOURED | Nos | 0.00 | 0.00 |  | 0
125977 |  | 3.5 C X 50 sq. mm. AL. XLPE ARMOURED | Nos | 0.00 | 0.00 |  | 0
125978 |  | 3.5 C X 70 sq. mm. AL. XLPE ARMOURED | Nos | 0.00 | 0.00 |  | 0
125979 |  | 3.5 C X 95 sq. mm. AL. XLPE ARMOURED | Nos | 0.00 | 0.00 |  | 0
125980 |  | 3.5 C X120 sq. mm. AL. XLPE CABLE ARMOURED | Nos | 0.00 | 0.00 |  | 0
125981 |  | 3.5 C X185 sq. mm. AL. XLPE CABLE ARMOURED | Nos | 0.00 | 0.00 |  | 0
125982 |  | 3.5 C X400 sq. mm. AL. XLPE CABLE ARMOURED | Nos | 0.00 | 0.00 |  | 0
125983 |  | Supply Installation of Following Cable Trays of 2mm thick GI fabricated ladder type cable trays of the following sizes. Ladder type cable trays shall be fabricated f0m 50 x 50 x 5 mm GI angles on the sides with 25 x 6 mm GI strips welded at intervals of 300 mm. The trays shall be painted with 2 coats of red oxide 2 coats of synthetic enamel paint of app0ved colour. All trays should have coupler plates with 4 number of bolt and nuts of galvanized hardware.Trays should be supported at ecvery 1.5 mtr interval. |  | 0.00 | 0.00 |  | 0
125984 |  | 200mm wide perforated cable tray with support (Power Supply) | Rmt | 0.00 | 10.00 |  | 0
125985 |  | 300mm wide perforated cable tray with support (LV supply) | Rmt | 0.00 | 25.00 |  | 0
125986 |  | Supply Installation of Chemical Earthing station as per specification and IS 3043-1985 for equipment earthing for panel and equipment earthing. Following guidelines to be maintained | Nos. | 0.00 | 0.00 |  | 0
125987 |  | Excavation in hard marrum |  | 0.00 | 0.00 |  | 0
125988 |  | Chemical compound |  | 0.00 | 0.00 |  | 0
125989 |  | Earthing strip or Earthing cable |  | 0.00 | 0.00 |  | 0
125990 |  | Cu pipe in pipe elect0de |  | 0.00 | 0.00 |  | 0
125991 |  | Hardware |  | 0.00 | 0.00 |  | 0
125992 |  | Brick masonry chamber with C.I. hinged cover and funnel |  | 0.00 | 0.00 |  | 0
125993 |  | Equipotential bar |  | 0.00 | 0.00 |  | 0
125994 |  | SITC of earthing wire including necessary accessories, clamped on over head slab or walls, laid over false ceiling or in wall chases. Rate to include making good the wall chases with cement mortar. Interconnection between lengths should be as per specifications and as per good installation practice. |  | 0.00 | 0.00 |  | 0
125995 |  | 10 SWG GI Wire | Rmt | 0.00 | 420.00 |  | 0
125996 |  | 25 X 3 mm GI Strip | Rmt | 0.00 | 10.00 |  | 0
125997 |  | 1 core x 6 sq.mm .Cu wire | Rmt | 0.00 | 75.00 |  | 0
125998 |  | 1 Core x 2.5 Sq.mm Cu Wire | Rmt | 0.00 | 0.00 |  | 0
125999 |  | SECTION-VII -IP SYSTEM CCTV |  | 0.00 | 0.00 |  | 0
126000 |  | SITC 3+1 CCTV flexible cable in 20or25mm Metal MS conduit | Rmt | 0.00 | 650.00 |  | 0
126001 |  | SITC RG6 co-axial cable in 20or25mm Metal MS conduit (For CCTV and LED TV) | Rmt | 0.00 | 0.00 |  | 0
126002 |  | SITC H.264 standalone DVR, 8 ch video, cif real-time, d1 non real-time, 1 sata hdd 2 tb cp-plus 0804hxt | Nos | 0.00 | 0.00 |  | 0
126003 |  | SITC IP color indoor IR dome camera GE est 12vdc, 24 ir led, , fixed board lens f=3.6mm ceiling mounted | Nos | 0.00 | 0.00 |  | 0
126004 |  | SITC Power supply 12v dc p0tek pktps1012nabs | Nos | 0.00 | 0.00 |  | 0
126005 |  | SITC 18.5 (19 ) TFT monitor with wall mount bracket Samsung b1930 | Nos | 0.00 | 0.00 |  | 0
126006 |  | SITC of Cat 6 cctv cabling in Metal MS Conduit | Rmt | 0.00 | 0.00 |  | 0
126007 |  | SECTION-VIII -UPS |  | 0.00 | 0.00 |  | 0
126008 |  | SITC of 1 phase online UPS for all critical load. Computer load IT load will be on separate UPS . Separate DB to be planned of UPS. UPS load to be balance in all phase.Battery bank to ne planned seperately on MS rack.UPS to connected with iorO MCB boxes.30 min should min backup on full load condition. |  | 0.00 | 0.00 |  | 0
126009 |  | 6KVA | Nos. | 0.00 | 1.00 |  | 0
126010 |  | 3 KVA | Nos. | 0.00 | 0.00 |  | 0
126011 |  | P0viding Temp0ry Light Fixture | job | 0.00 | 1.00 |  | 0
126012 |  | Removing of Existing Cables Wiring, Conduits, Light Fixture,Fire Equipments and related Itmes | job | 0.00 | 0.00 |  | 0
126013 |  | SECTION-IX-GAS DETECTION SYSTEM |  | 0.00 | 0.00 |  | 0
126014 |  | SITC of FR 4C x 1.5 sq. mm 1100V copper conducter, PVC insulated cable and shielded armoured and PVC sheathed cable for Gas Detection System. Cable shall be cleated to wall and ceiling (Red colour) | Rmt | 0.00 | 130.00 |  | 0
126015 |  | SITC of Gas panel LED lamp indicator in case of detection. | Nos | 0.00 | 1.00 |  | 0
126016 |  | SITC of gas detector to be mounted at gas flexible hose | Nos | 0.00 | 2.00 |  | 0
126017 |  | SECTION-X-MUSIC SYSTEM |  | 0.00 | 0.00 |  | 0
126018 |  | SITC of 70or36 Transparent Speaker cable in 20or25mm MS metal conduit | Rmt | 0.00 | 225.00 |  | 0
126019 |  | SITC of 15W speakers SPW4 to be mounted on ceiling or Wall | Nos | 0.00 | 0.00 |  | 0
126020 |  | SITC of Sub-woofer SPW8S to be mounted on ceiling. | Nos | 0.00 | 0.00 |  | 0
126021 |  | SITC of 15W speakers SPW4 to be mounted on wall. | Nos | 0.00 | 0.00 |  | 0
126022 |  | SITC of Sub-woofer SPW8S to be mounted on wall. | Nos | 0.00 | 0.00 |  | 0
126023 |  | SITC of get up signaling device. | Nos | 0.00 | 0.00 |  | 0
126024 |  | Installation of amplifier 120W for music system suitable to operate on 230V ACor12V DC, with low impedance mic0phone input two auxiliary inputs, tone cont0l, p0tection circuit complete for the speakers output 4or8or16 lines | Nos | 0.00 | 0.00 |  | 0
126025 |  | SITC of table top mic0phone | Nos | 0.00 | 0.00 |  | 0
126026 |  | SIEMENS orL T MAKE MK1 3 PHASE DOL STARTER FOR ALL EXHAUST FANorFRESH AIRorINLINE FAN |  | 0.00 | 0.00 |  | 0
126027 |  | 7.5 KW | Nos. | 0.00 | 0.00 |  | 0
126028 |  | 5.5 KW | Nos. | 0.00 | 0.00 |  | 0
126029 |  | 3.7 KW | Nos. | 0.00 | 0.00 |  | 0
126030 |  | 2.2 KW | Nos. | 0.00 | 0.00 |  | 0
126031 |  | Above 7.5KW StarorDelta Starter (3 Phase) |  | 0.00 | 0.00 |  | 0
126032 |  | SITC OF ENCLOSURES FOR MCB FOR OUTDOOR APPLICATION WITH MCB DP FP |  | 0.00 | 0.00 |  | 0
126033 |  | DP MCB in weather p0of enclosure with MCB |  | 0.00 | 0.00 |  | 0
126034 |  | 40-63A | Nos | 0.00 | 0.00 |  | 0
126035 |  | 6-32A | Nos | 0.00 | 2.00 |  | 0
126036 |  | TPN MCB in weather p0of enclosure with MCB |  | 0.00 | 0.00 |  | 0
126037 |  | 80-100A | Nos | 0.00 | 0.00 |  | 0
126038 |  | 40-63A | Nos | 0.00 | 5.00 |  | 0
126039 |  | 6-32A | Nos | 0.00 | 0.00 |  | 0
126040 |  | SITC OF INDUSTRIAL TYPE METRA PLUGorTEMPRA PLUG FOR EQUIPMENT POWER CONNECTIONS WITH REQUIRED MCB |  | 0.00 | 0.00 |  | 0
126041 |  | 63A 5Pin 3 Phase Plug and Socket with TPN MCB | Nos | 0.00 | 1.00 |  | 0
126042 |  | 40A 5Pin 3 Phase Plug and Socket with TPN MCB | Nos | 0.00 | 1.00 |  | 0
126043 |  | 20or32A 3Pin Single Phase Plug and Socket with DP MCB | Nos | 0.00 | 5.00 |  | 0
126044 |  | 20A 2Pin SP Metal Clad Socket with SP MCB (Industrial Type) | Nos | 0.00 | 0.00 |  | 0
126045 |  | SECTION-XI- IT (Passive) |  | 0.00 | 0.00 |  | 0
126046 |  | CAT 6 -305 M | Nos | 0.00 | 0.00 |  | 0
126047 |  | Jackpanel | Nos | 0.00 | 0.00 |  | 0
126048 |  | CAT 6 IO | Nos | 0.00 | 0.00 |  | 0
126049 |  | 4 port wall plate | Nos | 0.00 | 0.00 |  | 0
126050 |  | 2 port Wall plate | Nos | 0.00 | 0.00 |  | 0
126051 |  | Patch cables - 2mtrs | Nos | 0.00 | 20.00 |  | 0
126052 |  | Patch cables - 1mtrs | Nos | 0.00 | 20.00 |  | 0
126053 |  | Cable laying IO Punching , Face plate installation,crimping ,testing ,Rack dressing, |  | 0.00 | 0.00 |  | 0
126054 |  | SECTION-XII- FIRE ALARM SYSTEM |  | 0.00 | 0.00 |  | 0
126055 |  | SITC of wall mounted 1 zone addressable type fire panel same to be intergrated with building BMS system. FAS panel to be ULorFM listed. Make- Notifier (Honeywell) |  | 0.00 | 0.00 |  | 0
126056 |  | Fire panel to also give output to trip HVAC system. | Nos. | 0.00 | 1.00 |  | 0
126057 |  | SITC of 2C x 1.5 Sq.mm, 1100V copper conductor, PVC insulated and sheilded armoured and overall FRLS PVC sheathed red color cable for fire Alarm system. Cable shall be cleated to wall, ceiling with required accessoires all complete. | Rmt | 0.00 | 350.00 |  | 0
126058 |  | SITC of Smoke detector addresable type | Nos. | 0.00 | 18.00 |  | 0
126059 |  | Response Indicator for smoke Detector | Nos | 0.00 | 7.00 |  | 0
126060 |  | SITC of Heat detector | Nos | 0.00 | 3.00 |  | 0
126061 |  | SITC of MCP at all exit door | Nos. | 0.00 | 3.00 |  | 0
126062 |  | SITC of Hooter | Nos. | 0.00 | 3.00 |  | 0
126063 |  | SITC of repeater module for integration with mall system | Nos | 0.00 | 1.00 |  | 0
126064 |  | SECTION-XIII- FIRE EXTINGUISHER |  | 0.00 | 0.00 |  | 0
126065 |  | SITC of Fire Extinguisher with cylinder it’s wall mounted brack floor stand as per site condition. Signage to be pasted on wall at the location of Fire Extinguisher |  | 0.00 | 0.00 |  | 0
126066 |  | ABC Type- 5 Kg | Nos | 0.00 | 8.00 |  | 0
126067 |  | CO2 Type - 5 Kg | Nos | 0.00 | 1.00 |  | 0
126068 |  | K Type - 5 Kg | Nos | 0.00 | 1.00 |  | 0
126069 |  | ARFF Type - 5 Kg | Nos | 0.00 | 1.00 |  | 0