## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
88244 | A.1 | If any termination or connection of the unit services is required outside the site location (i.e., connection termination of the MEP unit to the airport MEP service or airport external façade or roof, etc.), then the contractor has to work in consultation with the airport to plan, design, and detail such connections. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor is to make good on any penetrations after installation, including providing fire seals as required as per airport requirements. |  | 0.00 | 0.00 | Provisional Sum | 0
88245 |  | AUTOMATIC FIRE SPRINKLER HEADS ACCESSORIES |  | 0.00 | 0.00 |  | 0
88246 | B.1 | Supply, Installation, Testing Commissioning of Automatic Concealed Fire Sprinkler Heads (Bulb type Sprinklers) with adjustable Escutcheon plates (Rosette plates). Standard Temperature Response with 5mm glass bulb, Temperature rating of 68° C, K-factor of 80, Nominal Thread size of 1 2 NPT (15mm) and a Orifice size of 13mm with a Max. Working Pressure of 12 Bar (Factory hydrostatic test presure of 35 Bar) and to be Manufactured Certified to UL 199. Shall also include suspending arrangement with ceiling wall etc. (Make Ansul, Buckeye, Smog Hog, Gem-Tyco, Spray safe or equivalent with airport approval) |  | 0.00 | 0.00 |  | 0
88247 | B.1.1 | Pendant type of 68° C (Finishing - Chrome Plated) | Nos | 0.00 | 12.00 |  | 750
88248 | B.1.2 | Pendant type of 79° C (Finishing - Chrome Plated) | Nos | 0.00 | 4.00 |  | 750
88249 | B.1.3 | Upright Pendant type of 68° C (Finishing - Chrome Plated) | Nos | 0.00 | 15.00 |  | 750
88250 |  | FIRE SPRINKLER PIPE VALVES ACCESSORIES |  | 0.00 | 0.00 |  | 0
88251 | B.2 | Supply, Installation, Testing Commissioning of Cast Iron Butterfly Valve slimseal PN16 (working pressure of 16 Bar), standard flow control lever operated with stainless steel shaft disc, seat material with Black Nitrile EPDM, flanges nuts and bots etc. (Make Tyco Viking Victualic HD fire Newage or equivalent with airport approval.) |  | 0.00 | 0.00 |  | 0
88252 | B.2.1 | 65 mm Dia | Nos | 0.00 | 1.00 |  | 12600
88253 | B.3 | Supply, Installation, Testing Commissioning of Brass body Test And Drain Valve with Sight Glass, working pressure of 20 Bar (300 PSI), standard lever operated with stainless steel stem lever, with necessary weldable fittings in position as per drawings site conditions. (Make Tyco Viking Victualic HD fire Newage or equivalent with airport approval.) |  | 0.00 | 0.00 |  | 0
88254 | B.3.1 | 25 mm Dia | Nos | 0.00 | 1.00 |  | 4300
88255 | B.4 | Supply, Installation, Testing Commissioning of Flow Switch on Sprinkler distribution header pipe with a working pressure of 31 Bar (450 PSI) and a flow sensitivity range of 4-10 GPM (15 - 38 LPM) on each floor zone inside proposed demise area tap of point, shall be connected to fire alarm panel through cable. (Make Potter System Sensor or equivalent with airport approval) |  | 0.00 | 0.00 |  | 0
88256 | B.4.1 | 65 mm Dia | Nos | 0.00 | 1.00 |  | 5400
88257 |  | FIRE SPRINKLER PIPING |  | 0.00 | 0.00 |  | 0
88258 | B.5 | Supply, Installation, Testing Commissioning of MS C Class Fire Sprinkler Pipe confirming to IS 1239 with all fittings like bends, tees, flanges, nut, bolt and washers etc, and proper pipe supports to not more than 3 meter apart of the pipe length. The pipe work shall be hydrostatically tested for not less than 2 hours at 15 Bar (or 1.5 times the working) pressure without leak. The pipes are to be applied with 2 coats of primer (indicated film thickness, dry 50 microns) and 2 coats of enamel finish paint of approved colour (indicated film thickness, dry 30 microns) (Make HSL, Mukut, Lalit steel or equivalent) |  | 0.00 | 0.00 |  | 0
88259 | B.5.1 | 25 mm Dia | Mtr | 0.00 | 53.00 |  | 950
88260 | B.5.2 | 32 mm Dia | Mtr | 0.00 | 10.00 |  | 1350
88261 | B.5.3 | 40 mm Dia | Mtr | 0.00 | 6.00 |  | 1650
88262 | B.5.4 | 50 mm Dia | Mtr | 0.00 | 4.00 |  | 2300
88263 | B.5.5 | 65 mm Dia | Mtr | 0.00 | 14.00 |  | 2870