## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
96155 |  | Note Prices shall be based on supply, installation, testing commissioning (SITC) at site including all taxes, duties, transportation insurance etc. |  | 0.00 | 0.00 |  | 0
96156 |  | SHEET METAL WORKS |  | 0.00 | 0.00 |  | 0
96157 |  | GI SHEET METAL DUCTING - Supply, Fabrication, Testing, Air Flow Balancing and Commissioning of Factory Fabricated GI Sheet Metal 180GSM Rectangular boxed ducting, Plenums, Cowls, Elbows, Splitters, Reducers, Flanges, Collars etc as per SMACNA standards, The complete ducting shall be provided with MS Supports, Rods, Angles, Flanges, Bracing, Rubber Gaskets, Wooden frames, Canvas Connections, etc. as per drawings and specifications. |  | 0.00 | 0.00 |  | 0
96158 |  | 22 Gauge GI Sheet Metal Duct (601-1100mm) | Sq.mtr | 0.00 | 50.00 |  | 0
96159 |  | 24 Gauge GI Sheet Metal Duct (0-600mm) | Sq.mtr | 0.00 | 150.00 |  | 0
96160 |  | SS EXHAUST AND FRESH AIR GRILLS - SITC of 18G SS 304 Fresh Air Grilles adjustable Double Deflector With S.S Volume Control Dampers. Grills to be of Double Deflection Type for ease of deflection on all sides. | Sq.mtr | 0.00 | 0.75 |  | 0
96161 |  | DOOR TRANSFER GRILLE SITC of Aluminium extruded powder coated Door transfer grills. Door transfer grille (Back to Back) | Sq.mtr | 0.00 | 0.25 |  | 0
96162 |  | MULTI LEAF VOLUME CONTROL DAMPER - SITC of opposed blade aerofoil type 1.2 mm thick Anodized Aluminium volume control dampers for ducts shall be provided with concealed gears, plastic operator and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawings and specifications. | Sq.mtr | 0.00 | 2.50 |  | 0
96163 |  | CURTAIN TYPE FIRE DAMPER - SITC of curtain type fire dampers consist of 16G GI frame, 20G GI interlocking blades secured with SS springs, blades outside airstream clamped with fusible link UL-555 listed with melting point 165 225°F, etc; as per the approved shop drawings and specifications. |  | 0.00 | 0.00 |  | 0
96164 |  | Bare fire dampers | Sq.mtr | 0.00 | 0.30 |  | 0
96165 |  | Fusible link as per specification UL 555 and CBRI approved | No. | 0.00 | 1.00 |  | 0
96166 |  | CANVAS CONNECTION - Supply fixing of flexible Canvas connections between mouth piece and initial piece of ducting. Flexible connections shall be fire resistant made of closely woven, double layer canvass neoprene coated fibre glass. |  | 0.00 | 0.00 |  | 0
96167 |  | Cabiner Exhaust Fan | Nos | 0.00 | 1.00 |  | 0
96168 |  | Dry Scrubber | Nos | 0.00 | 1.00 |  | 0
96169 |  | NOTES The ducting support should be as per tender specification and additional supports are to be provided by Contractor as decided by Consultant. Muslin cloth cover for all air outlets during construction. Pressure testing of complete duct work as per DW SMACNA standard. Silicon sealant for longitudinal transverse joints as per specification. Diffusers grilles shall be powder coated as per color approved by Architect. |  | 0.00 | 0.00 |  | 0
96170 |  | THERMAL INSULATION SITC of Rockwool roll Insulation with stonewool fibres bonded with thermosetting resins, with factory applied laminated Woven Fiber glass cloth of 271GSM. Nominal density 48 Kg CuM. Thermal conductivity, < 0.042 W m.K at 50°C. All Insulation material and adhesives shall be as per Class O for surface spread and in accordance with BS 476, Class O for non-combustible grade. Also, cost shall include all necessary support and accessories. 50 mm Thick | Sq.mtr | 0.00 | 200.00 |  | 0
96171 |  | ELECTRICAL WORKS |  | 0.00 | 0.00 |  | 0
96172 |  | STARTER PANEL with VFD SITC of indoor outdoor, wall mounting type 3PH, 415VAC MOTOR STARTERS IN CRCA SHEET STEEL ENCLOSURE with necssary supporting brackets and required accessories, etc., The Enclosure shall be provided with knockouts suitable for cable termination at TOP BOTTOM for incoming and outgoing power cables of A2XFY type and size specified. The starters shall be complete with suitable MPCB MCCB, Contactor, Bi-metal O L relay with SPP, ON OFF Push buttons, on off trip indication Lamp, on off push button, phase indication Lamp. Selection of relay, contractor, MPCB MCCB etc. as per Type-2 Coordination. Starter panel shall be BMS compatible. Variable frequency drives shall be provided with necessary sensors and controllers complete with control wiring in all respect as required. VFDs shall be provided with necessary bypass arrangement inside electrical starter panels with IP-55 enclosure. 5.5KW, 3PH, DOL Starter type for exhaust air fan | No | 0.00 | 1.00 |  | 0
96173 |  | POWER CABLING - Supply, handling, laying effecting proper connections testing and commissioning of following sizes of 1.1 KV grade XLPE insulated FRLS Aluminium Copper conductor cables laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with Copper earthing as specified for continuous earthing along with cable. All complete as required and as per final instruction as given by Owners Consultants and as per Technical specifications. Earthing shall be measured separately and shall be connected in two runs. Power to ELCB to be provided near each ODU by electrical contractor. Power Cable |  | 0.00 | 0.00 |  | 0
96174 |  | CU 2.5 sqmm 4 core - Exhaust Fan | Rmt | 0.00 | 10.00 |  | 0
96175 |  | CU 2.5 sqmm 3 core - Dry Scrubber | Rmt | 0.00 | 10.00 |  | 0
96176 |  | Earthing - 8 SWG GI Earthing | Rmt | 0.00 | 20.00 |  | 0
96177 |  | CABLE TERMINATION Supply Making of Cable termination of armoured unarmoured cables 1.1 KV grade including installation of cable glands, cable lugs (Aluminium for A2XFY copper for 2XFY YY Double compression type), heat shrinkable sleeves on long ends, crimping paste etc. The work includes testing commissioning of cables, meggaring values submitting reports of tests. (One set includes termination of all cores of one end only). All crimping tools dies shall be arranged by contractor. CU 2.5 sqmm 4 core - Exhaust Fan | Nos. | 0.00 | 2.00 |  | 0
96178 |  | CABLE TRAYS Supplying Fixing of following sizes of GI cable tray duly painted perforated type of height 50mm along with necessary bends, reducers etc. anchored along the wall suspended from the ceiling with necessary MS supports. 150mm wide | Rmt | 0.00 | 20.00 |  | 0