## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
91109 |  | Installation,testing commissioning of the following Centrifugal Blower would be used to supply Exhaust Air into the Kitchen, Fan to have Backward inclined Blades, Impeller Should be statically and Dynamically Balanced, Motor to have Squirrel cage, to operate on 3Phase 50Hz AC supply, TEFC Class F Insulation, IE2 Type Motor - Crompton Siemens Make, Fan would be supplied with Anti Vibration Pads 7000 CFM (Air quantity) 75 mm (Static) | Nos | 0.00 | 1.00 | EXHAUST AIR BLOWER | 0
91110 |  | Installation,testing commissioning of the following Centrifugal Blower would be used to supply Exhaust Air into the Kitchen, Fan to have Backward inclined Blades, Impeller Should be statically and Dynamically Balanced, Motor to have Squirrel cage, to operate on 3Phase 50Hz AC supply, TEFC Class F Insulation, IE2 Type Motor - Crompton Siemens Make, Fan would be supplied with Anti Vibration Pads 5800 CFM (Air quantity) 50 mm (Static) | Nos | 0.00 | 1.00 | EXHAUST AIR BLOWER | 0
91111 |  | Installation,testing commissioning of the following Centrifugal Blower would be used to supply Fresh Air into the Kitchen, Fan to have Backward inclined Blades, Impeller Should be statically and Dynamically Balanced, Motor to have Squirrel cage, to operate on 3Phase 50Hz AC supply, TEFC Class F Insulation, IE2 Type Motor - Crompton Siemens Make, Fan would be supplied with Anti Vibration Pads 5200 CFM(Air quantity) 50mm(Static) | Nos | 0.00 | 1.00 | FRESH AIR BLOWER | 0
91112 |  | Installation,testing commissioning of the following Centrifugal Blower would be used to supply Fresh Air into the Kitchen, Fan to have Backward inclined Blades, Impeller Should be statically and Dynamically Balanced, Motor to have Squirrel cage, to operate on 3Phase 50Hz AC supply, TEFC Class F Insulation, IE2 Type Motor - Crompton Siemens Make, Fan would be supplied with Anti Vibration Pads 5000 CFM(Air quantity) 75 mm(Static) | Nos | 0.00 | 1.00 | FRESH AIR BLOWER | 0
91113 |  | - Construction Made of 16 gauge galvanized sheet, high bake epoxy powder coated or 2 mm mild steel plate oil proof of IP 54. - Operating Voltage 220V 1Ph 50Hz - Power consumption 50 watts per module unit up to 5000 cfm. - Pre Filter Washable type aluminum mesh pre-filter - Ionizer spring loaded Tungsten wires to create high voltage DC field 12-13 kV - Collector Plate High grade Aluminum collector plates which should be alternatively charged positive negative with large collecting area. Collector cell should be of permanent type and slide out facility for easy removal for cleaning. - Insulator Teaflon insulator. - Access door to filter section shall be equipped with safety limit switch. Exhaust Air Qty -7000CFM (Approved make - APC-DS-3) | Nos | 0.00 | 1.00 | Electrostatic Precipitator Filter for Kitchen Exhaust Air Treatment | 0
91114 |  | - Construction Made of 16 gauge galvanized sheet, high bake epoxy powder coated or 2 mm mild steel plate oil proof of IP 54. - Operating Voltage 220V 1Ph 50Hz - Power consumption 50 watts per module unit up to 5000 cfm. - Pre Filter Washable type aluminum mesh pre-filter - Ionizer spring loaded Tungsten wires to create high voltage DC field 12-13 kV - Collector Plate High grade Aluminum collector plates which should be alternatively charged positive negative with large collecting area. Collector cell should be of permanent type and slide out facility for easy removal for cleaning. - Insulator Teaflon insulator. - Access door to filter section shall be equipped with safety limit switch. Exhaust Air Qty -5800 CFM (Approved make - APC-DS-3) | Nos | 0.00 | 1.00 | Electrostatic Precipitator Filter for Kitchen Exhaust Air Treatment | 0
91115 |  | 0.80 mm (22 SWG) GSS ducting (751mm-1500mm) Supply, fabrication, installation and testing of MS SS metal ducts as per IS-277 (120 GSM both sides, LFQ confirming to Class VIII) for MS SS Sheets and IS-655 for fabrication of following thicknesses including necessary G.I. hangers supports, volume control duct dampers, accessories, vanes, 3 mm neoprene rubber gasket etc. complete as per specifications in accordance with the approved shop drawings. No slip joints shall be allowed. Flanges shall be Rolamate or equivalent and ducts upto 1500 mm width shall be with rigid support (Gripple support to be provided wherever required) as per technical specifications. Ducts shall be leak pressure tested leakages should be within acceptable limits as specified at Min. 500 Pa | Sqmt | 0.00 | 145.00 | Sheet Metal Ducting - Site Fabricated | 0
91116 |  | 13 mm thick Supplying and fixing of following thickness duly laminated aluminum foil of mat finish. (Make - Hira Technologies) | Sqmt | 0.00 | 70.00 | Insulation of Duct | 0
91117 |  | Supply, installation and adjusting of GSS Volume Control Damper within ducts complete as specified and with suitable links, levers. Blades should be opposed blade type. The blades should be mounted in nylon bushes operated by an interior wheel gear system. Manual quadrant control with position indicator to be provided to enable adjust volume of air as required. | Sqmt | 0.00 | 2.50 | Volume Control Damper | 0
91118 |  | Supplying fixing of black mat finish extruded aluminium opposed blade volume control dampers in supply air duct collars as per approved shop drawings and specifications | Nos | 0.00 | 6.00 | Volume Control Damper | 0
91119 |  | Grilles - 300mmX300mm Make - Cosmos Extruded Aluminum Powder Coated Grilles Of Required Airflow Angles Without V.C.D- EP -00 15 30 with four side flanges as following sizes. | Nos | 0.00 | 16.00 | Grilles | 0
91120 |  | Supply Instalation Terminal Lovure with air flow movement for Exhuast Fresh Air duct outside mouth end. | Nos | 0.00 | 4.00 | Mesh Terminal Grilles | 0